## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6023-26_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6023-26_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6023-26_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6023-26_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6023-26_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6023-26_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6023-26_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_6023-26_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_6023-26_0_4_node_69 | 0.4 | n |  | TRUE
9 | bus_LV_6023-26_0_4_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_6023-26_0_4_node_77 | 0.4 | n |  | TRUE
11 | bus_LV_6023-26_0_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_6023-26_0_4_node_48 | 0.4 | n |  | TRUE
13 | bus_LV_6023-26_0_4_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_6023-26_0_4_node_81 | 0.4 | n |  | TRUE
15 | bus_LV_6023-26_0_4_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_6023-26_0_4_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_6023-26_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_6023-26_0_4_node_51 | 0.4 | n |  | TRUE
19 | bus_LV_6023-26_0_4_node_47 | 0.4 | n |  | TRUE
20 | bus_LV_6023-26_0_4_node_36 | 0.4 | n |  | TRUE
21 | bus_LV_6023-26_0_4_node_34 | 0.4 | n |  | TRUE
22 | bus_LV_6023-26_0_4_node_8 | 0.4 | n |  | TRUE
23 | bus_LV_6023-26_0_4_node_9 | 0.4 | n |  | TRUE
24 | bus_LV_6023-26_0_4_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_6023-26_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_6023-26_0_4_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_6023-26_0_4_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_6023-26_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_6023-26_0_4_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_6023-26_0_4_node_70 | 0.4 | n |  | TRUE
31 | bus_LV_6023-26_0_4_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_6023-26_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_6023-26_0_4_node_78 | 0.4 | n |  | TRUE
34 | bus_LV_6023-26_0_4_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_6023-26_0_4_node_79 | 0.4 | n |  | TRUE
36 | bus_LV_6023-26_0_4_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_6023-26_0_4_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_6023-26_0_4_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_6023-26_0_4_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_6023-26_0_4_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_6023-26_0_4_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_6023-26_0_4_node_31 | 0.4 | n |  | TRUE
43 | bus_LV_6023-26_0_4_node_32 | 0.4 | n |  | TRUE
44 | bus_LV_6023-26_0_4_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_6023-26_0_4_node_72 | 0.4 | n |  | TRUE
46 | bus_LV_6023-26_0_4_node_73 | 0.4 | n |  | TRUE
47 | bus_LV_6023-26_0_4_node_60 | 0.4 | n |  | TRUE
48 | bus_LV_6023-26_0_4_node_56 | 0.4 | n |  | TRUE
49 | bus_LV_6023-26_0_4_node_61 | 0.4 | n |  | TRUE
50 | bus_LV_6023-26_0_4_node_57 | 0.4 | n |  | TRUE
51 | bus_LV_6023-26_0_4_node_37 | 0.4 | n |  | TRUE
52 | bus_LV_6023-26_0_4_node_38 | 0.4 | n |  | TRUE
53 | bus_LV_6023-26_0_4_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_6023-26_0_4_node_40 | 0.4 | n |  | TRUE
55 | bus_LV_6023-26_0_4_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_6023-26_0_4_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_6023-26_0_4_node_67 | 0.4 | n |  | TRUE
58 | bus_LV_6023-26_0_4_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_6023-26_0_4_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_6023-26_0_4_node_44 | 0.4 | n |  | TRUE
61 | bus_LV_6023-26_0_4_node_54 | 0.4 | n |  | TRUE
62 | bus_LV_6023-26_0_4_node_68 | 0.4 | n |  | TRUE
63 | bus_LV_6023-26_0_4_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_6023-26_0_4_node_46 | 0.4 | n |  | TRUE
65 | bus_LV_6023-26_0_4_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_6023-26_0_4_node_49 | 0.4 | n |  | TRUE
67 | bus_LV_6023-26_0_4_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_6023-26_0_4_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_6023-26_0_4_node_64 | 0.4 | n |  | TRUE
70 | bus_LV_6023-26_0_4_node_63 | 0.4 | n |  | TRUE
71 | bus_LV_6023-26_0_4_node_65 | 0.4 | n |  | TRUE
72 | bus_LV_6023-26_0_4_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_6023-26_0_4_node_59 | 0.4 | n |  | TRUE
74 | bus_LV_6023-26_0_4_node_82 | 0.4 | n |  | TRUE
75 | bus_LV_6023-26_0_4_node_76 | 0.4 | n |  | TRUE
76 | bus_LV_6023-26_0_4_node_62 | 0.4 | n |  | TRUE
77 | bus_LV_6023-26_0_4_node_66 | 0.4 | n |  | TRUE
78 | bus_LV_6023-26_0_4_node_80 | 0.4 | n |  | TRUE
79 | bus_LV_6023-26_0_4_node_74 | 0.4 | n |  | TRUE
80 | bus_LV_6023-26_0_4_node_75 | 0.4 | n |  | TRUE
81 | bus_MV_266_0_node_170 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6023-26_0_4_load_0 | 0 | 0.0027994 | 0.00070159 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6023-26_0_4_load_1 | 1 | 0.0057082 | 0.0014306 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6023-26_0_4_load_2 | 2 | 0.0041175 | 0.0010319 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6023-26_0_4_load_6 | 6 | 0.011039 | 0.0027667 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6023-26_0_4_load_7 | 7 | 0.0050035 | 0.001254 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6023-26_0_4_load_77 | 10 | 0.011453 | 0.0028705 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6023-26_0_4_load_12 | 11 | 0.0023073 | 0.00057827 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6023-26_0_4_load_81 | 14 | 0.0024799 | 0.00062152 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6023-26_0_4_load_29 | 15 | 0.0032064 | 0.00080359 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6023-26_0_4_load_11 | 17 | 0.0039399 | 0.00098742 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6023-26_0_4_load_47 | 19 | 0.0070229 | 0.0017601 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6023-26_0_4_load_34 | 21 | 0.0095389 | 0.0023907 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6023-26_0_4_load_8 | 22 | 0.0021306 | 0.00053397 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6023-26_0_4_load_10 | 24 | 0.0048894 | 0.0012254 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6023-26_0_4_load_13 | 25 | 0.0043302 | 0.0010853 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6023-26_0_4_load_16 | 27 | 0.0094146 | 0.0023595 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6023-26_0_4_load_17 | 28 | 0.0057129 | 0.0014318 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6023-26_0_4_load_70 | 30 | 0.007047 | 0.0017662 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6023-26_0_4_load_78 | 33 | 0.0047911 | 0.0012008 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6023-26_0_4_load_20 | 34 | 0.0030824 | 0.00077253 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6023-26_0_4_load_79 | 35 | 0.0036906 | 0.00092496 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6023-26_0_4_load_21 | 36 | 0.0038259 | 0.00095885 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6023-26_0_4_load_24 | 37 | 0.0052266 | 0.0013099 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6023-26_0_4_load_25 | 38 | 0.0097175 | 0.0024354 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6023-26_0_4_load_28 | 39 | 0.0059549 | 0.0014924 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6023-26_0_4_load_27 | 40 | 0.010382 | 0.0026019 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6023-26_0_4_load_30 | 41 | 0.0047332 | 0.0011862 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6023-26_0_4_load_32 | 43 | 0.0045851 | 0.0011491 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6023-26_0_4_load_33 | 44 | 0.0027526 | 0.00068985 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6023-26_0_4_load_60 | 47 | 0.0044365 | 0.0011119 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6023-26_0_4_load_56 | 48 | 0.0068108 | 0.001707 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6023-26_0_4_load_61 | 49 | 0.0052471 | 0.001315 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6023-26_0_4_load_37 | 51 | 0.0056699 | 0.001421 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6023-26_0_4_load_38 | 52 | 0.0079714 | 0.0019978 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6023-26_0_4_load_40 | 54 | 0.0078605 | 0.00197 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6023-26_0_4_load_67 | 57 | 0.015814 | 0.0039635 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6023-26_0_4_load_42 | 59 | 0.0059898 | 0.0015012 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6023-26_0_4_load_44 | 60 | 0.010304 | 0.0025823 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6023-26_0_4_load_54 | 61 | 0.0092472 | 0.0023176 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6023-26_0_4_load_68 | 62 | 0.0081422 | 0.0020406 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6023-26_0_4_load_46 | 64 | 0.0078062 | 0.0019564 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6023-26_0_4_load_55 | 65 | 0.0071517 | 0.0017924 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6023-26_0_4_load_49 | 66 | 0.0096904 | 0.0024286 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6023-26_0_4_load_52 | 67 | 0.0073081 | 0.0018316 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6023-26_0_4_load_53 | 68 | 0.0086602 | 0.0021704 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6023-26_0_4_load_64 | 69 | 0.0096366 | 0.0024152 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6023-26_0_4_load_63 | 70 | 0.0067444 | 0.0016903 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6023-26_0_4_load_58 | 72 | 0.0031492 | 0.00078927 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6023-26_0_4_load_82 | 74 | 0.0027124 | 0.00067979 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6023-26_0_4_load_76 | 75 | 0.002888 | 0.0007238 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6023-26_0_4_load_62 | 76 | 0.0071419 | 0.0017899 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6023-26_0_4_load_80 | 78 | 0.0053051 | 0.0013296 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6023-26_0_4_load_74 | 79 | 0.003035 | 0.00076064 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6023-26_0_4_load_75 | 80 | 0.0025844 | 0.00064772 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6023-26_0_4_line_0 |  | 0 | 1 | 0.030112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6023-26_0_4_line_1 |  | 0 | 2 | 0.033883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6023-26_0_4_line_2 |  | 1 | 3 | 0.046885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6023-26_0_4_line_3 |  | 2 | 4 | 0.025105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6023-26_0_4_line_4 |  | 3 | 5 | 0.032518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6023-26_0_4_line_5 |  | 3 | 6 | 0.02498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_6023-26_0_4_line_6 |  | 3 | 7 | 0.017656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_6023-26_0_4_line_7 |  | 4 | 8 | 0.038241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6023-26_0_4_line_8 |  | 4 | 9 | 0.039402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6023-26_0_4_line_9 |  | 5 | 10 | 0.012264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6023-26_0_4_line_10 |  | 5 | 11 | 0.024583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6023-26_0_4_line_11 |  | 6 | 12 | 0.01621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_6023-26_0_4_line_12 |  | 7 | 13 | 0.019809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_6023-26_0_4_line_13 |  | 8 | 14 | 0.02623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6023-26_0_4_line_14 |  | 9 | 15 | 0.012777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6023-26_0_4_line_15 |  | 9 | 16 | 0.050822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6023-26_0_4_line_16 |  | 11 | 17 | 0.015889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6023-26_0_4_line_17 |  | 12 | 18 | 0.02489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6023-26_0_4_line_18 |  | 12 | 19 | 0.012602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6023-26_0_4_line_19 |  | 13 | 20 | 0.001824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6023-26_0_4_line_20 |  | 13 | 21 | 0.034304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6023-26_0_4_line_21 |  | 15 | 39 | 0.013255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6023-26_0_4_line_22 |  | 16 | 37 | 0.019888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6023-26_0_4_line_23 |  | 16 | 32 | 0.034127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6023-26_0_4_line_24 |  | 17 | 24 | 0.0085781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6023-26_0_4_line_25 |  | 18 | 65 | 0.029836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6023-26_0_4_line_26 |  | 18 | 66 | 0.0061565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6023-26_0_4_line_27 |  | 19 | 64 | 0.0085452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6023-26_0_4_line_28 |  | 20 | 47 | 0.016999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6023-26_0_4_line_29 |  | 20 | 48 | 0.012194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6023-26_0_4_line_30 |  | 22 | 23 | 0.037455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6023-26_0_4_line_31 |  | 23 | 24 | 0.014585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6023-26_0_4_line_32 |  | 25 | 26 | 0.007227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6023-26_0_4_line_33 |  | 26 | 27 | 0.025192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6023-26_0_4_line_34 |  | 26 | 28 | 0.020278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6023-26_0_4_line_35 |  | 27 | 29 | 0.0034615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6023-26_0_4_line_36 |  | 28 | 30 | 0.026868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6023-26_0_4_line_37 |  | 29 | 31 | 0.013877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6023-26_0_4_line_38 |  | 31 | 32 | 0.003676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6023-26_0_4_line_39 |  | 31 | 33 | 0.055515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6023-26_0_4_line_40 |  | 32 | 34 | 0.013554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6023-26_0_4_line_41 |  | 33 | 35 | 0.019111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6023-26_0_4_line_42 |  | 34 | 36 | 0.016992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6023-26_0_4_line_43 |  | 37 | 38 | 0.019447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6023-26_0_4_line_44 |  | 39 | 40 | 0.02045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6023-26_0_4_line_45 |  | 41 | 42 | 0.011318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6023-26_0_4_line_46 |  | 41 | 43 | 0.039087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6023-26_0_4_line_47 |  | 42 | 44 | 0.032727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6023-26_0_4_line_48 |  | 44 | 45 | 0.010645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6023-26_0_4_line_49 |  | 45 | 46 | 0.007659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6023-26_0_4_line_50 |  | 46 | 75 | 0.015529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6023-26_0_4_line_51 |  | 46 | 73 | 0.026479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6023-26_0_4_line_52 |  | 47 | 49 | 0.00063818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6023-26_0_4_line_53 |  | 48 | 50 | 0.014488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6023-26_0_4_line_54 |  | 49 | 76 | 0.027359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6023-26_0_4_line_55 |  | 50 | 72 | 0.01724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6023-26_0_4_line_56 |  | 50 | 73 | 0.016836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6023-26_0_4_line_57 |  | 51 | 52 | 0.013124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6023-26_0_4_line_58 |  | 51 | 53 | 0.020101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6023-26_0_4_line_59 |  | 52 | 54 | 0.026475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6023-26_0_4_line_60 |  | 53 | 55 | 0.008636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6023-26_0_4_line_61 |  | 55 | 56 | 0.032383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6023-26_0_4_line_62 |  | 55 | 57 | 0.026126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6023-26_0_4_line_63 |  | 56 | 58 | 0.01771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6023-26_0_4_line_64 |  | 56 | 59 | 0.013799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6023-26_0_4_line_65 |  | 58 | 61 | 0.007936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6023-26_0_4_line_66 |  | 58 | 62 | 0.019103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6023-26_0_4_line_67 |  | 59 | 60 | 0.033315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6023-26_0_4_line_68 |  | 61 | 63 | 0.023698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6023-26_0_4_line_69 |  | 63 | 67 | 0.01945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6023-26_0_4_line_70 |  | 63 | 68 | 0.016485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6023-26_0_4_line_71 |  | 63 | 66 | 0.032353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_6023-26_0_4_line_72 |  | 65 | 70 | 0.0038176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_6023-26_0_4_line_73 |  | 67 | 69 | 0.034953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_6023-26_0_4_line_74 |  | 69 | 71 | 0.044561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_6023-26_0_4_line_75 |  | 71 | 77 | 0.041528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_6023-26_0_4_line_76 |  | 73 | 74 | 0.038823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_6023-26_0_4_line_77 |  | 75 | 79 | 0.020895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_6023-26_0_4_line_78 |  | 77 | 78 | 0.015704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_6023-26_0_4_line_79 |  | 79 | 80 | 0.016563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6023-26_0_4_trafo_35 | 0.63 MVA 20/0.4 kV | 81 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2589784.2969 | 1119546.9092 | 2589783.39 | 1119548.7083 | 2589771.4065 | 1119574.1224
1 | 2589784.2969 | 1119546.9092 | 2589799.5482 | 1119516.6531
2 | 2589751.4103 | 1119616.5294 | 2589771.4065 | 1119574.1224
3 | 2589810.8487 | 1119494.235 | 2589799.5482 | 1119516.6531
4 | 2589751.4103 | 1119616.5294 | 2589783.5533 | 1119622.0329
5 | 2589751.4103 | 1119616.5294 | 2589745.0883 | 1119640.6959
6 | 2589751.4103 | 1119616.5294 | 2589735.9651 | 1119607.9746
7 | 2589810.8487 | 1119494.235 | 2589848.5575 | 1119501.219
8 | 2589772.9559 | 1119483.4385 | 2589781.3776 | 1119485.9698 | 2589810.8487 | 1119494.235
9 | 2589783.5533 | 1119622.0329 | 2589785.9708 | 1119610.0118
10 | 2589783.5533 | 1119622.0329 | 2589807.7826 | 1119626.1875
11 | 2589740.9858 | 1119656.3778 | 2589745.0883 | 1119640.6959
12 | 2589718.6362 | 1119598.3765 | 2589735.9651 | 1119607.9746
13 | 2589841.3322 | 1119526.3658 | 2589846.3771 | 1119512.1281 | 2589848.5575 | 1119501.219
14 | 2589772.9559 | 1119483.4385 | 2589767.2464 | 1119494.8686
15 | 2589724.4162 | 1119468.3917 | 2589744.409 | 1119474.2715 | 2589772.9559 | 1119483.4385
16 | 2589823.4427 | 1119628.8728 | 2589807.7826 | 1119626.1875
17 | 2589734.5616 | 1119680.4228 | 2589737.7742 | 1119668.6671 | 2589740.9858 | 1119656.3778
18 | 2589740.9858 | 1119656.3778 | 2589729.9556 | 1119650.2832
19 | 2589718.6362 | 1119598.3765 | 2589717.0376 | 1119597.4899
20 | 2589718.6362 | 1119598.3765 | 2589702.5546 | 1119628.6776
21 | 2589761.3234 | 1119506.7262 | 2589767.2464 | 1119494.8686
22 | 2589724.4162 | 1119468.3917 | 2589718.3805 | 1119487.3414
23 | 2589691.7786 | 1119458.4205 | 2589722.6948 | 1119467.8944 | 2589724.4162 | 1119468.3917
24 | 2589823.4427 | 1119628.8728 | 2589831.8974 | 1119630.3225
25 | 2589734.5616 | 1119680.4228 | 2589761.8605 | 1119692.4639
26 | 2589734.5616 | 1119680.4228 | 2589732.925 | 1119686.3578
27 | 2589722.4762 | 1119646.1505 | 2589729.9556 | 1119650.2832
28 | 2589717.0376 | 1119597.4899 | 2589724.5489 | 1119582.2407
29 | 2589717.0376 | 1119597.4899 | 2589706.372 | 1119591.5793
30 | 2589846.2724 | 1119632.7874 | 2589850.9082 | 1119613.9259 | 2589851.3168 | 1119609.1784 | 2589852.4859 | 1119595.9629
31 | 2589846.2724 | 1119632.7874 | 2589831.8974 | 1119630.3225
32 | 2589647.508 | 1119445.0233 | 2589640.5887 | 1119442.9371
33 | 2589647.508 | 1119445.0233 | 2589671.6284 | 1119452.2925
34 | 2589641.1255 | 1119461.7981 | 2589643.5491 | 1119462.3609 | 2589646.8096 | 1119447.1367 | 2589647.508 | 1119445.0233
35 | 2589674.9426 | 1119453.2913 | 2589671.6284 | 1119452.2925
36 | 2589641.1255 | 1119461.7981 | 2589622.3103 | 1119480.9777
37 | 2589688.2662 | 1119457.3037 | 2589674.9426 | 1119453.2913
38 | 2589688.2662 | 1119457.3037 | 2589691.7786 | 1119458.4205
39 | 2589688.2662 | 1119457.3037 | 2589675.4878 | 1119501.136 | 2589666.2213 | 1119497.7738
40 | 2589691.7786 | 1119458.4205 | 2589688.1997 | 1119471.4929
41 | 2589666.2213 | 1119497.7738 | 2589648.2565 | 1119491.2555
42 | 2589683.7127 | 1119487.8821 | 2589688.1997 | 1119471.4929
43 | 2589719.5577 | 1119505.6961 | 2589719.394 | 1119500.227 | 2589716.2433 | 1119494.0516 | 2589718.3805 | 1119487.3414
44 | 2589752.1851 | 1119525.0204 | 2589761.3234 | 1119506.7262
45 | 2589611.8531 | 1119537.4302 | 2589615.1434 | 1119526.601
46 | 2589640.0377 | 1119511.0797 | 2589629.8467 | 1119507.1176 | 2589626.0964 | 1119506.7127 | 2589622.1021 | 1119508.0203 | 2589620.3456 | 1119509.4796 | 2589615.1434 | 1119526.601
47 | 2589611.8531 | 1119537.4302 | 2589639.9423 | 1119554.2251
48 | 2589649.0789 | 1119559.688 | 2589639.9423 | 1119554.2251
49 | 2589655.7514 | 1119563.4784 | 2589652.3536 | 1119561.65 | 2589649.0789 | 1119559.688
50 | 2589655.7514 | 1119563.4784 | 2589663.0125 | 1119549.7514
51 | 2589655.7514 | 1119563.4784 | 2589678.9424 | 1119576.3782
52 | 2589724.8309 | 1119581.6682 | 2589724.5489 | 1119582.2407
53 | 2589693.7002 | 1119584.5568 | 2589706.372 | 1119591.5793
54 | 2589736.9201 | 1119557.125 | 2589724.8309 | 1119581.6682
55 | 2589701.9758 | 1119569.4241 | 2589693.7002 | 1119584.5568
56 | 2589678.9424 | 1119576.3782 | 2589693.7002 | 1119584.5568
57 | 2589646.4557 | 1119676.4034 | 2589652.6965 | 1119664.8586
58 | 2589636.897 | 1119694.086 | 2589646.4557 | 1119676.4034
59 | 2589663.7388 | 1119640.9248 | 2589661.1148 | 1119649.4113 | 2589658.0153 | 1119655.0194 | 2589652.6965 | 1119664.8586
60 | 2589645.2793 | 1119696.2616 | 2589636.897 | 1119694.086
61 | 2589645.2793 | 1119696.2616 | 2589676.709 | 1119704.4226
62 | 2589645.2793 | 1119696.2616 | 2589640.2802 | 1119721.9051
63 | 2589676.709 | 1119704.4226 | 2589693.8291 | 1119709.14
64 | 2589676.709 | 1119704.4226 | 2589682.3813 | 1119691.8434
65 | 2589693.8291 | 1119709.14 | 2589701.4796 | 1119711.2491
66 | 2589693.8291 | 1119709.14 | 2589688.9072 | 1119727.5981
67 | 2589687.597 | 1119660.6936 | 2589689.5159 | 1119663.9141 | 2589690.1256 | 1119668.5709 | 2589690.1332 | 1119672.9841 | 2589689.5366 | 1119675.9755 | 2589682.3813 | 1119691.8434
68 | 2589724.3255 | 1119717.5474 | 2589701.4796 | 1119711.2491
69 | 2589724.3255 | 1119717.5474 | 2589736.8216 | 1119720.761 | 2589743.2015 | 1119722.2309
70 | 2589724.3255 | 1119717.5474 | 2589719.4714 | 1119733.3017
71 | 2589724.3255 | 1119717.5474 | 2589726.7868 | 1119708.6166 | 2589732.925 | 1119686.3578
72 | 2589761.8605 | 1119692.4639 | 2589765.3534 | 1119694.0046
73 | 2589743.2015 | 1119722.2309 | 2589777.262 | 1119730.0785
74 | 2589820.6857 | 1119740.0834 | 2589777.262 | 1119730.0785
75 | 2589820.6857 | 1119740.0834 | 2589830.8967 | 1119742.4339 | 2589836.7007 | 1119711.9313
76 | 2589678.9424 | 1119576.3782 | 2589695.4157 | 1119541.2104
77 | 2589672.7827 | 1119531.2809 | 2589663.0125 | 1119549.7514
78 | 2589836.7007 | 1119711.9313 | 2589835.4535 | 1119708.9431 | 2589833.5921 | 1119707.7123 | 2589823.5512 | 1119705.5616
79 | 2589672.7827 | 1119531.2809 | 2589680.5273 | 1119516.6397

## bus_geodata
| x | y | coords
0 | 2589784.2969 | 1119546.9092
1 | 2589771.4065 | 1119574.1224
2 | 2589799.5482 | 1119516.6531
3 | 2589751.4103 | 1119616.5294
4 | 2589810.8487 | 1119494.235
5 | 2589783.5533 | 1119622.0329
6 | 2589745.0883 | 1119640.6959
7 | 2589735.9651 | 1119607.9746
8 | 2589848.5575 | 1119501.219
9 | 2589772.9559 | 1119483.4385
10 | 2589785.9708 | 1119610.0118
11 | 2589807.7826 | 1119626.1875
12 | 2589740.9858 | 1119656.3778
13 | 2589718.6362 | 1119598.3765
14 | 2589841.3322 | 1119526.3658
15 | 2589767.2464 | 1119494.8686
16 | 2589724.4162 | 1119468.3917
17 | 2589823.4427 | 1119628.8728
18 | 2589734.5616 | 1119680.4228
19 | 2589729.9556 | 1119650.2832
20 | 2589717.0376 | 1119597.4899
21 | 2589702.5546 | 1119628.6776
22 | 2589852.4859 | 1119595.9629
23 | 2589846.2724 | 1119632.7874
24 | 2589831.8974 | 1119630.3225
25 | 2589640.5887 | 1119442.9371
26 | 2589647.508 | 1119445.0233
27 | 2589671.6284 | 1119452.2925
28 | 2589641.1255 | 1119461.7981
29 | 2589674.9426 | 1119453.2913
30 | 2589622.3103 | 1119480.9777
31 | 2589688.2662 | 1119457.3037
32 | 2589691.7786 | 1119458.4205
33 | 2589666.2213 | 1119497.7738
34 | 2589688.1997 | 1119471.4929
35 | 2589648.2565 | 1119491.2555
36 | 2589683.7127 | 1119487.8821
37 | 2589718.3805 | 1119487.3414
38 | 2589719.5577 | 1119505.6961
39 | 2589761.3234 | 1119506.7262
40 | 2589752.1851 | 1119525.0204
41 | 2589615.1434 | 1119526.601
42 | 2589611.8531 | 1119537.4302
43 | 2589640.0377 | 1119511.0797
44 | 2589639.9423 | 1119554.2251
45 | 2589649.0789 | 1119559.688
46 | 2589655.7514 | 1119563.4784
47 | 2589724.5489 | 1119582.2407
48 | 2589706.372 | 1119591.5793
49 | 2589724.8309 | 1119581.6682
50 | 2589693.7002 | 1119584.5568
51 | 2589646.4557 | 1119676.4034
52 | 2589652.6965 | 1119664.8586
53 | 2589636.897 | 1119694.086
54 | 2589663.7388 | 1119640.9248
55 | 2589645.2793 | 1119696.2616
56 | 2589676.709 | 1119704.4226
57 | 2589640.2802 | 1119721.9051
58 | 2589693.8291 | 1119709.14
59 | 2589682.3813 | 1119691.8434
60 | 2589687.597 | 1119660.6936
61 | 2589701.4796 | 1119711.2491
62 | 2589688.9072 | 1119727.5981
63 | 2589724.3255 | 1119717.5474
64 | 2589722.4762 | 1119646.1505
65 | 2589761.8605 | 1119692.4639
66 | 2589732.925 | 1119686.3578
67 | 2589743.2015 | 1119722.2309
68 | 2589719.4714 | 1119733.3017
69 | 2589777.262 | 1119730.0785
70 | 2589765.3534 | 1119694.0046
71 | 2589820.6857 | 1119740.0834
72 | 2589701.9758 | 1119569.4241
73 | 2589678.9424 | 1119576.3782
74 | 2589695.4157 | 1119541.2104
75 | 2589663.0125 | 1119549.7514
76 | 2589736.9201 | 1119557.125
77 | 2589836.7007 | 1119711.9313
78 | 2589823.5512 | 1119705.5616
79 | 2589672.7827 | 1119531.2809
80 | 2589680.5273 | 1119516.6397
81 | 2589717.0376 | 1119597.4899

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1