## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6025-29_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6025-29_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6025-29_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_6025-29_0_5_node_22 | 0.4 | n |  | TRUE
4 | bus_LV_6025-29_0_5_node_25 | 0.4 | n |  | TRUE
5 | bus_LV_6025-29_0_5_node_28 | 0.4 | n |  | TRUE
6 | bus_LV_6025-29_0_5_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_6025-29_0_5_node_37 | 0.4 | n |  | TRUE
8 | bus_LV_6025-29_0_5_node_20 | 0.4 | n |  | TRUE
9 | bus_LV_6025-29_0_5_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_6025-29_0_5_node_36 | 0.4 | n |  | TRUE
11 | bus_LV_6025-29_0_5_node_35 | 0.4 | n |  | TRUE
12 | bus_LV_6025-29_0_5_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_6025-29_0_5_node_46 | 0.4 | n |  | TRUE
14 | bus_LV_6025-29_0_5_node_41 | 0.4 | n |  | TRUE
15 | bus_LV_6025-29_0_5_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_6025-29_0_5_node_45 | 0.4 | n |  | TRUE
17 | bus_LV_6025-29_0_5_node_43 | 0.4 | n |  | TRUE
18 | bus_LV_6025-29_0_5_node_6 | 0.4 | n |  | TRUE
19 | bus_LV_6025-29_0_5_node_7 | 0.4 | n |  | TRUE
20 | bus_LV_6025-29_0_5_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_6025-29_0_5_node_76 | 0.4 | n |  | TRUE
22 | bus_LV_6025-29_0_5_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_6025-29_0_5_node_91 | 0.4 | n |  | TRUE
24 | bus_LV_6025-29_0_5_node_85 | 0.4 | n |  | TRUE
25 | bus_LV_6025-29_0_5_node_75 | 0.4 | n |  | TRUE
26 | bus_LV_6025-29_0_5_node_10 | 0.4 | n |  | TRUE
27 | bus_LV_6025-29_0_5_node_8 | 0.4 | n |  | TRUE
28 | bus_LV_6025-29_0_5_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_6025-29_0_5_node_56 | 0.4 | n |  | TRUE
30 | bus_LV_6025-29_0_5_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_6025-29_0_5_node_82 | 0.4 | n |  | TRUE
32 | bus_LV_6025-29_0_5_node_70 | 0.4 | n |  | TRUE
33 | bus_LV_6025-29_0_5_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_6025-29_0_5_node_64 | 0.4 | n |  | TRUE
35 | bus_LV_6025-29_0_5_node_61 | 0.4 | n |  | TRUE
36 | bus_LV_6025-29_0_5_node_12 | 0.4 | n |  | TRUE
37 | bus_LV_6025-29_0_5_node_44 | 0.4 | n |  | TRUE
38 | bus_LV_6025-29_0_5_node_74 | 0.4 | n |  | TRUE
39 | bus_LV_6025-29_0_5_node_98 | 0.4 | n |  | TRUE
40 | bus_LV_6025-29_0_5_node_95 | 0.4 | n |  | TRUE
41 | bus_LV_6025-29_0_5_node_50 | 0.4 | n |  | TRUE
42 | bus_LV_6025-29_0_5_node_5 | 0.4 | n |  | TRUE
43 | bus_LV_6025-29_0_5_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_6025-29_0_5_node_55 | 0.4 | n |  | TRUE
45 | bus_LV_6025-29_0_5_node_73 | 0.4 | n |  | TRUE
46 | bus_LV_6025-29_0_5_node_94 | 0.4 | n |  | TRUE
47 | bus_LV_6025-29_0_5_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_6025-29_0_5_node_84 | 0.4 | n |  | TRUE
49 | bus_LV_6025-29_0_5_node_88 | 0.4 | n |  | TRUE
50 | bus_LV_6025-29_0_5_node_69 | 0.4 | n |  | TRUE
51 | bus_LV_6025-29_0_5_node_83 | 0.4 | n |  | TRUE
52 | bus_LV_6025-29_0_5_node_92 | 0.4 | n |  | TRUE
53 | bus_LV_6025-29_0_5_node_71 | 0.4 | n |  | TRUE
54 | bus_LV_6025-29_0_5_node_97 | 0.4 | n |  | TRUE
55 | bus_LV_6025-29_0_5_node_62 | 0.4 | n |  | TRUE
56 | bus_LV_6025-29_0_5_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_6025-29_0_5_node_38 | 0.4 | n |  | TRUE
58 | bus_LV_6025-29_0_5_node_27 | 0.4 | n |  | TRUE
59 | bus_LV_6025-29_0_5_node_32 | 0.4 | n |  | TRUE
60 | bus_LV_6025-29_0_5_node_29 | 0.4 | n |  | TRUE
61 | bus_LV_6025-29_0_5_node_51 | 0.4 | n |  | TRUE
62 | bus_LV_6025-29_0_5_node_26 | 0.4 | n |  | TRUE
63 | bus_LV_6025-29_0_5_node_30 | 0.4 | n |  | TRUE
64 | bus_LV_6025-29_0_5_node_31 | 0.4 | n |  | TRUE
65 | bus_LV_6025-29_0_5_node_33 | 0.4 | n |  | TRUE
66 | bus_LV_6025-29_0_5_node_34 | 0.4 | n |  | TRUE
67 | bus_LV_6025-29_0_5_node_58 | 0.4 | n |  | TRUE
68 | bus_LV_6025-29_0_5_node_52 | 0.4 | n |  | TRUE
69 | bus_LV_6025-29_0_5_node_59 | 0.4 | n |  | TRUE
70 | bus_LV_6025-29_0_5_node_53 | 0.4 | n |  | TRUE
71 | bus_LV_6025-29_0_5_node_39 | 0.4 | n |  | TRUE
72 | bus_LV_6025-29_0_5_node_40 | 0.4 | n |  | TRUE
73 | bus_LV_6025-29_0_5_node_49 | 0.4 | n |  | TRUE
74 | bus_LV_6025-29_0_5_node_48 | 0.4 | n |  | TRUE
75 | bus_LV_6025-29_0_5_node_54 | 0.4 | n |  | TRUE
76 | bus_LV_6025-29_0_5_node_57 | 0.4 | n |  | TRUE
77 | bus_LV_6025-29_0_5_node_81 | 0.4 | n |  | TRUE
78 | bus_LV_6025-29_0_5_node_79 | 0.4 | n |  | TRUE
79 | bus_LV_6025-29_0_5_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_6025-29_0_5_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_6025-29_0_5_node_66 | 0.4 | n |  | TRUE
82 | bus_LV_6025-29_0_5_node_63 | 0.4 | n |  | TRUE
83 | bus_LV_6025-29_0_5_node_65 | 0.4 | n |  | TRUE
84 | bus_LV_6025-29_0_5_node_72 | 0.4 | n |  | TRUE
85 | bus_LV_6025-29_0_5_node_77 | 0.4 | n |  | TRUE
86 | bus_LV_6025-29_0_5_node_78 | 0.4 | n |  | TRUE
87 | bus_LV_6025-29_0_5_node_80 | 0.4 | n |  | TRUE
88 | bus_LV_6025-29_0_5_node_90 | 0.4 | n |  | TRUE
89 | bus_LV_6025-29_0_5_node_93 | 0.4 | n |  | TRUE
90 | bus_LV_6025-29_0_5_node_89 | 0.4 | n |  | TRUE
91 | bus_LV_6025-29_0_5_node_86 | 0.4 | n |  | TRUE
92 | bus_LV_6025-29_0_5_node_87 | 0.4 | n |  | TRUE
93 | bus_LV_6025-29_0_5_node_96 | 0.4 | n |  | TRUE
94 | bus_MV_267_0_node_30 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6025-29_0_5_load_0 | 0 | 0.01494 | 0.0037442 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6025-29_0_5_load_1 | 1 | 0.0098366 | 0.0024653 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6025-29_0_5_load_25 | 4 | 0.0038994 | 0.00097728 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6025-29_0_5_load_28 | 5 | 0.024723 | 0.0061961 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6025-29_0_5_load_37 | 7 | 0.011483 | 0.002878 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6025-29_0_5_load_36 | 10 | 0.0097555 | 0.002445 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6025-29_0_5_load_35 | 11 | 0.0029183 | 0.00073139 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6025-29_0_5_load_46 | 13 | 0.065942 | 0.016527 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6025-29_0_5_load_41 | 14 | 0.012208 | 0.0030597 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6025-29_0_5_load_45 | 16 | 0.01736 | 0.0043509 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6025-29_0_5_load_43 | 17 | 0.017419 | 0.0043656 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6025-29_0_5_load_76 | 21 | 0.011375 | 0.0028507 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6025-29_0_5_load_85 | 24 | 0.011604 | 0.0029082 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6025-29_0_5_load_75 | 25 | 0.0073077 | 0.0018315 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6025-29_0_5_load_56 | 29 | 0.0075176 | 0.0018841 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6025-29_0_5_load_70 | 32 | 0.0036772 | 0.00092159 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6025-29_0_5_load_61 | 35 | 0.0041407 | 0.0010378 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6025-29_0_5_load_74 | 38 | 0.0036515 | 0.00091514 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6025-29_0_5_load_98 | 39 | 0.0081008 | 0.0020303 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6025-29_0_5_load_95 | 40 | 0.0036448 | 0.00091346 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6025-29_0_5_load_50 | 41 | 0.0094085 | 0.002358 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6025-29_0_5_load_5 | 42 | 0.002827 | 0.00070852 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6025-29_0_5_load_24 | 43 | 0.0064167 | 0.0016082 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6025-29_0_5_load_73 | 45 | 0.0079771 | 0.0019992 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6025-29_0_5_load_84 | 48 | 0.010474 | 0.002625 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6025-29_0_5_load_88 | 49 | 0.0018005 | 0.00045124 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6025-29_0_5_load_69 | 50 | 0.016271 | 0.0040779 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6025-29_0_5_load_83 | 51 | 0.0052973 | 0.0013276 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6025-29_0_5_load_92 | 52 | 0.0060889 | 0.001526 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6025-29_0_5_load_97 | 54 | 0.006231 | 0.0015616 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6025-29_0_5_load_62 | 55 | 0.0022607 | 0.00056658 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6025-29_0_5_load_27 | 58 | 0.0077654 | 0.0019462 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6025-29_0_5_load_29 | 60 | 0.0074283 | 0.0018617 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6025-29_0_5_load_51 | 61 | 0.0065203 | 0.0016341 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6025-29_0_5_load_26 | 62 | 0.0061911 | 0.0015516 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6025-29_0_5_load_30 | 63 | 0.0086267 | 0.0021621 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6025-29_0_5_load_31 | 64 | 0.0030332 | 0.0007602 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6025-29_0_5_load_33 | 65 | 0.003963 | 0.00099323 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6025-29_0_5_load_34 | 66 | 0.0031274 | 0.0007838 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6025-29_0_5_load_58 | 67 | 0.0035848 | 0.00089842 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6025-29_0_5_load_52 | 68 | 0.0026723 | 0.00066974 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6025-29_0_5_load_59 | 69 | 0.0045592 | 0.0011426 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6025-29_0_5_load_53 | 70 | 0.0036698 | 0.00091975 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6025-29_0_5_load_39 | 71 | 0.014895 | 0.003733 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6025-29_0_5_load_40 | 72 | 0.026178 | 0.0065609 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6025-29_0_5_load_49 | 73 | 0.004596 | 0.0011519 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6025-29_0_5_load_54 | 75 | 0.0027363 | 0.00068579 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6025-29_0_5_load_81 | 77 | 0.0045793 | 0.0011477 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6025-29_0_5_load_79 | 78 | 0.0020824 | 0.0005219 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6025-29_0_5_load_60 | 79 | 0.0049008 | 0.0012283 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6025-29_0_5_load_67 | 80 | 0.010908 | 0.0027337 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6025-29_0_5_load_66 | 81 | 0.0034369 | 0.00086138 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6025-29_0_5_load_63 | 82 | 0.0032544 | 0.00081564 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6025-29_0_5_load_65 | 83 | 0.002547 | 0.00063834 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6025-29_0_5_load_72 | 84 | 0.01292 | 0.003238 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6025-29_0_5_load_77 | 85 | 0.0050215 | 0.0012585 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6025-29_0_5_load_78 | 86 | 0.0027786 | 0.00069637 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6025-29_0_5_load_80 | 87 | 0.0072122 | 0.0018075 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6025-29_0_5_load_93 | 89 | 0.0082334 | 0.0020635 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6025-29_0_5_load_89 | 90 | 0.0017658 | 0.00044256 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6025-29_0_5_load_86 | 91 | 0.0030771 | 0.00077118 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6025-29_0_5_load_87 | 92 | 0.0029615 | 0.00074223 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6025-29_0_5_load_96 | 93 | 0.0065248 | 0.0016353 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 73 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6025-29_0_5_line_0 |  | 0 | 1 | 0.047718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6025-29_0_5_line_1 |  | 1 | 2 | 0.016274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6025-29_0_5_line_2 |  | 2 | 3 | 0.049286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6025-29_0_5_line_3 |  | 2 | 4 | 0.043112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6025-29_0_5_line_4 |  | 3 | 5 | 0.037188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6025-29_0_5_line_5 |  | 4 | 43 | 0.0025012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6025-29_0_5_line_6 |  | 5 | 60 | 0.044318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6025-29_0_5_line_7 |  | 6 | 7 | 0.014344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6025-29_0_5_line_8 |  | 6 | 8 | 0.032703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_6025-29_0_5_line_9 |  | 6 | 9 | 0.020487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_6025-29_0_5_line_10 |  | 6 | 10 | 0.014009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6025-29_0_5_line_11 |  | 7 | 57 | 0.011028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6025-29_0_5_line_12 |  | 8 | 14 | 0.047681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6025-29_0_5_line_13 |  | 8 | 12 | 0.019585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_6025-29_0_5_line_14 |  | 9 | 11 | 0.021664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_6025-29_0_5_line_15 |  | 10 | 58 | 0.014836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6025-29_0_5_line_16 |  | 11 | 59 | 0.010694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_6025-29_0_5_line_17 |  | 12 | 13 | 0.013738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_6025-29_0_5_line_18 |  | 13 | 56 | 0.019968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_6025-29_0_5_line_19 |  | 15 | 16 | 0.018171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6025-29_0_5_line_20 |  | 15 | 17 | 0.029982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6025-29_0_5_line_21 |  | 15 | 18 | 0.009826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6025-29_0_5_line_22 |  | 17 | 47 | 0.027903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6025-29_0_5_line_23 |  | 18 | 42 | 0.015337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6025-29_0_5_line_24 |  | 19 | 20 | 0.010382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6025-29_0_5_line_25 |  | 19 | 21 | 0.014127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6025-29_0_5_line_26 |  | 20 | 25 | 0.012295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6025-29_0_5_line_27 |  | 20 | 26 | 0.059154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6025-29_0_5_line_28 |  | 22 | 23 | 0.018246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6025-29_0_5_line_29 |  | 22 | 24 | 0.0083943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6025-29_0_5_line_30 |  | 23 | 52 | 0.0079396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6025-29_0_5_line_31 |  | 26 | 39 | 0.025925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6025-29_0_5_line_32 |  | 26 | 40 | 0.0031494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6025-29_0_5_line_33 |  | 27 | 28 | 0.033747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6025-29_0_5_line_34 |  | 27 | 29 | 0.055539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6025-29_0_5_line_35 |  | 28 | 41 | 0.013943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6025-29_0_5_line_36 |  | 29 | 44 | 0.023145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6025-29_0_5_line_37 |  | 30 | 31 | 0.016584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_6025-29_0_5_line_38 |  | 30 | 32 | 0.012262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_6025-29_0_5_line_39 |  | 31 | 48 | 0.014671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6025-29_0_5_line_40 |  | 31 | 49 | 0.0091921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_6025-29_0_5_line_41 |  | 32 | 50 | 0.044101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_6025-29_0_5_line_42 |  | 33 | 34 | 0.002081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_6025-29_0_5_line_43 |  | 33 | 35 | 0.017958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_6025-29_0_5_line_44 |  | 34 | 53 | 0.012375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_6025-29_0_5_line_45 |  | 34 | 54 | 0.046856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6025-29_0_5_line_46 |  | 35 | 55 | 0.01563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_6025-29_0_5_line_47 |  | 36 | 37 | 0.023036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6025-29_0_5_line_48 |  | 36 | 38 | 0.012345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6025-29_0_5_line_49 |  | 37 | 47 | 0.003086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6025-29_0_5_line_50 |  | 37 | 45 | 0.0060738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6025-29_0_5_line_51 |  | 40 | 46 | 0.0057998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6025-29_0_5_line_52 |  | 41 | 61 | 0.0095546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6025-29_0_5_line_53 |  | 43 | 62 | 0.0090622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6025-29_0_5_line_54 |  | 44 | 76 | 0.005972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6025-29_0_5_line_55 |  | 46 | 93 | 0.028809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6025-29_0_5_line_56 |  | 46 | 89 | 0.0070638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6025-29_0_5_line_57 |  | 47 | 71 | 0.0096261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6025-29_0_5_line_58 |  | 48 | 51 | 0.0035777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6025-29_0_5_line_59 |  | 49 | 91 | 0.013267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_6025-29_0_5_line_60 |  | 50 | 53 | 0.0083425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_6025-29_0_5_line_61 |  | 52 | 88 | 0.016208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6025-29_0_5_line_62 |  | 53 | 84 | 0.032703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6025-29_0_5_line_63 |  | 54 | 76 | 0.017977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6025-29_0_5_line_64 |  | 55 | 82 | 0.021318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_6025-29_0_5_line_65 |  | 56 | 73 | 0.036812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_6025-29_0_5_line_66 |  | 57 | 71 | 0.043809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6025-29_0_5_line_67 |  | 57 | 72 | 0.007042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6025-29_0_5_line_68 |  | 58 | 62 | 0.020534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6025-29_0_5_line_69 |  | 59 | 66 | 0.023191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6025-29_0_5_line_70 |  | 59 | 63 | 0.038806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_6025-29_0_5_line_71 |  | 63 | 64 | 0.024889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_6025-29_0_5_line_72 |  | 64 | 65 | 0.0043221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_6025-29_0_5_line_73 |  | 65 | 67 | 0.02547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_6025-29_0_5_line_74 |  | 66 | 68 | 0.010405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_6025-29_0_5_line_75 |  | 67 | 69 | 0.01909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_6025-29_0_5_line_76 |  | 68 | 70 | 0.015707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_6025-29_0_5_line_77 |  | 69 | 79 | 0.027534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_6025-29_0_5_line_78 |  | 70 | 74 | 0.0018053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_6025-29_0_5_line_79 |  | 74 | 75 | 0.021995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_6025-29_0_5_line_80 |  | 77 | 78 | 0.0097535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_6025-29_0_5_line_81 |  | 78 | 85 | 0.0020592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_6025-29_0_5_line_82 |  | 79 | 80 | 0.025928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
83 | LV_6025-29_0_5_line_83 |  | 80 | 81 | 0.031491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
84 | LV_6025-29_0_5_line_84 |  | 81 | 83 | 0.0022952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_6025-29_0_5_line_85 |  | 82 | 83 | 0.022855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
86 | LV_6025-29_0_5_line_86 |  | 85 | 86 | 0.0053258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_6025-29_0_5_line_87 |  | 86 | 87 | 0.014759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_6025-29_0_5_line_88 |  | 87 | 88 | 0.013153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_6025-29_0_5_line_89 |  | 88 | 89 | 0.0098784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_6025-29_0_5_line_90 |  | 88 | 90 | 0.0093501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
91 | LV_6025-29_0_5_line_91 |  | 90 | 92 | 0.0044178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
92 | LV_6025-29_0_5_line_92 |  | 91 | 92 | 0.009708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6025-29_0_5_trafo_49 | 0.63 MVA 20/0.4 kV | 94 | 73 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2587567.5719 | 1119298.6094 | 2587546.0657 | 1119341.2061
1 | 2587538.9508 | 1119355.8233 | 2587539.3877 | 1119354.4329 | 2587546.0657 | 1119341.2061
2 | 2587499.5307 | 1119355.0381 | 2587502.0653 | 1119349.4856 | 2587513.8873 | 1119354.0744 | 2587525.106 | 1119357.9864 | 2587537.1265 | 1119361.6077 | 2587538.9508 | 1119355.8233
3 | 2587538.9508 | 1119355.8233 | 2587551.719 | 1119359.0763 | 2587560.5648 | 1119360.9367 | 2587568.8929 | 1119362.4424 | 2587575.9547 | 1119363.4506 | 2587581.2079 | 1119364.1524
4 | 2587499.5307 | 1119355.0381 | 2587500.7122 | 1119355.5136 | 2587510.797 | 1119359.5502 | 2587516.5261 | 1119361.5838 | 2587523.6836 | 1119364.0924 | 2587531.1341 | 1119366.5559 | 2587534.5531 | 1119367.4761
5 | 2587583.6871 | 1119364.4837 | 2587581.2079 | 1119364.1524
6 | 2587534.5531 | 1119367.4761 | 2587538.5529 | 1119368.5526 | 2587545.7087 | 1119370.2942 | 2587554.848 | 1119372.2874 | 2587565.4147 | 1119374.3555 | 2587572.716 | 1119375.541 | 2587577.9701 | 1119376.1792
7 | 2587642.0502 | 1119365.7267 | 2587642.009 | 1119364.4484 | 2587642.9447 | 1119361.7673 | 2587648.2537 | 1119353.0278
8 | 2587642.0502 | 1119365.7267 | 2587651.2301 | 1119365.0297 | 2587671.718 | 1119362.8755 | 2587674.4546 | 1119361.6693
9 | 2587634.0306 | 1119379.2053 | 2587634.3204 | 1119377.5261 | 2587634.501 | 1119371.5895 | 2587642.2226 | 1119370.8066 | 2587642.0502 | 1119365.7267
10 | 2587642.0502 | 1119365.7267 | 2587635.9173 | 1119366.184 | 2587628.0584 | 1119366.249
11 | 2587653.9792 | 1119343.6024 | 2587648.2537 | 1119353.0278
12 | 2587674.4546 | 1119361.6693 | 2587682.5331 | 1119358.1177 | 2587697.1043 | 1119356.4871 | 2587700.4138 | 1119356.2246 | 2587703.2069 | 1119356.2745 | 2587705.2985 | 1119356.6593 | 2587707.19 | 1119357.2335 | 2587711.1733 | 1119358.2481 | 2587713.2647 | 1119358.4995 | 2587720.9952 | 1119357.8213
13 | 2587674.4546 | 1119361.6693 | 2587675.238 | 1119367.4817 | 2587675.9667 | 1119372.9162 | 2587684.1274 | 1119371.7989
14 | 2587634.0306 | 1119379.2053 | 2587633.4323 | 1119380.9185 | 2587632.3494 | 1119383.3219 | 2587625.6906 | 1119394.4077 | 2587623.4946 | 1119398.083
15 | 2587628.0584 | 1119366.249 | 2587626.9906 | 1119366.2579 | 2587620.0544 | 1119366.2499 | 2587613.2226 | 1119366.1582
16 | 2587618.0094 | 1119407.2632 | 2587623.4946 | 1119398.083
17 | 2587684.1274 | 1119371.7989 | 2587684.3959 | 1119378.6129 | 2587684.3401 | 1119385.2273 | 2587684.2758 | 1119385.5244
18 | 2587679.1489 | 1119404.7142 | 2587679.7325 | 1119403.379 | 2587680.0893 | 1119400.5324 | 2587682.0013 | 1119396.0485 | 2587684.2758 | 1119385.5244
19 | 2587640.7845 | 1119297.9849 | 2587649.3729 | 1119283.4601 | 2587650.1114 | 1119282.3803
20 | 2587650.1114 | 1119282.3803 | 2587659.7958 | 1119290.5533 | 2587672.6033 | 1119302.1985
21 | 2587650.1114 | 1119282.3803 | 2587642.8528 | 1119275.7364
22 | 2587693.8206 | 1119320.2871 | 2587691.2321 | 1119318.4248 | 2587685.3587 | 1119313.7234 | 2587679.9479 | 1119308.8766 | 2587672.6033 | 1119302.1985
23 | 2587642.8528 | 1119275.7364 | 2587636.9006 | 1119270.2792 | 2587631.3603 | 1119265.5841
24 | 2587852.0245 | 1119425.6396 | 2587861.9911 | 1119428.6432
25 | 2587852.0245 | 1119425.6396 | 2587838.4574 | 1119421.7003
26 | 2587861.9911 | 1119428.6432 | 2587857.8977 | 1119440.2372
27 | 2587861.9911 | 1119428.6432 | 2587888.0592 | 1119435.1939 | 2587876.3385 | 1119465.2656
28 | 2587918.2625 | 1119499.2313 | 2587909.9334 | 1119497.0914 | 2587900.3785 | 1119495.432
29 | 2587918.2625 | 1119499.2313 | 2587914.5908 | 1119506.78
30 | 2587900.3785 | 1119495.432 | 2587896.4809 | 1119494.7506 | 2587892.5778 | 1119493.9572
31 | 2587876.3385 | 1119465.2656 | 2587851.4797 | 1119457.6676
32 | 2587876.3385 | 1119465.2656 | 2587876.0298 | 1119468.3998
33 | 2587730.6013 | 1119377.3623 | 2587734.3676 | 1119374.1419 | 2587738.7192 | 1119370.4201 | 2587746.3633 | 1119392.1819
34 | 2587746.3633 | 1119392.1819 | 2587753.3741 | 1119413.6337 | 2587761.2705 | 1119438.1297 | 2587763.7599 | 1119444.921
35 | 2587730.6013 | 1119377.3623 | 2587731.8217 | 1119381.8175 | 2587732.1067 | 1119385.352 | 2587729.5251 | 1119390.5209
36 | 2587771.3665 | 1119466.7788 | 2587769.3328 | 1119460.7577 | 2587766.0264 | 1119451.1042 | 2587763.7599 | 1119444.921
37 | 2587868.1924 | 1119550.0348 | 2587877.3224 | 1119536.1762
38 | 2587868.1924 | 1119550.0348 | 2587857.3334 | 1119544.3396
39 | 2587877.3224 | 1119536.1762 | 2587891.9055 | 1119537.7807
40 | 2587877.3224 | 1119536.1762 | 2587879.3113 | 1119531.5588 | 2587879.586 | 1119527.4033
41 | 2587814.5779 | 1119535.3014 | 2587817.4815 | 1119535.4968 | 2587821.2239 | 1119535.756 | 2587830.5762 | 1119536.4485 | 2587839.0575 | 1119537.5764 | 2587847.1251 | 1119540.128 | 2587857.0861 | 1119544.2099 | 2587857.3334 | 1119544.3396
42 | 2587793.8846 | 1119533.7215 | 2587791.8012 | 1119533.5923
43 | 2587791.8012 | 1119533.5923 | 2587773.8591 | 1119532.8358
44 | 2587793.8846 | 1119533.7215 | 2587806.2542 | 1119534.7414
45 | 2587793.8846 | 1119533.7215 | 2587793.6374 | 1119529.7534 | 2587792.5561 | 1119525.3757 | 2587780.0018 | 1119489.1161
46 | 2587773.8591 | 1119532.8358 | 2587768.6611 | 1119532.6166 | 2587758.241 | 1119532.2339
47 | 2587695.3891 | 1119317.6271 | 2587688.4957 | 1119312.1607 | 2587677.6595 | 1119302.8672
48 | 2587677.6595 | 1119302.8672 | 2587680.6772 | 1119299.5816 | 2587684.2573 | 1119292.557
49 | 2587695.3891 | 1119317.6271 | 2587693.8206 | 1119320.2871
50 | 2587695.3891 | 1119317.6271 | 2587700.5595 | 1119320.8143
51 | 2587875.4614 | 1119474.1717 | 2587876.0298 | 1119468.3998
52 | 2587729.5251 | 1119390.5209 | 2587725.256 | 1119399.0688
53 | 2587583.6871 | 1119364.4837 | 2587584.7219 | 1119364.6219 | 2587592.7098 | 1119365.3179
54 | 2587773.4764 | 1119472.3661 | 2587771.3665 | 1119466.7788
55 | 2587847.8082 | 1119465.8234 | 2587875.4614 | 1119474.1717
56 | 2587875.4614 | 1119474.1717 | 2587875.545 | 1119481.235
57 | 2587693.8206 | 1119320.2871 | 2587688.9245 | 1119328.575
58 | 2587895.4618 | 1119538.172 | 2587891.9055 | 1119537.7807
59 | 2587879.6176 | 1119514.1406 | 2587879.7082 | 1119525.5551 | 2587879.586 | 1119527.4033
60 | 2587806.2542 | 1119534.7414 | 2587814.5779 | 1119535.3014
61 | 2587876.6449 | 1119490.9887 | 2587889.4416 | 1119493.3196 | 2587892.5778 | 1119493.9572
62 | 2587816.7479 | 1119565.6353 | 2587815.8634 | 1119563.2137 | 2587806.6154 | 1119537.8533 | 2587806.2542 | 1119534.7414
63 | 2587773.4764 | 1119472.3661 | 2587779.4635 | 1119487.5614 | 2587780.0018 | 1119489.1161
64 | 2587758.241 | 1119532.2339 | 2587737.1188 | 1119531.458 | 2587736.9379 | 1119531.4483
65 | 2587679.1489 | 1119404.7142 | 2587681.1954 | 1119405.666 | 2587686.7846 | 1119407.222 | 2587692.4997 | 1119410.0006 | 2587696.7611 | 1119411.2036 | 2587699.8012 | 1119411.3196 | 2587701.9807 | 1119409.3809 | 2587704.0407 | 1119405.6193 | 2587705.371 | 1119403.4377 | 2587707.1894 | 1119402.2223 | 2587710.1046 | 1119401.6049
66 | 2587653.9792 | 1119343.6024 | 2587670.7651 | 1119342.1562 | 2587675.3042 | 1119343.2919 | 2587677.3813 | 1119344.0991 | 2587678.1451 | 1119344.0976 | 2587679.2942 | 1119343.8284 | 2587680.6573 | 1119342.5695 | 2587688.9245 | 1119328.575
67 | 2587657.6394 | 1119337.5809 | 2587653.9792 | 1119343.6024
68 | 2587592.7098 | 1119365.3179 | 2587592.948 | 1119365.3387 | 2587598.3728 | 1119365.7165 | 2587611.4437 | 1119366.1343 | 2587613.2226 | 1119366.1582
69 | 2587618.0094 | 1119407.2632 | 2587632.8339 | 1119416.326 | 2587637.7287 | 1119419.4668
70 | 2587618.0094 | 1119407.2632 | 2587614.9869 | 1119411.9606 | 2587597.7184 | 1119440.34
71 | 2587600.7388 | 1119462.1359 | 2587595.9673 | 1119456.3327 | 2587594.1315 | 1119452.8125 | 2587593.7916 | 1119448.8669 | 2587594.688 | 1119445.7968 | 2587596.0096 | 1119443.1484 | 2587597.7184 | 1119440.34
72 | 2587603.4837 | 1119465.4745 | 2587600.7388 | 1119462.1359
73 | 2587620.6646 | 1119484.272 | 2587604.9551 | 1119467.264 | 2587603.4837 | 1119465.4745
74 | 2587646.4862 | 1119425.086 | 2587637.7287 | 1119419.4668
75 | 2587620.6646 | 1119484.272 | 2587625.4928 | 1119489.4993 | 2587634.5095 | 1119497.3785
76 | 2587646.4862 | 1119425.086 | 2587659.706 | 1119433.5684
77 | 2587657.8404 | 1119511.8222 | 2587655.6264 | 1119510.8701 | 2587646.7438 | 1119505.9637 | 2587637.5117 | 1119500.002 | 2587634.5095 | 1119497.3785
78 | 2587661.2254 | 1119434.5434 | 2587659.706 | 1119433.5684
79 | 2587661.2254 | 1119434.5434 | 2587663.4427 | 1119435.9729 | 2587668.9732 | 1119439.0186 | 2587675.5753 | 1119441.7175 | 2587681.2499 | 1119443.37
80 | 2587841.6874 | 1119489.9902 | 2587832.2758 | 1119487.4306
81 | 2587843.6744 | 1119490.5305 | 2587841.6874 | 1119489.9902
82 | 2587681.654 | 1119522.0771 | 2587674.3834 | 1119518.9356 | 2587657.8404 | 1119511.8222
83 | 2587711.8239 | 1119530.0947 | 2587703.9318 | 1119529.6693 | 2587697.3242 | 1119528.0598 | 2587688.6462 | 1119525.0984 | 2587681.654 | 1119522.0771
84 | 2587714.1158 | 1119530.2182 | 2587711.8239 | 1119530.0947
85 | 2587736.9379 | 1119531.4483 | 2587714.1158 | 1119530.2182
86 | 2587843.6744 | 1119490.5305 | 2587844.9811 | 1119490.8859 | 2587848.8827 | 1119491.6282
87 | 2587848.8827 | 1119491.6282 | 2587851.4567 | 1119492.1179 | 2587857.5143 | 1119492.6726 | 2587863.5336 | 1119492.0059
88 | 2587876.6449 | 1119490.9887 | 2587866.4081 | 1119491.6875 | 2587863.5336 | 1119492.0059
89 | 2587876.6449 | 1119490.9887 | 2587875.6102 | 1119486.7443 | 2587875.545 | 1119481.235
90 | 2587876.6449 | 1119490.9887 | 2587877.909 | 1119494.1877 | 2587878.4844 | 1119500.0701
91 | 2587878.9165 | 1119504.4667 | 2587878.8385 | 1119503.6905 | 2587878.4844 | 1119500.0701
92 | 2587879.6176 | 1119514.1406 | 2587879.5944 | 1119511.2149 | 2587878.9165 | 1119504.4667

## bus_geodata
| x | y | coords
0 | 2587567.5719 | 1119298.6094
1 | 2587546.0657 | 1119341.2061
2 | 2587538.9508 | 1119355.8233
3 | 2587499.5307 | 1119355.0381
4 | 2587581.2079 | 1119364.1524
5 | 2587534.5531 | 1119367.4761
6 | 2587642.0502 | 1119365.7267
7 | 2587648.2537 | 1119353.0278
8 | 2587674.4546 | 1119361.6693
9 | 2587634.0306 | 1119379.2053
10 | 2587628.0584 | 1119366.249
11 | 2587623.4946 | 1119398.083
12 | 2587684.1274 | 1119371.7989
13 | 2587684.2758 | 1119385.5244
14 | 2587720.9952 | 1119357.8213
15 | 2587650.1114 | 1119282.3803
16 | 2587640.7845 | 1119297.9849
17 | 2587672.6033 | 1119302.1985
18 | 2587642.8528 | 1119275.7364
19 | 2587852.0245 | 1119425.6396
20 | 2587861.9911 | 1119428.6432
21 | 2587838.4574 | 1119421.7003
22 | 2587918.2625 | 1119499.2313
23 | 2587900.3785 | 1119495.432
24 | 2587914.5908 | 1119506.78
25 | 2587857.8977 | 1119440.2372
26 | 2587876.3385 | 1119465.2656
27 | 2587746.3633 | 1119392.1819
28 | 2587730.6013 | 1119377.3623
29 | 2587763.7599 | 1119444.921
30 | 2587868.1924 | 1119550.0348
31 | 2587877.3224 | 1119536.1762
32 | 2587857.3334 | 1119544.3396
33 | 2587791.8012 | 1119533.5923
34 | 2587793.8846 | 1119533.7215
35 | 2587773.8591 | 1119532.8358
36 | 2587677.6595 | 1119302.8672
37 | 2587695.3891 | 1119317.6271
38 | 2587684.2573 | 1119292.557
39 | 2587851.4797 | 1119457.6676
40 | 2587876.0298 | 1119468.3998
41 | 2587729.5251 | 1119390.5209
42 | 2587631.3603 | 1119265.5841
43 | 2587583.6871 | 1119364.4837
44 | 2587771.3665 | 1119466.7788
45 | 2587700.5595 | 1119320.8143
46 | 2587875.4614 | 1119474.1717
47 | 2587693.8206 | 1119320.2871
48 | 2587891.9055 | 1119537.7807
49 | 2587879.586 | 1119527.4033
50 | 2587814.5779 | 1119535.3014
51 | 2587895.4618 | 1119538.172
52 | 2587892.5778 | 1119493.9572
53 | 2587806.2542 | 1119534.7414
54 | 2587780.0018 | 1119489.1161
55 | 2587758.241 | 1119532.2339
56 | 2587679.1489 | 1119404.7142
57 | 2587653.9792 | 1119343.6024
58 | 2587613.2226 | 1119366.1582
59 | 2587618.0094 | 1119407.2632
60 | 2587577.9701 | 1119376.1792
61 | 2587725.256 | 1119399.0688
62 | 2587592.7098 | 1119365.3179
63 | 2587597.7184 | 1119440.34
64 | 2587600.7388 | 1119462.1359
65 | 2587603.4837 | 1119465.4745
66 | 2587637.7287 | 1119419.4668
67 | 2587620.6646 | 1119484.272
68 | 2587646.4862 | 1119425.086
69 | 2587634.5095 | 1119497.3785
70 | 2587659.706 | 1119433.5684
71 | 2587688.9245 | 1119328.575
72 | 2587657.6394 | 1119337.5809
73 | 2587710.1046 | 1119401.6049
74 | 2587661.2254 | 1119434.5434
75 | 2587681.2499 | 1119443.37
76 | 2587773.4764 | 1119472.3661
77 | 2587832.2758 | 1119487.4306
78 | 2587841.6874 | 1119489.9902
79 | 2587657.8404 | 1119511.8222
80 | 2587681.654 | 1119522.0771
81 | 2587711.8239 | 1119530.0947
82 | 2587736.9379 | 1119531.4483
83 | 2587714.1158 | 1119530.2182
84 | 2587816.7479 | 1119565.6353
85 | 2587843.6744 | 1119490.5305
86 | 2587848.8827 | 1119491.6282
87 | 2587863.5336 | 1119492.0059
88 | 2587876.6449 | 1119490.9887
89 | 2587875.545 | 1119481.235
90 | 2587878.4844 | 1119500.0701
91 | 2587879.6176 | 1119514.1406
92 | 2587878.9165 | 1119504.4667
93 | 2587847.8082 | 1119465.8234
94 | 2587712.906 | 1119401.966

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1