## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6136-38_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6136-38_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6136-38_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6136-38_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6136-38_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6136-38_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6136-38_0_4_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_6136-38_0_4_node_47 | 0.4 | n |  | TRUE
8 | bus_LV_6136-38_0_4_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_6136-38_0_4_node_24 | 0.4 | n |  | TRUE
10 | bus_LV_6136-38_0_4_node_50 | 0.4 | n |  | TRUE
11 | bus_LV_6136-38_0_4_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_6136-38_0_4_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_6136-38_0_4_node_60 | 0.4 | n |  | TRUE
14 | bus_LV_6136-38_0_4_node_56 | 0.4 | n |  | TRUE
15 | bus_LV_6136-38_0_4_node_49 | 0.4 | n |  | TRUE
16 | bus_LV_6136-38_0_4_node_6 | 0.4 | n |  | TRUE
17 | bus_LV_6136-38_0_4_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_6136-38_0_4_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_6136-38_0_4_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_6136-38_0_4_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_6136-38_0_4_node_57 | 0.4 | n |  | TRUE
22 | bus_LV_6136-38_0_4_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_6136-38_0_4_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_6136-38_0_4_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_6136-38_0_4_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_6136-38_0_4_node_76 | 0.4 | n |  | TRUE
27 | bus_LV_6136-38_0_4_node_73 | 0.4 | n |  | TRUE
28 | bus_LV_6136-38_0_4_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_6136-38_0_4_node_71 | 0.4 | n |  | TRUE
30 | bus_LV_6136-38_0_4_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_6136-38_0_4_node_70 | 0.4 | n |  | TRUE
32 | bus_LV_6136-38_0_4_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_6136-38_0_4_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_6136-38_0_4_node_72 | 0.4 | n |  | TRUE
35 | bus_LV_6136-38_0_4_node_55 | 0.4 | n |  | TRUE
36 | bus_LV_6136-38_0_4_node_38 | 0.4 | n |  | TRUE
37 | bus_LV_6136-38_0_4_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_6136-38_0_4_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_6136-38_0_4_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_6136-38_0_4_node_75 | 0.4 | n |  | TRUE
41 | bus_LV_6136-38_0_4_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_6136-38_0_4_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_6136-38_0_4_node_54 | 0.4 | n |  | TRUE
44 | bus_LV_6136-38_0_4_node_51 | 0.4 | n |  | TRUE
45 | bus_LV_6136-38_0_4_node_34 | 0.4 | n |  | TRUE
46 | bus_LV_6136-38_0_4_node_52 | 0.4 | n |  | TRUE
47 | bus_LV_6136-38_0_4_node_66 | 0.4 | n |  | TRUE
48 | bus_LV_6136-38_0_4_node_63 | 0.4 | n |  | TRUE
49 | bus_LV_6136-38_0_4_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_6136-38_0_4_node_26 | 0.4 | n |  | TRUE
51 | bus_LV_6136-38_0_4_node_27 | 0.4 | n |  | TRUE
52 | bus_LV_6136-38_0_4_node_58 | 0.4 | n |  | TRUE
53 | bus_LV_6136-38_0_4_node_31 | 0.4 | n |  | TRUE
54 | bus_LV_6136-38_0_4_node_32 | 0.4 | n |  | TRUE
55 | bus_LV_6136-38_0_4_node_33 | 0.4 | n |  | TRUE
56 | bus_LV_6136-38_0_4_node_35 | 0.4 | n |  | TRUE
57 | bus_LV_6136-38_0_4_node_36 | 0.4 | n |  | TRUE
58 | bus_LV_6136-38_0_4_node_37 | 0.4 | n |  | TRUE
59 | bus_LV_6136-38_0_4_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_6136-38_0_4_node_40 | 0.4 | n |  | TRUE
61 | bus_LV_6136-38_0_4_node_41 | 0.4 | n |  | TRUE
62 | bus_LV_6136-38_0_4_node_42 | 0.4 | n |  | TRUE
63 | bus_LV_6136-38_0_4_node_69 | 0.4 | n |  | TRUE
64 | bus_LV_6136-38_0_4_node_68 | 0.4 | n |  | TRUE
65 | bus_LV_6136-38_0_4_node_43 | 0.4 | n |  | TRUE
66 | bus_LV_6136-38_0_4_node_44 | 0.4 | n |  | TRUE
67 | bus_LV_6136-38_0_4_node_45 | 0.4 | n |  | TRUE
68 | bus_LV_6136-38_0_4_node_48 | 0.4 | n |  | TRUE
69 | bus_LV_6136-38_0_4_node_53 | 0.4 | n |  | TRUE
70 | bus_LV_6136-38_0_4_node_65 | 0.4 | n |  | TRUE
71 | bus_LV_6136-38_0_4_node_64 | 0.4 | n |  | TRUE
72 | bus_LV_6136-38_0_4_node_59 | 0.4 | n |  | TRUE
73 | bus_LV_6136-38_0_4_node_62 | 0.4 | n |  | TRUE
74 | bus_LV_6136-38_0_4_node_61 | 0.4 | n |  | TRUE
75 | bus_LV_6136-38_0_4_node_67 | 0.4 | n |  | TRUE
76 | bus_MV_101_0_node_184 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6136-38_0_4_load_0 | 0 | 0.0058216 | 0.001459 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6136-38_0_4_load_1 | 1 | 0.023987 | 0.0060117 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6136-38_0_4_load_2 | 2 | 0.0077163 | 0.0019339 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6136-38_0_4_load_5 | 5 | 0.0059261 | 0.0014852 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6136-38_0_4_load_13 | 6 | 0.0069404 | 0.0017394 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6136-38_0_4_load_47 | 7 | 0.0083613 | 0.0020955 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6136-38_0_4_load_24 | 9 | 0.0098445 | 0.0024673 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6136-38_0_4_load_50 | 10 | 0.0061846 | 0.00155 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6136-38_0_4_load_11 | 11 | 0.0075163 | 0.0018838 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6136-38_0_4_load_29 | 12 | 0.009505 | 0.0023822 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6136-38_0_4_load_56 | 14 | 0.0062741 | 0.0015724 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6136-38_0_4_load_49 | 15 | 0.011468 | 0.0028742 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6136-38_0_4_load_6 | 16 | 0.0083932 | 0.0021035 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6136-38_0_4_load_7 | 17 | 0.0067632 | 0.001695 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6136-38_0_4_load_8 | 18 | 0.0046371 | 0.0011622 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6136-38_0_4_load_30 | 20 | 0.0065415 | 0.0016395 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6136-38_0_4_load_57 | 21 | 0.0046245 | 0.001159 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6136-38_0_4_load_28 | 22 | 0.0064188 | 0.0016087 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6136-38_0_4_load_10 | 23 | 0.01192 | 0.0029874 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6136-38_0_4_load_12 | 24 | 0.0078769 | 0.0019741 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6136-38_0_4_load_14 | 25 | 0.002593 | 0.00064987 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6136-38_0_4_load_76 | 26 | 0.040408 | 0.010127 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6136-38_0_4_load_16 | 28 | 0.0046416 | 0.0011633 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6136-38_0_4_load_71 | 29 | 0.0091729 | 0.0022989 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6136-38_0_4_load_15 | 30 | 0.0045721 | 0.0011459 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6136-38_0_4_load_70 | 31 | 0.0088678 | 0.0022225 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6136-38_0_4_load_17 | 32 | 0.0069292 | 0.0017366 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6136-38_0_4_load_38 | 36 | 0.0055462 | 0.00139 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6136-38_0_4_load_19 | 37 | 0.0068739 | 0.0017228 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6136-38_0_4_load_20 | 38 | 0.0062812 | 0.0015742 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6136-38_0_4_load_75 | 40 | 0.0089065 | 0.0022322 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6136-38_0_4_load_22 | 41 | 0.0031656 | 0.00079338 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6136-38_0_4_load_51 | 44 | 0.004226 | 0.0010591 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6136-38_0_4_load_34 | 45 | 0.0073753 | 0.0018484 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6136-38_0_4_load_52 | 46 | 0.0076354 | 0.0019136 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6136-38_0_4_load_66 | 47 | 0.0083297 | 0.0020876 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6136-38_0_4_load_63 | 48 | 0.0078374 | 0.0019642 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6136-38_0_4_load_26 | 50 | 0.0094461 | 0.0023674 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6136-38_0_4_load_27 | 51 | 0.0063195 | 0.0015838 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6136-38_0_4_load_58 | 52 | 0.0032788 | 0.00082174 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6136-38_0_4_load_31 | 53 | 0.0063873 | 0.0016008 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6136-38_0_4_load_32 | 54 | 0.0074161 | 0.0018586 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6136-38_0_4_load_33 | 55 | 0.0093838 | 0.0023518 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6136-38_0_4_load_35 | 56 | 0.005573 | 0.0013967 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6136-38_0_4_load_36 | 57 | 0.007268 | 0.0018215 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6136-38_0_4_load_39 | 59 | 0.0092905 | 0.0023284 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6136-38_0_4_load_40 | 60 | 0.0049552 | 0.0012419 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6136-38_0_4_load_41 | 61 | 0.0069488 | 0.0017415 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6136-38_0_4_load_42 | 62 | 0.0059333 | 0.001487 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6136-38_0_4_load_69 | 63 | 0.0040657 | 0.001019 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6136-38_0_4_load_68 | 64 | 0.0061621 | 0.0015444 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6136-38_0_4_load_43 | 65 | 0.0065688 | 0.0016463 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6136-38_0_4_load_44 | 66 | 0.0094079 | 0.0023578 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6136-38_0_4_load_45 | 67 | 0.0082201 | 0.0020602 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6136-38_0_4_load_48 | 68 | 0.0074297 | 0.0018621 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6136-38_0_4_load_53 | 69 | 0.008339 | 0.00209 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6136-38_0_4_load_65 | 70 | 0.0097729 | 0.0024493 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6136-38_0_4_load_64 | 71 | 0.0085086 | 0.0021325 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6136-38_0_4_load_62 | 73 | 0.0097221 | 0.0024366 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6136-38_0_4_load_61 | 74 | 0.0051894 | 0.0013006 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6136-38_0_4_load_67 | 75 | 0.0055896 | 0.0014009 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 68 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6136-38_0_4_line_0 |  | 0 | 1 | 0.036084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_6136-38_0_4_line_1 |  | 0 | 2 | 0.016598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_6136-38_0_4_line_2 |  | 1 | 3 | 0.019468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_6136-38_0_4_line_3 |  | 2 | 4 | 0.021057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_6136-38_0_4_line_4 |  | 2 | 5 | 0.011798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_6136-38_0_4_line_5 |  | 3 | 6 | 0.010458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6136-38_0_4_line_6 |  | 3 | 7 | 0.019039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6136-38_0_4_line_7 |  | 4 | 8 | 0.01542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_6136-38_0_4_line_8 |  | 4 | 9 | 0.029464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6136-38_0_4_line_9 |  | 5 | 10 | 0.012816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_6136-38_0_4_line_10 |  | 6 | 11 | 0.0057086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6136-38_0_4_line_11 |  | 7 | 12 | 0.0032362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6136-38_0_4_line_12 |  | 8 | 13 | 0.035587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_6136-38_0_4_line_13 |  | 8 | 14 | 0.0097588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6136-38_0_4_line_14 |  | 10 | 15 | 0.0048626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_6136-38_0_4_line_15 |  | 11 | 23 | 0.01438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6136-38_0_4_line_16 |  | 12 | 51 | 0.023553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6136-38_0_4_line_17 |  | 13 | 47 | 0.014845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6136-38_0_4_line_18 |  | 13 | 48 | 0.032816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6136-38_0_4_line_19 |  | 14 | 49 | 0.020347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6136-38_0_4_line_20 |  | 15 | 68 | 0.019978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_6136-38_0_4_line_21 |  | 16 | 17 | 0.027332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6136-38_0_4_line_22 |  | 16 | 18 | 0.01737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6136-38_0_4_line_23 |  | 18 | 19 | 0.012916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6136-38_0_4_line_24 |  | 19 | 20 | 0.016355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6136-38_0_4_line_25 |  | 20 | 21 | 0.019052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6136-38_0_4_line_26 |  | 20 | 22 | 0.01601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6136-38_0_4_line_27 |  | 21 | 52 | 0.015295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6136-38_0_4_line_28 |  | 22 | 50 | 0.0074419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6136-38_0_4_line_29 |  | 23 | 24 | 0.0042238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6136-38_0_4_line_30 |  | 24 | 25 | 0.018307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6136-38_0_4_line_31 |  | 25 | 28 | 0.0084997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6136-38_0_4_line_32 |  | 25 | 29 | 0.03323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6136-38_0_4_line_33 |  | 26 | 27 | 0.045165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6136-38_0_4_line_34 |  | 27 | 34 | 0.030966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6136-38_0_4_line_35 |  | 28 | 30 | 0.011046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6136-38_0_4_line_36 |  | 29 | 31 | 0.02143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6136-38_0_4_line_37 |  | 30 | 32 | 0.026714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6136-38_0_4_line_38 |  | 31 | 34 | 0.042462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6136-38_0_4_line_39 |  | 32 | 33 | 0.019476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6136-38_0_4_line_40 |  | 33 | 35 | 0.01269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6136-38_0_4_line_41 |  | 35 | 36 | 0.030469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6136-38_0_4_line_42 |  | 36 | 58 | 0.023435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6136-38_0_4_line_43 |  | 37 | 38 | 0.042659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6136-38_0_4_line_44 |  | 37 | 39 | 0.01826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6136-38_0_4_line_45 |  | 37 | 40 | 0.052398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6136-38_0_4_line_46 |  | 38 | 41 | 0.011755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6136-38_0_4_line_47 |  | 39 | 42 | 0.027012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6136-38_0_4_line_48 |  | 42 | 43 | 0.027311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6136-38_0_4_line_49 |  | 42 | 44 | 0.017997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6136-38_0_4_line_50 |  | 43 | 45 | 0.018621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6136-38_0_4_line_51 |  | 44 | 46 | 0.035598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6136-38_0_4_line_52 |  | 45 | 54 | 0.0094643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6136-38_0_4_line_53 |  | 46 | 69 | 0.015486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6136-38_0_4_line_54 |  | 47 | 75 | 0.0076731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6136-38_0_4_line_55 |  | 48 | 71 | 0.011186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6136-38_0_4_line_56 |  | 49 | 66 | 0.02775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6136-38_0_4_line_57 |  | 50 | 51 | 0.0015195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6136-38_0_4_line_58 |  | 52 | 72 | 0.011279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6136-38_0_4_line_59 |  | 53 | 54 | 0.0097919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6136-38_0_4_line_60 |  | 53 | 55 | 0.011599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6136-38_0_4_line_61 |  | 56 | 57 | 0.025583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6136-38_0_4_line_62 |  | 56 | 58 | 0.030776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6136-38_0_4_line_63 |  | 59 | 60 | 0.0072099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6136-38_0_4_line_64 |  | 59 | 61 | 0.00028059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6136-38_0_4_line_65 |  | 60 | 62 | 0.0064819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6136-38_0_4_line_66 |  | 62 | 63 | 0.0061381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6136-38_0_4_line_67 |  | 63 | 64 | 0.0064206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6136-38_0_4_line_68 |  | 64 | 75 | 0.0068107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6136-38_0_4_line_69 |  | 65 | 66 | 0.0030562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6136-38_0_4_line_70 |  | 65 | 67 | 0.004698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6136-38_0_4_line_71 |  | 69 | 70 | 0.014226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_6136-38_0_4_line_72 |  | 70 | 71 | 0.024244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_6136-38_0_4_line_73 |  | 72 | 73 | 0.024986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_6136-38_0_4_line_74 |  | 72 | 74 | 0.016404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6136-38_0_4_trafo_48 | 0.63 MVA 20/0.4 kV | 76 | 68 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2570840.0497 | 1104592.4421 | 2570846.8738 | 1104627.875
1 | 2570836.9108 | 1104576.1439 | 2570840.0497 | 1104592.4421
2 | 2570850.5556 | 1104646.992 | 2570846.8738 | 1104627.875
3 | 2570831.6845 | 1104555.7476 | 2570836.9108 | 1104576.1439
4 | 2570836.9108 | 1104576.1439 | 2570827.5875 | 1104583.3734
5 | 2570850.5556 | 1104646.992 | 2570851.4944 | 1104657.4076
6 | 2570850.5556 | 1104646.992 | 2570865.7232 | 1104635.4841
7 | 2570827.4287 | 1104540.9383 | 2570829.5239 | 1104547.187 | 2570831.6845 | 1104555.7476
8 | 2570831.6845 | 1104555.7476 | 2570855.6089 | 1104538.5496
9 | 2570827.5875 | 1104583.3734 | 2570817.4599 | 1104591.2266
10 | 2570852.0069 | 1104663.0932 | 2570851.4944 | 1104657.4076
11 | 2570868.3013 | 1104633.528 | 2570865.7232 | 1104635.4841
12 | 2570827.4287 | 1104540.9383 | 2570801.1858 | 1104565.0549
13 | 2570827.4287 | 1104540.9383 | 2570824.2002 | 1104531.729
14 | 2570817.4599 | 1104591.2266 | 2570813.6172 | 1104594.2064
15 | 2570852.0069 | 1104663.0932 | 2570853.2979 | 1104677.4151
16 | 2570868.3013 | 1104633.528 | 2570887.0646 | 1104619.2921
17 | 2570801.1858 | 1104565.0549 | 2570799.5755 | 1104569.5539 | 2570792.1377 | 1104576.3373
18 | 2570801.1858 | 1104565.0549 | 2570790.8148 | 1104554.0438 | 2570778.8647 | 1104560.4048 | 2570774.7331 | 1104560.8224
19 | 2570817.4687 | 1104512.5274 | 2570824.2002 | 1104531.729
20 | 2570797.8297 | 1104606.4484 | 2570813.6172 | 1104594.2064
21 | 2570910.5709 | 1104565.8285 | 2570913.3508 | 1104561.6797 | 2570903.1795 | 1104541.7922
22 | 2570910.5709 | 1104565.8285 | 2570910.5709 | 1104565.8285 | 2570914.3219 | 1104582.7886
23 | 2570920.0046 | 1104594.2866 | 2570914.864 | 1104585.24 | 2570914.3219 | 1104582.7886
24 | 2570920.0046 | 1104594.2866 | 2570906.9578 | 1104604.1988
25 | 2570906.9578 | 1104604.1988 | 2570912.2359 | 1104622.5048
26 | 2570906.9578 | 1104604.1988 | 2570894.2037 | 1104613.8755
27 | 2570912.2359 | 1104622.5048 | 2570916.4731 | 1104637.2008
28 | 2570894.2037 | 1104613.8755 | 2570888.2751 | 1104618.3737
29 | 2570853.6771 | 1104681.6219 | 2570853.2979 | 1104677.4151
30 | 2570853.6771 | 1104681.6219 | 2570855.3206 | 1104699.8546
31 | 2570856.0837 | 1104708.32 | 2570855.3206 | 1104699.8546
32 | 2570855.3206 | 1104699.8546 | 2570822.2473 | 1104696.6315
33 | 2570784.7335 | 1104680.1486 | 2570780.0972 | 1104690.643 | 2570758.2529 | 1104709.3247 | 2570754.4479 | 1104712.578
34 | 2570754.4479 | 1104712.578 | 2570760.1597 | 1104719.7763 | 2570774.1237 | 1104736.5285
35 | 2570856.0837 | 1104708.32 | 2570857.0754 | 1104719.3216
36 | 2570822.2473 | 1104696.6315 | 2570820.0273 | 1104701.378 | 2570811.9683 | 1104707.8201 | 2570806.1561 | 1104708.6597
37 | 2570858.8804 | 1104745.971 | 2570857.9586 | 1104729.1204 | 2570857.0754 | 1104719.3216
38 | 2570774.1237 | 1104736.5285 | 2570778.2507 | 1104732.6844 | 2570806.1561 | 1104708.6597
39 | 2570858.1717 | 1104765.3156 | 2570859.5107 | 1104757.4941 | 2570858.8804 | 1104745.971
40 | 2570870.5401 | 1104765.5895 | 2570865.1636 | 1104766.9494 | 2570858.1717 | 1104765.3156
41 | 2570870.5401 | 1104765.5895 | 2570899.8611 | 1104757.3047
42 | 2570922.4128 | 1104750.9326 | 2570899.8611 | 1104757.3047
43 | 2570687.5675 | 1104598.7715 | 2570719.923 | 1104570.9704
44 | 2570673.718 | 1104610.6723 | 2570676.8528 | 1104607.978 | 2570687.5675 | 1104598.7715
45 | 2570687.5675 | 1104598.7715 | 2570662.7397 | 1104552.6293
46 | 2570728.839 | 1104563.3094 | 2570719.923 | 1104570.9704
47 | 2570673.718 | 1104610.6723 | 2570678.2639 | 1104616.6534 | 2570685.4001 | 1104625.6678 | 2570690.3882 | 1104631.9246
48 | 2570690.3882 | 1104631.9246 | 2570707.3915 | 1104653.331
49 | 2570690.3882 | 1104631.9246 | 2570695.1994 | 1104628.8109 | 2570704.4637 | 1104620.7711
50 | 2570707.3915 | 1104653.331 | 2570713.5043 | 1104649.0659 | 2570721.9659 | 1104641.7782
51 | 2570704.4637 | 1104620.7711 | 2570731.3493 | 1104597.4392
52 | 2570729.1372 | 1104635.602 | 2570721.9659 | 1104641.7782
53 | 2570743.0451 | 1104587.2894 | 2570731.3493 | 1104597.4392
54 | 2570792.1377 | 1104576.3373 | 2570786.4684 | 1104581.5078
55 | 2570774.7331 | 1104560.8224 | 2570767.1991 | 1104561.5839 | 2570764.4803 | 1104563.9649
56 | 2570817.4687 | 1104512.5274 | 2570797.151 | 1104531.4281
57 | 2570887.0646 | 1104619.2921 | 2570888.2751 | 1104618.3737
58 | 2570919.5978 | 1104648.0381 | 2570916.4731 | 1104637.2008
59 | 2570729.1372 | 1104635.602 | 2570736.5567 | 1104629.2119
60 | 2570745.3456 | 1104621.6424 | 2570736.5567 | 1104629.2119
61 | 2570907.0364 | 1104697.7238 | 2570914.4913 | 1104711.9953 | 2570918.0365 | 1104720.7893
62 | 2570922.4128 | 1104750.9326 | 2570922.1176 | 1104744.2306 | 2570921.0979 | 1104728.383 | 2570918.0365 | 1104720.7893
63 | 2570762.0406 | 1104603.7863 | 2570767.3678 | 1104598.9279
64 | 2570762.0406 | 1104603.7863 | 2570761.8333 | 1104603.9754
65 | 2570772.157 | 1104594.56 | 2570767.3678 | 1104598.9279
66 | 2570776.6922 | 1104590.4238 | 2570772.157 | 1104594.56
67 | 2570781.4362 | 1104586.0973 | 2570776.6922 | 1104590.4238
68 | 2570786.4684 | 1104581.5078 | 2570781.4362 | 1104586.0973
69 | 2570794.9133 | 1104533.5097 | 2570797.151 | 1104531.4281
70 | 2570791.4736 | 1104536.7096 | 2570794.9133 | 1104533.5097
71 | 2570752.1296 | 1104577.0424 | 2570752.1296 | 1104577.0424 | 2570750.1926 | 1104577.93 | 2570748.8537 | 1104579.3594 | 2570748.4301 | 1104581.3291 | 2570747.5791 | 1104582.9007 | 2570746.4415 | 1104584.3514 | 2570745.1166 | 1104585.4917 | 2570743.0451 | 1104587.2894
72 | 2570752.1296 | 1104577.0424 | 2570754.5724 | 1104576.7638 | 2570756.4132 | 1104576.766 | 2570758.0182 | 1104575.9801 | 2570759.4363 | 1104574.9505 | 2570760.9769 | 1104573.6424 | 2570763.6969 | 1104573.1178 | 2570765.7187 | 1104572.152 | 2570766.8385 | 1104570.2012 | 2570767.1522 | 1104567.8985 | 2570765.8797 | 1104565.4478 | 2570764.4803 | 1104563.9649 | 2570764.4803 | 1104563.9649
73 | 2570919.5978 | 1104648.0381 | 2570923.785 | 1104661.5027 | 2570927.3459 | 1104671.7908
74 | 2570919.5978 | 1104648.0381 | 2570906.3617 | 1104657.7273

## bus_geodata
| x | y | coords
0 | 2570840.0497 | 1104592.4421
1 | 2570846.8738 | 1104627.875
2 | 2570836.9108 | 1104576.1439
3 | 2570850.5556 | 1104646.992
4 | 2570831.6845 | 1104555.7476
5 | 2570827.5875 | 1104583.3734
6 | 2570851.4944 | 1104657.4076
7 | 2570865.7232 | 1104635.4841
8 | 2570827.4287 | 1104540.9383
9 | 2570855.6089 | 1104538.5496
10 | 2570817.4599 | 1104591.2266
11 | 2570852.0069 | 1104663.0932
12 | 2570868.3013 | 1104633.528
13 | 2570801.1858 | 1104565.0549
14 | 2570824.2002 | 1104531.729
15 | 2570813.6172 | 1104594.2064
16 | 2570910.5709 | 1104565.8285
17 | 2570903.1795 | 1104541.7922
18 | 2570914.3219 | 1104582.7886
19 | 2570920.0046 | 1104594.2866
20 | 2570906.9578 | 1104604.1988
21 | 2570912.2359 | 1104622.5048
22 | 2570894.2037 | 1104613.8755
23 | 2570853.2979 | 1104677.4151
24 | 2570853.6771 | 1104681.6219
25 | 2570855.3206 | 1104699.8546
26 | 2570784.7335 | 1104680.1486
27 | 2570754.4479 | 1104712.578
28 | 2570856.0837 | 1104708.32
29 | 2570822.2473 | 1104696.6315
30 | 2570857.0754 | 1104719.3216
31 | 2570806.1561 | 1104708.6597
32 | 2570858.8804 | 1104745.971
33 | 2570858.1717 | 1104765.3156
34 | 2570774.1237 | 1104736.5285
35 | 2570870.5401 | 1104765.5895
36 | 2570899.8611 | 1104757.3047
37 | 2570687.5675 | 1104598.7715
38 | 2570719.923 | 1104570.9704
39 | 2570673.718 | 1104610.6723
40 | 2570662.7397 | 1104552.6293
41 | 2570728.839 | 1104563.3094
42 | 2570690.3882 | 1104631.9246
43 | 2570707.3915 | 1104653.331
44 | 2570704.4637 | 1104620.7711
45 | 2570721.9659 | 1104641.7783
46 | 2570731.3493 | 1104597.4392
47 | 2570792.1377 | 1104576.3373
48 | 2570774.7331 | 1104560.8224
49 | 2570817.4687 | 1104512.5274
50 | 2570888.2751 | 1104618.3737
51 | 2570887.0646 | 1104619.2921
52 | 2570916.4731 | 1104637.2008
53 | 2570736.5567 | 1104629.2119
54 | 2570729.1372 | 1104635.602
55 | 2570745.3456 | 1104621.6424
56 | 2570918.0365 | 1104720.7893
57 | 2570907.0364 | 1104697.7238
58 | 2570922.4128 | 1104750.9326
59 | 2570762.0406 | 1104603.7863
60 | 2570767.3678 | 1104598.9279
61 | 2570761.8333 | 1104603.9754
62 | 2570772.157 | 1104594.56
63 | 2570776.6922 | 1104590.4238
64 | 2570781.4362 | 1104586.0973
65 | 2570794.9133 | 1104533.5097
66 | 2570797.151 | 1104531.4281
67 | 2570791.4736 | 1104536.7096
68 | 2570797.8297 | 1104606.4484
69 | 2570743.0451 | 1104587.2894
70 | 2570752.1296 | 1104577.0424
71 | 2570764.4803 | 1104563.9649
72 | 2570919.5978 | 1104648.0381
73 | 2570927.3459 | 1104671.7908
74 | 2570906.3617 | 1104657.7273
75 | 2570786.4684 | 1104581.5078
76 | 2570793.921 | 1104609.4793

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1