## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6136-94_1_4_node_54 | 0.4 | n |  | TRUE
1 | bus_LV_6136-94_1_4_node_55 | 0.4 | n |  | TRUE
2 | bus_LV_6136-94_1_4_node_6 | 0.4 | n |  | TRUE
3 | bus_LV_6136-94_1_4_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_6136-94_1_4_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_6136-94_1_4_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_6136-94_1_4_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_6136-94_1_4_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_6136-94_1_4_node_72 | 0.4 | n |  | TRUE
9 | bus_LV_6136-94_1_4_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_6136-94_1_4_node_84 | 0.4 | n |  | TRUE
11 | bus_LV_6136-94_1_4_node_71 | 0.4 | n |  | TRUE
12 | bus_LV_6136-94_1_4_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_6136-94_1_4_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_6136-94_1_4_node_83 | 0.4 | n |  | TRUE
15 | bus_LV_6136-94_1_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_6136-94_1_4_node_24 | 0.4 | n |  | TRUE
17 | bus_LV_6136-94_1_4_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_6136-94_1_4_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_6136-94_1_4_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_6136-94_1_4_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_6136-94_1_4_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_6136-94_1_4_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_6136-94_1_4_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_6136-94_1_4_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_6136-94_1_4_node_77 | 0.4 | n |  | TRUE
26 | bus_LV_6136-94_1_4_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_6136-94_1_4_node_75 | 0.4 | n |  | TRUE
28 | bus_LV_6136-94_1_4_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_6136-94_1_4_node_79 | 0.4 | n |  | TRUE
30 | bus_LV_6136-94_1_4_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_6136-94_1_4_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_6136-94_1_4_node_49 | 0.4 | n |  | TRUE
33 | bus_LV_6136-94_1_4_node_50 | 0.4 | n |  | TRUE
34 | bus_LV_6136-94_1_4_node_61 | 0.4 | n |  | TRUE
35 | bus_LV_6136-94_1_4_node_58 | 0.4 | n |  | TRUE
36 | bus_LV_6136-94_1_4_node_62 | 0.4 | n |  | TRUE
37 | bus_LV_6136-94_1_4_node_53 | 0.4 | n |  | TRUE
38 | bus_LV_6136-94_1_4_node_56 | 0.4 | n |  | TRUE
39 | bus_LV_6136-94_1_4_node_57 | 0.4 | n |  | TRUE
40 | bus_LV_6136-94_1_4_node_104 | 0.4 | n |  | TRUE
41 | bus_LV_6136-94_1_4_node_87 | 0.4 | n |  | TRUE
42 | bus_LV_6136-94_1_4_node_86 | 0.4 | n |  | TRUE
43 | bus_LV_6136-94_1_4_node_59 | 0.4 | n |  | TRUE
44 | bus_LV_6136-94_1_4_node_60 | 0.4 | n |  | TRUE
45 | bus_LV_6136-94_1_4_node_66 | 0.4 | n |  | TRUE
46 | bus_LV_6136-94_1_4_node_64 | 0.4 | n |  | TRUE
47 | bus_LV_6136-94_1_4_node_65 | 0.4 | n |  | TRUE
48 | bus_LV_6136-94_1_4_node_67 | 0.4 | n |  | TRUE
49 | bus_LV_6136-94_1_4_node_68 | 0.4 | n |  | TRUE
50 | bus_LV_6136-94_1_4_node_69 | 0.4 | n |  | TRUE
51 | bus_LV_6136-94_1_4_node_70 | 0.4 | n |  | TRUE
52 | bus_LV_6136-94_1_4_node_73 | 0.4 | n |  | TRUE
53 | bus_LV_6136-94_1_4_node_74 | 0.4 | n |  | TRUE
54 | bus_LV_6136-94_1_4_node_76 | 0.4 | n |  | TRUE
55 | bus_LV_6136-94_1_4_node_78 | 0.4 | n |  | TRUE
56 | bus_LV_6136-94_1_4_node_81 | 0.4 | n |  | TRUE
57 | bus_LV_6136-94_1_4_node_85 | 0.4 | n |  | TRUE
58 | bus_MV_102_0_node_140 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6136-94_1_4_load_54 | 0 | 0.0075545 | 0.0018933 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6136-94_1_4_load_55 | 1 | 0.0038046 | 0.00095351 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6136-94_1_4_load_6 | 2 | 0.0036094 | 0.00090459 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6136-94_1_4_load_7 | 3 | 0.0030512 | 0.0007647 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6136-94_1_4_load_8 | 4 | 0.0023956 | 0.0006004 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6136-94_1_4_load_10 | 6 | 0.0022164 | 0.00055547 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6136-94_1_4_load_11 | 7 | 0.0033446 | 0.00083824 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6136-94_1_4_load_72 | 8 | 0.0026879 | 0.00067366 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6136-94_1_4_load_84 | 10 | 0.0048195 | 0.0012079 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6136-94_1_4_load_71 | 11 | 0.0056176 | 0.0014079 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6136-94_1_4_load_13 | 12 | 0.0033587 | 0.00084176 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6136-94_1_4_load_14 | 13 | 0.0019641 | 0.00049225 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6136-94_1_4_load_83 | 14 | 0.0039316 | 0.00098535 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6136-94_1_4_load_15 | 15 | 0.0039472 | 0.00098926 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6136-94_1_4_load_24 | 16 | 0.0022529 | 0.00056463 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6136-94_1_4_load_16 | 17 | 0.0043778 | 0.0010972 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6136-94_1_4_load_17 | 19 | 0.002593 | 0.00064987 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6136-94_1_4_load_19 | 20 | 0.0034938 | 0.00087563 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6136-94_1_4_load_20 | 21 | 0.0032496 | 0.00081443 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6136-94_1_4_load_22 | 22 | 0.0037017 | 0.00092773 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6136-94_1_4_load_23 | 23 | 0.0018683 | 0.00046825 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6136-94_1_4_load_25 | 24 | 0.0077311 | 0.0019376 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6136-94_1_4_load_77 | 25 | 0.00193 | 0.0004837 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6136-94_1_4_load_26 | 26 | 0.009185 | 0.002302 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6136-94_1_4_load_75 | 27 | 0.0027722 | 0.00069477 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6136-94_1_4_load_27 | 28 | 0.0061706 | 0.0015465 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6136-94_1_4_load_79 | 29 | 0.0053368 | 0.0013375 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6136-94_1_4_load_28 | 30 | 0.0023112 | 0.00057924 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6136-94_1_4_load_29 | 31 | 0.005991 | 0.0015015 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6136-94_1_4_load_49 | 32 | 0.0097641 | 0.0024471 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6136-94_1_4_load_50 | 33 | 0.0057272 | 0.0014354 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6136-94_1_4_load_61 | 34 | 0.0072945 | 0.0018282 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6136-94_1_4_load_58 | 35 | 0.0066564 | 0.0016682 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6136-94_1_4_load_62 | 36 | 0.014873 | 0.0037276 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6136-94_1_4_load_56 | 38 | 0.0056179 | 0.001408 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6136-94_1_4_load_57 | 39 | 0.0096566 | 0.0024202 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6136-94_1_4_load_104 | 40 | 0.0059204 | 0.0014838 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6136-94_1_4_load_86 | 42 | 0.0034535 | 0.00086553 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6136-94_1_4_load_59 | 43 | 0.0076936 | 0.0019282 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6136-94_1_4_load_60 | 44 | 0.0080357 | 0.0020139 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6136-94_1_4_load_66 | 45 | 0.011088 | 0.002779 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6136-94_1_4_load_64 | 46 | 0.0070235 | 0.0017602 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6136-94_1_4_load_65 | 47 | 0.010814 | 0.0027103 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6136-94_1_4_load_67 | 48 | 0.0053587 | 0.001343 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6136-94_1_4_load_68 | 49 | 0.0013966 | 0.00035002 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6136-94_1_4_load_69 | 50 | 0.0014789 | 0.00037065 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6136-94_1_4_load_70 | 51 | 0.0075627 | 0.0018954 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6136-94_1_4_load_73 | 52 | 0.015397 | 0.0038589 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6136-94_1_4_load_74 | 53 | 0.0058442 | 0.0014647 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6136-94_1_4_load_76 | 54 | 0.0091028 | 0.0022814 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6136-94_1_4_load_78 | 55 | 0.011613 | 0.0029105 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6136-94_1_4_load_81 | 56 | 0.011442 | 0.0028676 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6136-94_1_4_load_85 | 57 | 0.0057168 | 0.0014328 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6136-94_1_4_line_0 |  | 0 | 1 | 0.0048592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6136-94_1_4_line_1 |  | 1 | 41 | 0.035587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6136-94_1_4_line_2 |  | 2 | 3 | 0.018276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_6136-94_1_4_line_3 |  | 2 | 4 | 0.022988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_6136-94_1_4_line_4 |  | 3 | 5 | 0.0135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_6136-94_1_4_line_5 |  | 4 | 6 | 0.0022288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6136-94_1_4_line_6 |  | 4 | 7 | 0.05166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_6136-94_1_4_line_7 |  | 5 | 8 | 0.0099589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_6136-94_1_4_line_8 |  | 6 | 9 | 0.039045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6136-94_1_4_line_9 |  | 7 | 10 | 0.0041098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_6136-94_1_4_line_10 |  | 8 | 11 | 0.012566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_6136-94_1_4_line_11 |  | 9 | 12 | 0.026645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6136-94_1_4_line_12 |  | 9 | 13 | 0.0049207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6136-94_1_4_line_13 |  | 10 | 14 | 0.026572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_6136-94_1_4_line_14 |  | 11 | 51 | 0.0062065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6136-94_1_4_line_15 |  | 12 | 15 | 0.0013356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6136-94_1_4_line_16 |  | 13 | 16 | 0.012221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6136-94_1_4_line_17 |  | 14 | 57 | 0.0038757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6136-94_1_4_line_18 |  | 15 | 17 | 0.010047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6136-94_1_4_line_19 |  | 16 | 18 | 0.030549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6136-94_1_4_line_20 |  | 17 | 19 | 0.030593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6136-94_1_4_line_21 |  | 18 | 23 | 0.022394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6136-94_1_4_line_22 |  | 18 | 20 | 0.013612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6136-94_1_4_line_23 |  | 20 | 21 | 0.0068747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6136-94_1_4_line_24 |  | 21 | 22 | 0.01214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6136-94_1_4_line_25 |  | 22 | 24 | 0.010588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6136-94_1_4_line_26 |  | 23 | 25 | 0.0025922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6136-94_1_4_line_27 |  | 24 | 26 | 0.010754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6136-94_1_4_line_28 |  | 25 | 27 | 0.022386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6136-94_1_4_line_29 |  | 26 | 28 | 0.026018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6136-94_1_4_line_30 |  | 27 | 52 | 0.050465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6136-94_1_4_line_31 |  | 28 | 29 | 0.022939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6136-94_1_4_line_32 |  | 30 | 31 | 0.020159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6136-94_1_4_line_33 |  | 31 | 32 | 0.053217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6136-94_1_4_line_34 |  | 32 | 35 | 0.074534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6136-94_1_4_line_35 |  | 32 | 33 | 0.021955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6136-94_1_4_line_36 |  | 33 | 34 | 0.028668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6136-94_1_4_line_37 |  | 34 | 36 | 0.036538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6136-94_1_4_line_38 |  | 35 | 43 | 0.0044353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6136-94_1_4_line_39 |  | 35 | 38 | 0.017783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6136-94_1_4_line_40 |  | 37 | 38 | 0.011197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6136-94_1_4_line_41 |  | 37 | 39 | 0.019689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6136-94_1_4_line_42 |  | 39 | 40 | 0.025799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6136-94_1_4_line_43 |  | 41 | 42 | 0.051673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6136-94_1_4_line_44 |  | 42 | 57 | 0.027228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6136-94_1_4_line_45 |  | 43 | 44 | 0.017736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6136-94_1_4_line_46 |  | 44 | 45 | 0.0087767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6136-94_1_4_line_47 |  | 45 | 46 | 0.018221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6136-94_1_4_line_48 |  | 46 | 47 | 0.0022736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6136-94_1_4_line_49 |  | 47 | 48 | 0.0036973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6136-94_1_4_line_50 |  | 48 | 49 | 0.017102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6136-94_1_4_line_51 |  | 49 | 50 | 0.0088973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6136-94_1_4_line_52 |  | 50 | 51 | 0.013718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6136-94_1_4_line_53 |  | 52 | 53 | 0.019204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6136-94_1_4_line_54 |  | 53 | 54 | 0.042631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6136-94_1_4_line_55 |  | 54 | 55 | 0.0063304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6136-94_1_4_line_56 |  | 55 | 56 | 0.031899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6136-94_1_4_trafo_83 | 0.63 MVA 20/0.4 kV | 58 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2576212.3941 | 1107999.393 | 2576208.8441 | 1108002.711
1 | 2576182.8449 | 1108027.0107 | 2576208.8441 | 1108002.711
2 | 2576160.5637 | 1107850.8178 | 2576172.8414 | 1107837.2804
3 | 2576145.12 | 1107867.8461 | 2576160.5637 | 1107850.8178
4 | 2576181.9106 | 1107827.2806 | 2576172.8414 | 1107837.2804
5 | 2576145.12 | 1107867.8461 | 2576143.6225 | 1107869.4968
6 | 2576145.12 | 1107867.8461 | 2576150.3925 | 1107873.8394 | 2576153.9013 | 1107881.4738 | 2576161.8641 | 1107915.8388
7 | 2576181.9106 | 1107827.2806 | 2576187.5822 | 1107835.4667
8 | 2576117.3888 | 1107898.4154 | 2576143.6225 | 1107869.4968
9 | 2576162.7918 | 1107919.8425 | 2576161.8641 | 1107915.8388
10 | 2576194.7384 | 1107845.796 | 2576187.5822 | 1107835.4667
11 | 2576117.3888 | 1107898.4154 | 2576096.9286 | 1107881.3476
12 | 2576117.3888 | 1107898.4154 | 2576114.1494 | 1107902.1192
13 | 2576168.7899 | 1107945.7283 | 2576162.7918 | 1107919.8425
14 | 2576194.7384 | 1107845.796 | 2576198.273 | 1107850.8978
15 | 2576095.903 | 1107880.4921 | 2576096.9286 | 1107881.3476
16 | 2576106.1037 | 1107911.3182 | 2576114.1494 | 1107902.1192
17 | 2576168.7899 | 1107945.7283 | 2576169.6648 | 1107949.5039
18 | 2576095.903 | 1107880.4921 | 2576088.1881 | 1107874.0564
19 | 2576085.9917 | 1107934.3131 | 2576106.1037 | 1107911.3182
20 | 2576064.6956 | 1107854.4592 | 2576088.1881 | 1107874.0564
21 | 2576085.9917 | 1107934.3131 | 2576093.6436 | 1107941.8867 | 2576096.1647 | 1107948.002 | 2576096.2405 | 1107953.0152
22 | 2576085.9917 | 1107934.3131 | 2576076.9624 | 1107944.4989
23 | 2576076.9624 | 1107944.4989 | 2576072.4021 | 1107949.6433
24 | 2576064.3489 | 1107958.7278 | 2576072.4021 | 1107949.6433
25 | 2576057.325 | 1107966.6512 | 2576064.3489 | 1107958.7278
26 | 2576096.2797 | 1107955.607 | 2576096.2405 | 1107953.0152
27 | 2576057.325 | 1107966.6512 | 2576050.191 | 1107974.6989
28 | 2576096.2797 | 1107955.607 | 2576096.6184 | 1107977.9903
29 | 2576032.9319 | 1107994.1683 | 2576050.191 | 1107974.6989
30 | 2576097.3819 | 1108028.4491 | 2576096.6184 | 1107977.9903
31 | 2576017.7156 | 1108011.3335 | 2576032.9319 | 1107994.1683
32 | 2576364.8698 | 1107868.4832 | 2576365.8716 | 1107863.7102 | 2576362.5186 | 1107856.3196 | 2576358.3069 | 1107850.7221 | 2576358.3063 | 1107850.5602
33 | 2576318.1442 | 1107893.955 | 2576364.8698 | 1107868.4832
34 | 2576252.2933 | 1107928.8698 | 2576318.1442 | 1107893.955
35 | 2576318.1442 | 1107893.955 | 2576307.8259 | 1107874.5757
36 | 2576307.8259 | 1107874.5757 | 2576294.3528 | 1107849.2712
37 | 2576294.3528 | 1107849.2712 | 2576277.1809 | 1107817.0199
38 | 2576252.2933 | 1107928.8698 | 2576249.7674 | 1107925.224
39 | 2576262.4203 | 1107943.487 | 2576252.2933 | 1107928.8698
40 | 2576268.7969 | 1107952.6908 | 2576262.4203 | 1107943.487
41 | 2576268.7969 | 1107952.6908 | 2576252.345 | 1107963.5072
42 | 2576230.7875 | 1107977.6802 | 2576252.345 | 1107963.5072
43 | 2576182.8449 | 1108027.0107 | 2576182.8729 | 1108014.5155 | 2576180.576 | 1107996.5933 | 2576175.8111 | 1107976.0296
44 | 2576175.8111 | 1107976.0296 | 2576169.6648 | 1107949.5039
45 | 2576239.6667 | 1107910.6448 | 2576249.7674 | 1107925.224
46 | 2576239.6667 | 1107910.6448 | 2576234.6685 | 1107903.4304
47 | 2576224.2918 | 1107888.453 | 2576234.6685 | 1107903.4304
48 | 2576224.2918 | 1107888.453 | 2576222.9971 | 1107886.5841
49 | 2576222.9971 | 1107886.5841 | 2576220.8915 | 1107883.5449
50 | 2576220.8915 | 1107883.5449 | 2576211.1521 | 1107869.4872
51 | 2576211.1521 | 1107869.4872 | 2576206.0851 | 1107862.1736
52 | 2576206.0851 | 1107862.1736 | 2576198.273 | 1107850.8978
53 | 2576097.3819 | 1108028.4491 | 2576097.6725 | 1108047.651
54 | 2576097.6725 | 1108047.651 | 2576098.3175 | 1108090.2776
55 | 2576098.4132 | 1108096.6073 | 2576098.3175 | 1108090.2776
56 | 2576099.6408 | 1108128.4804 | 2576098.5092 | 1108102.9485 | 2576098.4132 | 1108096.6073

## bus_geodata
| x | y | coords
0 | 2576212.3941 | 1107999.393
1 | 2576208.8441 | 1108002.711
2 | 2576160.5637 | 1107850.8178
3 | 2576172.8414 | 1107837.2804
4 | 2576145.12 | 1107867.8461
5 | 2576181.9106 | 1107827.2806
6 | 2576143.6225 | 1107869.4968
7 | 2576161.8641 | 1107915.8388
8 | 2576187.5821 | 1107835.4667
9 | 2576117.3888 | 1107898.4154
10 | 2576162.7918 | 1107919.8425
11 | 2576194.7384 | 1107845.796
12 | 2576096.9286 | 1107881.3476
13 | 2576114.1494 | 1107902.1192
14 | 2576168.7899 | 1107945.7283
15 | 2576095.903 | 1107880.4921
16 | 2576106.1037 | 1107911.3182
17 | 2576088.1881 | 1107874.0564
18 | 2576085.9917 | 1107934.3131
19 | 2576064.6956 | 1107854.4592
20 | 2576076.9624 | 1107944.4989
21 | 2576072.4021 | 1107949.6433
22 | 2576064.3489 | 1107958.7278
23 | 2576096.2405 | 1107953.0152
24 | 2576057.325 | 1107966.6512
25 | 2576096.2797 | 1107955.607
26 | 2576050.191 | 1107974.6989
27 | 2576096.6184 | 1107977.9903
28 | 2576032.9319 | 1107994.1684
29 | 2576017.7156 | 1108011.3335
30 | 2576358.3063 | 1107850.5602
31 | 2576364.8698 | 1107868.4832
32 | 2576318.1442 | 1107893.955
33 | 2576307.8259 | 1107874.5757
34 | 2576294.3528 | 1107849.2712
35 | 2576252.2933 | 1107928.8698
36 | 2576277.1809 | 1107817.0199
37 | 2576268.7969 | 1107952.6908
38 | 2576262.4203 | 1107943.487
39 | 2576252.345 | 1107963.5072
40 | 2576230.7875 | 1107977.6802
41 | 2576182.8449 | 1108027.0107
42 | 2576175.8111 | 1107976.0296
43 | 2576249.7674 | 1107925.224
44 | 2576239.6667 | 1107910.6448
45 | 2576234.6685 | 1107903.4304
46 | 2576224.2918 | 1107888.453
47 | 2576222.9971 | 1107886.5841
48 | 2576220.8915 | 1107883.5449
49 | 2576211.1521 | 1107869.4872
50 | 2576206.0851 | 1107862.1736
51 | 2576198.273 | 1107850.8978
52 | 2576097.3819 | 1108028.4491
53 | 2576097.6725 | 1108047.651
54 | 2576098.3175 | 1108090.2776
55 | 2576098.4132 | 1108096.6073
56 | 2576099.6408 | 1108128.4804
57 | 2576169.6648 | 1107949.5039
58 | 2576145.12 | 1107867.8461

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1