## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6152-25_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6152-25_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6152-25_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6152-25_0_7_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6152-25_0_7_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6152-25_0_7_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6152-25_0_7_node_48 | 0.4 | n |  | TRUE
7 | bus_LV_6152-25_0_7_node_62 | 0.4 | n |  | TRUE
8 | bus_LV_6152-25_0_7_node_47 | 0.4 | n |  | TRUE
9 | bus_LV_6152-25_0_7_node_67 | 0.4 | n |  | TRUE
10 | bus_LV_6152-25_0_7_node_68 | 0.4 | n |  | TRUE
11 | bus_LV_6152-25_0_7_node_69 | 0.4 | n |  | TRUE
12 | bus_LV_6152-25_0_7_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_6152-25_0_7_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_6152-25_0_7_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_6152-25_0_7_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_6152-25_0_7_node_75 | 0.4 | n |  | TRUE
17 | bus_LV_6152-25_0_7_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_6152-25_0_7_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_6152-25_0_7_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_6152-25_0_7_node_63 | 0.4 | n |  | TRUE
21 | bus_LV_6152-25_0_7_node_76 | 0.4 | n |  | TRUE
22 | bus_LV_6152-25_0_7_node_59 | 0.4 | n |  | TRUE
23 | bus_LV_6152-25_0_7_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_6152-25_0_7_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_6152-25_0_7_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_6152-25_0_7_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_6152-25_0_7_node_57 | 0.4 | n |  | TRUE
28 | bus_LV_6152-25_0_7_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_6152-25_0_7_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_6152-25_0_7_node_66 | 0.4 | n |  | TRUE
31 | bus_LV_6152-25_0_7_node_65 | 0.4 | n |  | TRUE
32 | bus_LV_6152-25_0_7_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_6152-25_0_7_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_6152-25_0_7_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_6152-25_0_7_node_15 | 0.4 | n |  | TRUE
36 | bus_LV_6152-25_0_7_node_16 | 0.4 | n |  | TRUE
37 | bus_LV_6152-25_0_7_node_17 | 0.4 | n |  | TRUE
38 | bus_LV_6152-25_0_7_node_61 | 0.4 | n |  | TRUE
39 | bus_LV_6152-25_0_7_node_64 | 0.4 | n |  | TRUE
40 | bus_LV_6152-25_0_7_node_58 | 0.4 | n |  | TRUE
41 | bus_LV_6152-25_0_7_node_52 | 0.4 | n |  | TRUE
42 | bus_LV_6152-25_0_7_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_6152-25_0_7_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_6152-25_0_7_node_49 | 0.4 | n |  | TRUE
45 | bus_LV_6152-25_0_7_node_25 | 0.4 | n |  | TRUE
46 | bus_LV_6152-25_0_7_node_26 | 0.4 | n |  | TRUE
47 | bus_LV_6152-25_0_7_node_27 | 0.4 | n |  | TRUE
48 | bus_LV_6152-25_0_7_node_28 | 0.4 | n |  | TRUE
49 | bus_LV_6152-25_0_7_node_29 | 0.4 | n |  | TRUE
50 | bus_LV_6152-25_0_7_node_30 | 0.4 | n |  | TRUE
51 | bus_LV_6152-25_0_7_node_77 | 0.4 | n |  | TRUE
52 | bus_LV_6152-25_0_7_node_31 | 0.4 | n |  | TRUE
53 | bus_LV_6152-25_0_7_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_6152-25_0_7_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_6152-25_0_7_node_33 | 0.4 | n |  | TRUE
56 | bus_LV_6152-25_0_7_node_32 | 0.4 | n |  | TRUE
57 | bus_LV_6152-25_0_7_node_36 | 0.4 | n |  | TRUE
58 | bus_LV_6152-25_0_7_node_56 | 0.4 | n |  | TRUE
59 | bus_LV_6152-25_0_7_node_74 | 0.4 | n |  | TRUE
60 | bus_LV_6152-25_0_7_node_79 | 0.4 | n |  | TRUE
61 | bus_LV_6152-25_0_7_node_37 | 0.4 | n |  | TRUE
62 | bus_LV_6152-25_0_7_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_6152-25_0_7_node_72 | 0.4 | n |  | TRUE
64 | bus_LV_6152-25_0_7_node_38 | 0.4 | n |  | TRUE
65 | bus_LV_6152-25_0_7_node_50 | 0.4 | n |  | TRUE
66 | bus_LV_6152-25_0_7_node_46 | 0.4 | n |  | TRUE
67 | bus_LV_6152-25_0_7_node_51 | 0.4 | n |  | TRUE
68 | bus_LV_6152-25_0_7_node_42 | 0.4 | n |  | TRUE
69 | bus_LV_6152-25_0_7_node_45 | 0.4 | n |  | TRUE
70 | bus_LV_6152-25_0_7_node_80 | 0.4 | n |  | TRUE
71 | bus_LV_6152-25_0_7_node_70 | 0.4 | n |  | TRUE
72 | bus_LV_6152-25_0_7_node_55 | 0.4 | n |  | TRUE
73 | bus_LV_6152-25_0_7_node_73 | 0.4 | n |  | TRUE
74 | bus_LV_6152-25_0_7_node_78 | 0.4 | n |  | TRUE
75 | bus_LV_6152-25_0_7_node_53 | 0.4 | n |  | TRUE
76 | bus_LV_6152-25_0_7_node_54 | 0.4 | n |  | TRUE
77 | bus_LV_6152-25_0_7_node_60 | 0.4 | n |  | TRUE
78 | bus_MV_192_0_node_120 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6152-25_0_7_load_0 | 0 | 0.0063909 | 0.0016017 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6152-25_0_7_load_1 | 1 | 0.0053865 | 0.00135 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6152-25_0_7_load_2 | 2 | 0.0047117 | 0.0011809 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6152-25_0_7_load_3 | 3 | 0.0058373 | 0.001463 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6152-25_0_7_load_4 | 4 | 0.0058388 | 0.0014633 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6152-25_0_7_load_5 | 5 | 0.0041897 | 0.00105 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6152-25_0_7_load_48 | 6 | 0.0064725 | 0.0016222 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6152-25_0_7_load_67 | 9 | 0.005969 | 0.001496 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6152-25_0_7_load_69 | 11 | 0.0048091 | 0.0012053 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6152-25_0_7_load_6 | 12 | 0.0059796 | 0.0014986 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6152-25_0_7_load_8 | 14 | 0.0069949 | 0.0017531 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6152-25_0_7_load_9 | 15 | 0.0069416 | 0.0017397 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6152-25_0_7_load_75 | 16 | 0.0046693 | 0.0011702 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6152-25_0_7_load_10 | 17 | 0.0065415 | 0.0016395 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6152-25_0_7_load_22 | 18 | 0.0066707 | 0.0016718 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6152-25_0_7_load_23 | 19 | 0.005987 | 0.0015005 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6152-25_0_7_load_63 | 20 | 0.0036696 | 0.00091968 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6152-25_0_7_load_76 | 21 | 0.0058641 | 0.0014697 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6152-25_0_7_load_11 | 23 | 0.0044836 | 0.0011237 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6152-25_0_7_load_12 | 24 | 0.0085328 | 0.0021385 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6152-25_0_7_load_13 | 25 | 0.0037516 | 0.00094025 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6152-25_0_7_load_57 | 27 | 0.0071697 | 0.0017969 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6152-25_0_7_load_66 | 30 | 0.010749 | 0.002694 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6152-25_0_7_load_24 | 32 | 0.0081288 | 0.0020373 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6152-25_0_7_load_20 | 33 | 0.019181 | 0.0048071 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6152-25_0_7_load_18 | 34 | 0.014953 | 0.0037476 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6152-25_0_7_load_15 | 35 | 0.013973 | 0.003502 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6152-25_0_7_load_16 | 36 | 0.022037 | 0.005523 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6152-25_0_7_load_17 | 37 | 0.010853 | 0.00272 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6152-25_0_7_load_61 | 38 | 0.0067486 | 0.0016914 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6152-25_0_7_load_64 | 39 | 0.008486 | 0.0021268 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6152-25_0_7_load_49 | 44 | 0.0049938 | 0.0012516 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6152-25_0_7_load_25 | 45 | 0.0030844 | 0.00077302 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6152-25_0_7_load_26 | 46 | 0.0032775 | 0.00082143 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6152-25_0_7_load_27 | 47 | 0.002731 | 0.00068446 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6152-25_0_7_load_28 | 48 | 0.003206 | 0.00080351 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6152-25_0_7_load_29 | 49 | 0.0027298 | 0.00068414 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6152-25_0_7_load_30 | 50 | 0.0042841 | 0.0010737 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6152-25_0_7_load_77 | 51 | 0.0069921 | 0.0017524 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6152-25_0_7_load_31 | 52 | 0.0039997 | 0.0010024 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6152-25_0_7_load_32 | 56 | 0.0030323 | 0.00075997 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6152-25_0_7_load_56 | 58 | 0.015472 | 0.0038775 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6152-25_0_7_load_79 | 60 | 0.015428 | 0.0038667 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6152-25_0_7_load_72 | 63 | 0.039052 | 0.0097874 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6152-25_0_7_load_50 | 65 | 0.0058899 | 0.0014762 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6152-25_0_7_load_46 | 66 | 0.0067973 | 0.0017036 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6152-25_0_7_load_51 | 67 | 0.022209 | 0.005566 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6152-25_0_7_load_80 | 70 | 0.038293 | 0.0095972 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6152-25_0_7_load_70 | 71 | 0.035703 | 0.0089479 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6152-25_0_7_load_55 | 72 | 0.015926 | 0.0039913 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6152-25_0_7_load_73 | 73 | 0.028994 | 0.0072665 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6152-25_0_7_load_78 | 74 | 0.015433 | 0.0038679 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6152-25_0_7_load_53 | 75 | 0.014149 | 0.003546 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6152-25_0_7_load_54 | 76 | 0.02259 | 0.0056617 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6152-25_0_7_line_0 |  | 0 | 1 | 0.0030699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6152-25_0_7_line_1 |  | 0 | 2 | 0.024115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6152-25_0_7_line_2 |  | 1 | 3 | 0.012031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6152-25_0_7_line_3 |  | 2 | 4 | 0.013028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6152-25_0_7_line_4 |  | 3 | 5 | 0.017765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6152-25_0_7_line_5 |  | 4 | 6 | 0.0083246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6152-25_0_7_line_6 |  | 5 | 7 | 0.045194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6152-25_0_7_line_7 |  | 6 | 8 | 0.0015103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6152-25_0_7_line_8 |  | 7 | 9 | 0.018106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6152-25_0_7_line_9 |  | 8 | 44 | 0.013856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6152-25_0_7_line_10 |  | 8 | 66 | 0.033275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6152-25_0_7_line_11 |  | 9 | 10 | 0.0064131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6152-25_0_7_line_12 |  | 10 | 11 | 0.017139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6152-25_0_7_line_13 |  | 11 | 16 | 0.0062892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6152-25_0_7_line_14 |  | 12 | 13 | 0.012448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6152-25_0_7_line_15 |  | 13 | 14 | 0.012641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6152-25_0_7_line_16 |  | 13 | 15 | 0.014344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6152-25_0_7_line_17 |  | 14 | 17 | 0.0011537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6152-25_0_7_line_18 |  | 15 | 18 | 0.019358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6152-25_0_7_line_19 |  | 18 | 19 | 0.0029761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6152-25_0_7_line_20 |  | 19 | 28 | 0.014798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6152-25_0_7_line_21 |  | 20 | 21 | 0.012659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6152-25_0_7_line_22 |  | 20 | 22 | 0.015754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6152-25_0_7_line_23 |  | 22 | 27 | 0.026605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6152-25_0_7_line_24 |  | 23 | 24 | 0.019728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6152-25_0_7_line_25 |  | 23 | 25 | 0.022407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6152-25_0_7_line_26 |  | 24 | 26 | 0.01563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6152-25_0_7_line_27 |  | 25 | 27 | 0.040763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6152-25_0_7_line_28 |  | 26 | 28 | 0.051069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_6152-25_0_7_line_29 |  | 26 | 29 | 0.031239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_6152-25_0_7_line_30 |  | 28 | 32 | 0.0014741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6152-25_0_7_line_31 |  | 29 | 33 | 0.021712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_6152-25_0_7_line_32 |  | 29 | 34 | 0.027545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6152-25_0_7_line_33 |  | 30 | 31 | 0.037175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6152-25_0_7_line_34 |  | 31 | 39 | 0.016464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6152-25_0_7_line_35 |  | 32 | 44 | 0.01976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6152-25_0_7_line_36 |  | 33 | 41 | 0.021526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_6152-25_0_7_line_37 |  | 34 | 36 | 0.018895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6152-25_0_7_line_38 |  | 35 | 36 | 0.0039902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6152-25_0_7_line_39 |  | 35 | 37 | 0.026282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6152-25_0_7_line_40 |  | 38 | 39 | 0.024349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6152-25_0_7_line_41 |  | 38 | 40 | 0.027057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6152-25_0_7_line_42 |  | 40 | 77 | 0.003979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6152-25_0_7_line_43 |  | 41 | 42 | 0.041992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_6152-25_0_7_line_44 |  | 41 | 43 | 0.019373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6152-25_0_7_line_45 |  | 42 | 57 | 0.089627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6152-25_0_7_line_46 |  | 42 | 58 | 0.02107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6152-25_0_7_line_47 |  | 43 | 67 | 0.014719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6152-25_0_7_line_48 |  | 43 | 61 | 0.094495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6152-25_0_7_line_49 |  | 45 | 46 | 0.00037795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6152-25_0_7_line_50 |  | 45 | 47 | 0.021341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6152-25_0_7_line_51 |  | 46 | 48 | 0.022565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6152-25_0_7_line_52 |  | 47 | 49 | 0.00034277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6152-25_0_7_line_53 |  | 48 | 50 | 0.029703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6152-25_0_7_line_54 |  | 49 | 51 | 0.011152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6152-25_0_7_line_55 |  | 50 | 52 | 0.00090461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6152-25_0_7_line_56 |  | 52 | 53 | 0.023186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6152-25_0_7_line_57 |  | 53 | 54 | 0.069994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6152-25_0_7_line_58 |  | 53 | 55 | 0.022043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6152-25_0_7_line_59 |  | 54 | 66 | 0.022277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6152-25_0_7_line_60 |  | 54 | 64 | 0.01934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6152-25_0_7_line_61 |  | 55 | 56 | 0.053562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6152-25_0_7_line_62 |  | 57 | 59 | 0.099331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6152-25_0_7_line_63 |  | 57 | 60 | 0.03937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6152-25_0_7_line_64 |  | 58 | 72 | 0.034886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6152-25_0_7_line_65 |  | 59 | 73 | 0.053963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6152-25_0_7_line_66 |  | 60 | 74 | 0.0131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6152-25_0_7_line_67 |  | 61 | 62 | 0.044558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6152-25_0_7_line_68 |  | 61 | 63 | 0.027779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6152-25_0_7_line_69 |  | 62 | 70 | 0.005965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6152-25_0_7_line_70 |  | 63 | 68 | 0.026274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6152-25_0_7_line_71 |  | 64 | 65 | 0.016537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_6152-25_0_7_line_72 |  | 68 | 69 | 0.085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_6152-25_0_7_line_73 |  | 69 | 71 | 0.020336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_6152-25_0_7_line_74 |  | 72 | 76 | 0.035032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_6152-25_0_7_line_75 |  | 75 | 76 | 0.027034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_6152-25_0_7_line_76 |  | 75 | 77 | 0.041765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6152-25_0_7_trafo_19 | 0.63 MVA 20/0.4 kV | 78 | 29 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2562052.3174 | 1124822.4849 | 2562054.9558 | 1124824.0544
1 | 2562052.3174 | 1124822.4849 | 2562031.5919 | 1124810.1567
2 | 2562065.2961 | 1124830.2051 | 2562054.9558 | 1124824.0544
3 | 2562031.5919 | 1124810.1567 | 2562029.8262 | 1124809.1064 | 2562024.8787 | 1124808.1259 | 2562022.2988 | 1124808.5312 | 2562020.0341 | 1124810.024 | 2562019.6604 | 1124810.5006
4 | 2562065.2961 | 1124830.2051 | 2562065.2961 | 1124830.2051 | 2562057.574 | 1124846.204
5 | 2562019.6604 | 1124810.5006 | 2562017.6864 | 1124813.0181 | 2562014.927 | 1124817.3373
6 | 2562057.574 | 1124846.204 | 2562096.3697 | 1124869.3853
7 | 2562014.1139 | 1124818.6101 | 2562014.927 | 1124817.3373
8 | 2562096.3697 | 1124869.3853 | 2562114.1298 | 1124872.9104
9 | 2562014.1139 | 1124818.6101 | 2562006.6559 | 1124830.2872
10 | 2562014.1139 | 1124818.6101 | 2561985.2747 | 1124802.0116
11 | 2562120.4201 | 1124874.1589 | 2562114.1298 | 1124872.9104
12 | 2562120.4201 | 1124874.1589 | 2562116.085 | 1124885.9921 | 2562113.6476 | 1124889.8179
13 | 2562110.2683 | 1124895.1222 | 2562113.6476 | 1124889.8179
14 | 2562040.3728 | 1124875.3959 | 2562041.1996 | 1124875.713 | 2562042.5698 | 1124875.4043 | 2562047.0662 | 1124866.2963
15 | 2562040.3728 | 1124875.3959 | 2562034.7999 | 1124886.742
16 | 2562040.3728 | 1124875.3959 | 2562038.3095 | 1124874.5973 | 2562028.1311 | 1124867.9961
17 | 2562034.7999 | 1124886.742 | 2562034.2913 | 1124887.7775
18 | 2562011.8896 | 1124857.4626 | 2562028.1311 | 1124867.9961
19 | 2562011.8896 | 1124857.4626 | 2562009.3926 | 1124855.8431
20 | 2561996.3659 | 1124848.8371 | 2562007.9055 | 1124854.8786 | 2562009.3926 | 1124855.8431
21 | 2562098.5474 | 1124925.7812 | 2562086.1549 | 1124923.1979
22 | 2562070.7326 | 1124919.9831 | 2562086.1549 | 1124923.1979
23 | 2562070.7326 | 1124919.9831 | 2562063.6666 | 1124933.9235 | 2562058.7611 | 1124943.7419
24 | 2561987.4339 | 1124901.564 | 2562004.1271 | 1124912.0771
25 | 2562023.0876 | 1124924.0182 | 2562004.1271 | 1124912.0771
26 | 2561973.5278 | 1124894.5375 | 2561981.9296 | 1124898.0975 | 2561987.4339 | 1124901.564
27 | 2562023.0876 | 1124924.0182 | 2562058.7611 | 1124943.7419
28 | 2561973.5278 | 1124894.5375 | 2561996.3659 | 1124848.8371
29 | 2561973.5278 | 1124894.5375 | 2561967.3925 | 1124902.0133 | 2561964.8261 | 1124904.553 | 2561961.8377 | 1124906.1726 | 2561956.9047 | 1124906.2593 | 2561952.7366 | 1124905.4074 | 2561948.036 | 1124908.1273
30 | 2561996.3659 | 1124848.8371 | 2561997.0382 | 1124847.5252
31 | 2561948.036 | 1124908.1273 | 2561945.0495 | 1124906.3897 | 2561929.1965 | 1124897.3347
32 | 2561948.036 | 1124908.1273 | 2561971.5323 | 1124922.5026
33 | 2562101.5166 | 1125005.1551 | 2562103.5336 | 1124987.5669 | 2562107.5535 | 1124968.5209
34 | 2562101.5166 | 1125005.1551 | 2562085.4038 | 1125001.7725
35 | 2562006.6559 | 1124830.2872 | 2562002.6865 | 1124836.5022 | 2561997.0382 | 1124847.5252
36 | 2561910.4828 | 1124886.6978 | 2561911.6507 | 1124887.3129 | 2561929.1965 | 1124897.3347
37 | 2561971.5323 | 1124922.5026 | 2561975.1751 | 1124924.7313 | 2561987.8753 | 1124931.983
38 | 2561987.8753 | 1124931.983 | 2561991.3404 | 1124933.9615
39 | 2562013.9746 | 1124947.3041 | 2562008.7591 | 1124943.9073 | 2561991.3404 | 1124933.9615
40 | 2562061.5745 | 1124996.7699 | 2562085.4038 | 1125001.7725
41 | 2562035.1341 | 1124991.0319 | 2562045.7331 | 1124993.4442 | 2562061.5745 | 1124996.7699
42 | 2562031.4855 | 1124989.4207 | 2562035.1341 | 1124991.0319
43 | 2561910.4828 | 1124886.6978 | 2561888.361 | 1124922.4222
44 | 2561910.4828 | 1124886.6978 | 2561920.6853 | 1124870.2139
45 | 2561888.361 | 1124922.4222 | 2561877.4012 | 1124941.0231 | 2561849.9367 | 1124987.5647 | 2561862.0222 | 1124994.6252
46 | 2561888.361 | 1124922.4222 | 2561906.375 | 1124933.3514
47 | 2561920.6853 | 1124870.2139 | 2561927.9007 | 1124857.3847
48 | 2561867.7185 | 1124928.7336 | 2561906.8839 | 1124861.2409 | 2561915.1663 | 1124866.6247 | 2561920.6853 | 1124870.2139
49 | 2562064.3487 | 1124772.8796 | 2562064.6682 | 1124773.0816
50 | 2562064.6682 | 1124773.0816 | 2562068.5833 | 1124775.5567 | 2562083.3793 | 1124783.321
51 | 2562045.0752 | 1124761.1882 | 2562045.8464 | 1124761.5259 | 2562053.8532 | 1124766 | 2562059.0945 | 1124769.5578 | 2562064.3487 | 1124772.8796
52 | 2562083.3793 | 1124783.321 | 2562083.6828 | 1124783.4803
53 | 2562045.0752 | 1124761.1882 | 2562041.216 | 1124759.4984 | 2562038.6375 | 1124757.6804 | 2562036.9374 | 1124753.3445 | 2562034.0529 | 1124749.4495 | 2562023.0588 | 1124743.1266 | 2562022.9303 | 1124743.0519
54 | 2562093.5575 | 1124788.662 | 2562083.6828 | 1124783.4803
55 | 2562022.148 | 1124742.5976 | 2562022.9303 | 1124743.0519
56 | 2562002.0987 | 1124730.9523 | 2562022.148 | 1124742.5976
57 | 2561965.9673 | 1124790.8992 | 2561973.7184 | 1124778.0328 | 2562002.0987 | 1124730.9523
58 | 2562013.4814 | 1124712.06 | 2562002.0987 | 1124730.9523
59 | 2561965.9673 | 1124790.8992 | 2561985.2747 | 1124802.0116
60 | 2561965.9673 | 1124790.8992 | 2561955.9733 | 1124807.4706
61 | 2562013.4814 | 1124712.06 | 2562037.8191 | 1124728.0705 | 2562058.9827 | 1124740.2737
62 | 2561947.9811 | 1125044.8192 | 2561862.0222 | 1124994.6252
63 | 2561862.0222 | 1124994.6252 | 2561866.8227 | 1124987.0022 | 2561882.5786 | 1124961.0489
64 | 2561936.1621 | 1124951.5103 | 2561927.1685 | 1124945.967 | 2561906.375 | 1124933.3514
65 | 2561947.9811 | 1125044.8192 | 2561974.9511 | 1124998.0796
66 | 2561889.377 | 1124949.8507 | 2561882.5786 | 1124961.0489
67 | 2561844.3246 | 1124902.2124 | 2561838.6786 | 1124911.464 | 2561844.5697 | 1124915.3731 | 2561867.7185 | 1124928.7336
68 | 2561867.7185 | 1124928.7336 | 2561853.7749 | 1124952.7599
69 | 2561844.3246 | 1124902.2124 | 2561849.3709 | 1124905.4155
70 | 2561840.5869 | 1124975.4844 | 2561853.7749 | 1124952.7599
71 | 2561955.9733 | 1124807.4706 | 2561968.1018 | 1124815.2204 | 2561969.9759 | 1124816.2607
72 | 2561785.1217 | 1124928.9673 | 2561791.657 | 1124934.7844 | 2561797.7162 | 1124939.693 | 2561801.8302 | 1124942.9686 | 2561802.538 | 1124943.9646 | 2561802.0701 | 1124944.3233 | 2561801.1132 | 1124946.5972 | 2561798.8408 | 1124950.5136 | 2561796.9456 | 1124953.1158 | 2561807.5395 | 1124958.3403 | 2561808.6761 | 1124956.4544 | 2561832.1842 | 1124970.5683 | 2561840.5869 | 1124975.4844
73 | 2561785.1217 | 1124928.9673 | 2561784.8969 | 1124928.7686 | 2561776.9352 | 1124920.4704 | 2561771.0202 | 1124914.3163
74 | 2561966.4722 | 1124969.0471 | 2561951.5919 | 1124961.0206 | 2561936.1621 | 1124951.5103
75 | 2561990.4854 | 1124981.4618 | 2561974 | 1124973.1077 | 2561966.4722 | 1124969.0471
76 | 2561990.4854 | 1124981.4618 | 2562031.4855 | 1124989.4207

## bus_geodata
| x | y | coords
0 | 2562052.3174 | 1124822.4849
1 | 2562054.9558 | 1124824.0543
2 | 2562031.5919 | 1124810.1567
3 | 2562065.2961 | 1124830.2051
4 | 2562019.6604 | 1124810.5006
5 | 2562057.574 | 1124846.204
6 | 2562014.927 | 1124817.3373
7 | 2562096.3697 | 1124869.3853
8 | 2562014.1139 | 1124818.6101
9 | 2562114.1298 | 1124872.9104
10 | 2562120.4201 | 1124874.1589
11 | 2562113.6476 | 1124889.8179
12 | 2562047.0662 | 1124866.2963
13 | 2562040.3728 | 1124875.3959
14 | 2562034.7999 | 1124886.742
15 | 2562028.1311 | 1124867.9961
16 | 2562110.2683 | 1124895.1222
17 | 2562034.2913 | 1124887.7775
18 | 2562011.8896 | 1124857.4626
19 | 2562009.3926 | 1124855.8431
20 | 2562086.1549 | 1124923.1979
21 | 2562098.5474 | 1124925.7812
22 | 2562070.7326 | 1124919.9831
23 | 2562004.1271 | 1124912.0771
24 | 2561987.4339 | 1124901.564
25 | 2562023.0876 | 1124924.0182
26 | 2561973.5278 | 1124894.5375
27 | 2562058.7611 | 1124943.7419
28 | 2561996.3659 | 1124848.8371
29 | 2561948.036 | 1124908.1273
30 | 2562107.5535 | 1124968.5209
31 | 2562101.5166 | 1125005.1551
32 | 2561997.0382 | 1124847.5252
33 | 2561929.1965 | 1124897.3347
34 | 2561971.5323 | 1124922.5026
35 | 2561991.3404 | 1124933.9615
36 | 2561987.8753 | 1124931.983
37 | 2562013.9746 | 1124947.3041
38 | 2562061.5745 | 1124996.7699
39 | 2562085.4038 | 1125001.7725
40 | 2562035.1341 | 1124991.0319
41 | 2561910.4828 | 1124886.6978
42 | 2561888.361 | 1124922.4222
43 | 2561920.6853 | 1124870.2139
44 | 2562006.6559 | 1124830.2872
45 | 2562064.6682 | 1124773.0816
46 | 2562064.3487 | 1124772.8796
47 | 2562083.3793 | 1124783.321
48 | 2562045.0752 | 1124761.1882
49 | 2562083.6828 | 1124783.4803
50 | 2562022.9303 | 1124743.0519
51 | 2562093.5575 | 1124788.662
52 | 2562022.148 | 1124742.5976
53 | 2562002.0987 | 1124730.9523
54 | 2561965.9673 | 1124790.8992
55 | 2562013.4814 | 1124712.06
56 | 2562058.9827 | 1124740.2737
57 | 2561862.0222 | 1124994.6252
58 | 2561906.375 | 1124933.3514
59 | 2561947.9811 | 1125044.8192
60 | 2561882.5786 | 1124961.0489
61 | 2561867.7185 | 1124928.7336
62 | 2561844.3246 | 1124902.2124
63 | 2561853.7749 | 1124952.7599
64 | 2561955.9733 | 1124807.4706
65 | 2561969.9759 | 1124816.2607
66 | 2561985.2747 | 1124802.0116
67 | 2561927.9007 | 1124857.3847
68 | 2561840.5869 | 1124975.4844
69 | 2561785.1217 | 1124928.9673
70 | 2561849.3709 | 1124905.4155
71 | 2561771.0202 | 1124914.3163
72 | 2561936.1621 | 1124951.5103
73 | 2561974.9511 | 1124998.0796
74 | 2561889.377 | 1124949.8507
75 | 2561990.4854 | 1124981.4618
76 | 2561966.4722 | 1124969.0471
77 | 2562031.4855 | 1124989.4207
78 | 2561973.5278 | 1124894.5375

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1