## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6152-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6152-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6152-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6152-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6152-4_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6152-4_0_4_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_6152-4_0_4_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_6152-4_0_4_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_6152-4_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_6152-4_0_4_node_27 | 0.4 | n |  | TRUE
10 | bus_LV_6152-4_0_4_node_71 | 0.4 | n |  | TRUE
11 | bus_LV_6152-4_0_4_node_70 | 0.4 | n |  | TRUE
12 | bus_LV_6152-4_0_4_node_69 | 0.4 | n |  | TRUE
13 | bus_LV_6152-4_0_4_node_68 | 0.4 | n |  | TRUE
14 | bus_LV_6152-4_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_6152-4_0_4_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_6152-4_0_4_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_6152-4_0_4_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_6152-4_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_6152-4_0_4_node_31 | 0.4 | n |  | TRUE
20 | bus_LV_6152-4_0_4_node_32 | 0.4 | n |  | TRUE
21 | bus_LV_6152-4_0_4_node_33 | 0.4 | n |  | TRUE
22 | bus_LV_6152-4_0_4_node_34 | 0.4 | n |  | TRUE
23 | bus_LV_6152-4_0_4_node_35 | 0.4 | n |  | TRUE
24 | bus_LV_6152-4_0_4_node_36 | 0.4 | n |  | TRUE
25 | bus_LV_6152-4_0_4_node_99 | 0.4 | n |  | TRUE
26 | bus_LV_6152-4_0_4_node_85 | 0.4 | n |  | TRUE
27 | bus_LV_6152-4_0_4_node_83 | 0.4 | n |  | TRUE
28 | bus_LV_6152-4_0_4_node_84 | 0.4 | n |  | TRUE
29 | bus_LV_6152-4_0_4_node_86 | 0.4 | n |  | TRUE
30 | bus_LV_6152-4_0_4_node_95 | 0.4 | n |  | TRUE
31 | bus_LV_6152-4_0_4_node_96 | 0.4 | n |  | TRUE
32 | bus_LV_6152-4_0_4_node_97 | 0.4 | n |  | TRUE
33 | bus_LV_6152-4_0_4_node_98 | 0.4 | n |  | TRUE
34 | bus_LV_6152-4_0_4_node_93 | 0.4 | n |  | TRUE
35 | bus_LV_6152-4_0_4_node_108 | 0.4 | n |  | TRUE
36 | bus_LV_6152-4_0_4_node_104 | 0.4 | n |  | TRUE
37 | bus_LV_6152-4_0_4_node_105 | 0.4 | n |  | TRUE
38 | bus_LV_6152-4_0_4_node_103 | 0.4 | n |  | TRUE
39 | bus_LV_6152-4_0_4_node_106 | 0.4 | n |  | TRUE
40 | bus_LV_6152-4_0_4_node_79 | 0.4 | n |  | TRUE
41 | bus_LV_6152-4_0_4_node_81 | 0.4 | n |  | TRUE
42 | bus_LV_6152-4_0_4_node_77 | 0.4 | n |  | TRUE
43 | bus_LV_6152-4_0_4_node_87 | 0.4 | n |  | TRUE
44 | bus_LV_6152-4_0_4_node_88 | 0.4 | n |  | TRUE
45 | bus_LV_6152-4_0_4_node_110 | 0.4 | n |  | TRUE
46 | bus_LV_6152-4_0_4_node_112 | 0.4 | n |  | TRUE
47 | bus_LV_6152-4_0_4_node_89 | 0.4 | n |  | TRUE
48 | bus_LV_6152-4_0_4_node_90 | 0.4 | n |  | TRUE
49 | bus_LV_6152-4_0_4_node_91 | 0.4 | n |  | TRUE
50 | bus_LV_6152-4_0_4_node_94 | 0.4 | n |  | TRUE
51 | bus_LV_6152-4_0_4_node_107 | 0.4 | n |  | TRUE
52 | bus_LV_6152-4_0_4_node_111 | 0.4 | n |  | TRUE
53 | bus_LV_6152-4_0_4_node_82 | 0.4 | n |  | TRUE
54 | bus_LV_6152-4_0_4_node_67 | 0.4 | n |  | TRUE
55 | bus_LV_6152-4_0_4_node_13 | 0.4 | n |  | TRUE
56 | bus_LV_6152-4_0_4_node_14 | 0.4 | n |  | TRUE
57 | bus_LV_6152-4_0_4_node_15 | 0.4 | n |  | TRUE
58 | bus_LV_6152-4_0_4_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_6152-4_0_4_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_6152-4_0_4_node_101 | 0.4 | n |  | TRUE
61 | bus_LV_6152-4_0_4_node_16 | 0.4 | n |  | TRUE
62 | bus_LV_6152-4_0_4_node_17 | 0.4 | n |  | TRUE
63 | bus_LV_6152-4_0_4_node_18 | 0.4 | n |  | TRUE
64 | bus_LV_6152-4_0_4_node_19 | 0.4 | n |  | TRUE
65 | bus_LV_6152-4_0_4_node_20 | 0.4 | n |  | TRUE
66 | bus_LV_6152-4_0_4_node_100 | 0.4 | n |  | TRUE
67 | bus_LV_6152-4_0_4_node_22 | 0.4 | n |  | TRUE
68 | bus_LV_6152-4_0_4_node_21 | 0.4 | n |  | TRUE
69 | bus_LV_6152-4_0_4_node_25 | 0.4 | n |  | TRUE
70 | bus_LV_6152-4_0_4_node_23 | 0.4 | n |  | TRUE
71 | bus_LV_6152-4_0_4_node_63 | 0.4 | n |  | TRUE
72 | bus_LV_6152-4_0_4_node_65 | 0.4 | n |  | TRUE
73 | bus_LV_6152-4_0_4_node_66 | 0.4 | n |  | TRUE
74 | bus_LV_6152-4_0_4_node_24 | 0.4 | n |  | TRUE
75 | bus_LV_6152-4_0_4_node_61 | 0.4 | n |  | TRUE
76 | bus_LV_6152-4_0_4_node_26 | 0.4 | n |  | TRUE
77 | bus_LV_6152-4_0_4_node_28 | 0.4 | n |  | TRUE
78 | bus_LV_6152-4_0_4_node_30 | 0.4 | n |  | TRUE
79 | bus_LV_6152-4_0_4_node_80 | 0.4 | n |  | TRUE
80 | bus_LV_6152-4_0_4_node_46 | 0.4 | n |  | TRUE
81 | bus_LV_6152-4_0_4_node_78 | 0.4 | n |  | TRUE
82 | bus_LV_6152-4_0_4_node_109 | 0.4 | n |  | TRUE
83 | bus_LV_6152-4_0_4_node_92 | 0.4 | n |  | TRUE
84 | bus_LV_6152-4_0_4_node_37 | 0.4 | n |  | TRUE
85 | bus_LV_6152-4_0_4_node_38 | 0.4 | n |  | TRUE
86 | bus_LV_6152-4_0_4_node_39 | 0.4 | n |  | TRUE
87 | bus_LV_6152-4_0_4_node_40 | 0.4 | n |  | TRUE
88 | bus_LV_6152-4_0_4_node_41 | 0.4 | n |  | TRUE
89 | bus_LV_6152-4_0_4_node_42 | 0.4 | n |  | TRUE
90 | bus_LV_6152-4_0_4_node_47 | 0.4 | n |  | TRUE
91 | bus_LV_6152-4_0_4_node_48 | 0.4 | n |  | TRUE
92 | bus_LV_6152-4_0_4_node_50 | 0.4 | n |  | TRUE
93 | bus_LV_6152-4_0_4_node_72 | 0.4 | n |  | TRUE
94 | bus_LV_6152-4_0_4_node_73 | 0.4 | n |  | TRUE
95 | bus_LV_6152-4_0_4_node_57 | 0.4 | n |  | TRUE
96 | bus_LV_6152-4_0_4_node_74 | 0.4 | n |  | TRUE
97 | bus_LV_6152-4_0_4_node_56 | 0.4 | n |  | TRUE
98 | bus_LV_6152-4_0_4_node_51 | 0.4 | n |  | TRUE
99 | bus_LV_6152-4_0_4_node_52 | 0.4 | n |  | TRUE
100 | bus_LV_6152-4_0_4_node_53 | 0.4 | n |  | TRUE
101 | bus_LV_6152-4_0_4_node_54 | 0.4 | n |  | TRUE
102 | bus_LV_6152-4_0_4_node_55 | 0.4 | n |  | TRUE
103 | bus_LV_6152-4_0_4_node_58 | 0.4 | n |  | TRUE
104 | bus_LV_6152-4_0_4_node_59 | 0.4 | n |  | TRUE
105 | bus_LV_6152-4_0_4_node_60 | 0.4 | n |  | TRUE
106 | bus_LV_6152-4_0_4_node_64 | 0.4 | n |  | TRUE
107 | bus_LV_6152-4_0_4_node_62 | 0.4 | n |  | TRUE
108 | bus_LV_6152-4_0_4_node_75 | 0.4 | n |  | TRUE
109 | bus_LV_6152-4_0_4_node_76 | 0.4 | n |  | TRUE
110 | bus_LV_6152-4_0_4_node_102 | 0.4 | n |  | TRUE
111 | bus_MV_192_0_node_63 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6152-4_0_4_load_0 | 0 | 0.0016697 | 0.00041846 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6152-4_0_4_load_1 | 1 | 0.00067835 | 0.00017001 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6152-4_0_4_load_10 | 7 | 0.00072033 | 0.00018053 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6152-4_0_4_load_71 | 10 | 0.001303 | 0.00032655 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6152-4_0_4_load_11 | 14 | 0.0021551 | 0.00054011 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6152-4_0_4_load_6 | 15 | 0.0045159 | 0.0011318 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6152-4_0_4_load_7 | 17 | 0.0036383 | 0.00091183 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6152-4_0_4_load_9 | 18 | 0.0005158 | 0.00012927 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6152-4_0_4_load_31 | 19 | 0.00072158 | 0.00018085 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6152-4_0_4_load_32 | 20 | 0.00060527 | 0.00015169 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6152-4_0_4_load_33 | 21 | 0.0023502 | 0.00058903 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6152-4_0_4_load_34 | 22 | 0.0017654 | 0.00044246 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6152-4_0_4_load_35 | 23 | 0.0023994 | 0.00060136 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6152-4_0_4_load_83 | 27 | 0.0014555 | 0.00036478 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6152-4_0_4_load_84 | 28 | 0.00016362 | 4.1008e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6152-4_0_4_load_95 | 30 | 0.00063698 | 0.00015964 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6152-4_0_4_load_96 | 31 | 0.00065183 | 0.00016336 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6152-4_0_4_load_108 | 35 | 0.00055531 | 0.00013917 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6152-4_0_4_load_105 | 37 | 0.00077101 | 0.00019323 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6152-4_0_4_load_106 | 39 | 0.0011884 | 0.00029784 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6152-4_0_4_load_79 | 40 | 0.00041872 | 0.00010494 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6152-4_0_4_load_81 | 41 | 0.00040837 | 0.00010235 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6152-4_0_4_load_77 | 42 | 0.00043209 | 0.00010829 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6152-4_0_4_load_87 | 43 | 0.00039114 | 9.8029e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6152-4_0_4_load_112 | 46 | 0.00036565 | 9.164e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6152-4_0_4_load_89 | 47 | 0.0022348 | 0.0005601 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6152-4_0_4_load_90 | 48 | 0.003934 | 0.00098595 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6152-4_0_4_load_94 | 50 | 0.0017288 | 0.00043327 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6152-4_0_4_load_107 | 51 | 0.00099109 | 0.00024839 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6152-4_0_4_load_111 | 52 | 0.00028957 | 7.2574e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6152-4_0_4_load_67 | 54 | 0.00063541 | 0.00015925 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6152-4_0_4_load_13 | 55 | 0.00054696 | 0.00013708 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6152-4_0_4_load_14 | 56 | 0.00059628 | 0.00014944 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6152-4_0_4_load_45 | 58 | 0.0068768 | 0.0017235 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6152-4_0_4_load_44 | 59 | 0.00020091 | 5.0353e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6152-4_0_4_load_16 | 61 | 0.00018685 | 4.683e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6152-4_0_4_load_17 | 62 | 0.00010625 | 2.663e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6152-4_0_4_load_18 | 63 | 0.00010897 | 2.731e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6152-4_0_4_load_20 | 65 | 0.00011439 | 2.8668e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6152-4_0_4_load_22 | 67 | 0.0003731 | 9.3507e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6152-4_0_4_load_21 | 68 | 0.00027758 | 6.9568e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6152-4_0_4_load_25 | 69 | 0.00074504 | 0.00018673 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6152-4_0_4_load_23 | 70 | 0.001561 | 0.00039122 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6152-4_0_4_load_63 | 71 | 0.014551 | 0.0036469 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6152-4_0_4_load_65 | 72 | 0.0084093 | 0.0021076 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6152-4_0_4_load_66 | 73 | 0.0028728 | 0.00071999 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6152-4_0_4_load_24 | 74 | 0.00010765 | 2.698e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6152-4_0_4_load_61 | 75 | 0.003541 | 0.00088745 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6152-4_0_4_load_26 | 76 | 0.0051164 | 0.0012823 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6152-4_0_4_load_46 | 80 | 0.0031234 | 0.00078281 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6152-4_0_4_load_78 | 81 | 0.00043602 | 0.00010928 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6152-4_0_4_load_109 | 82 | 0.00034076 | 8.5404e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6152-4_0_4_load_92 | 83 | 0.0069705 | 0.001747 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6152-4_0_4_load_37 | 84 | 0.0001416 | 3.5489e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6152-4_0_4_load_39 | 86 | 0.00056242 | 0.00014096 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6152-4_0_4_load_40 | 87 | 0.00018408 | 4.6135e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6152-4_0_4_load_41 | 88 | 0.00080884 | 0.00020271 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6152-4_0_4_load_42 | 89 | 0.0015086 | 0.00037809 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6152-4_0_4_load_47 | 90 | 0.00020243 | 5.0733e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6152-4_0_4_load_72 | 93 | 0.0017594 | 0.00044095 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6152-4_0_4_load_57 | 95 | 0.0005539 | 0.00013882 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6152-4_0_4_load_74 | 96 | 0.0013008 | 0.00032601 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6152-4_0_4_load_56 | 97 | 0.0013697 | 0.00034327 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_6152-4_0_4_load_51 | 98 | 0.00049875 | 0.000125 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_6152-4_0_4_load_52 | 99 | 0.0038798 | 0.00097237 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_6152-4_0_4_load_53 | 100 | 0.0038798 | 0.00097238 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_6152-4_0_4_load_54 | 101 | 0.00049883 | 0.00012502 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_6152-4_0_4_load_55 | 102 | 0.0020825 | 0.00052192 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_6152-4_0_4_load_58 | 103 | 0.00073054 | 0.00018309 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_6152-4_0_4_load_59 | 104 | 0.00093361 | 0.00023398 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_6152-4_0_4_load_60 | 105 | 0.00073048 | 0.00018308 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_6152-4_0_4_load_64 | 106 | 0.0020823 | 0.00052187 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_6152-4_0_4_load_62 | 107 | 0.0030347 | 0.00076057 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_6152-4_0_4_load_75 | 108 | 0.0002936 | 7.3584e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_6152-4_0_4_load_76 | 109 | 0.0040226 | 0.0010082 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_6152-4_0_4_load_102 | 110 | 0.0080649 | 0.0020213 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6152-4_0_4_line_0 |  | 0 | 1 | 0.014179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_6152-4_0_4_line_1 |  | 0 | 2 | 0.024898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_6152-4_0_4_line_2 |  | 1 | 3 | 0.019892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_6152-4_0_4_line_3 |  | 2 | 4 | 0.011523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_6152-4_0_4_line_4 |  | 3 | 5 | 0.014432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_6152-4_0_4_line_5 |  | 4 | 6 | 0.064721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_6152-4_0_4_line_6 |  | 4 | 7 | 0.023924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6152-4_0_4_line_7 |  | 5 | 13 | 0.010333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_6152-4_0_4_line_8 |  | 5 | 14 | 0.0044963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6152-4_0_4_line_9 |  | 6 | 15 | 0.039454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_6152-4_0_4_line_10 |  | 8 | 9 | 0.10903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_6152-4_0_4_line_11 |  | 8 | 10 | 0.039223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_6152-4_0_4_line_12 |  | 9 | 16 | 0.071135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_6152-4_0_4_line_13 |  | 10 | 11 | 0.033665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_6152-4_0_4_line_14 |  | 11 | 12 | 0.028116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_6152-4_0_4_line_15 |  | 12 | 54 | 0.056127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_6152-4_0_4_line_16 |  | 12 | 73 | 0.049456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_6152-4_0_4_line_17 |  | 13 | 54 | 0.028508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_6152-4_0_4_line_18 |  | 15 | 17 | 0.050782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_6152-4_0_4_line_19 |  | 16 | 58 | 0.073923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_6152-4_0_4_line_20 |  | 16 | 55 | 0.12341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6152-4_0_4_line_21 |  | 17 | 18 | 0.033652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6152-4_0_4_line_22 |  | 19 | 20 | 0.00085312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6152-4_0_4_line_23 |  | 19 | 21 | 0.014988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6152-4_0_4_line_24 |  | 20 | 22 | 0.038416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6152-4_0_4_line_25 |  | 21 | 23 | 0.011999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6152-4_0_4_line_26 |  | 22 | 24 | 0.016769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6152-4_0_4_line_27 |  | 24 | 25 | 0.036215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_6152-4_0_4_line_28 |  | 24 | 26 | 0.047396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_6152-4_0_4_line_29 |  | 25 | 37 | 0.022478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6152-4_0_4_line_30 |  | 25 | 38 | 0.082753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_6152-4_0_4_line_31 |  | 26 | 27 | 0.027017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_6152-4_0_4_line_32 |  | 27 | 28 | 0.017626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_6152-4_0_4_line_33 |  | 28 | 29 | 0.015833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_6152-4_0_4_line_34 |  | 29 | 43 | 0.017995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6152-4_0_4_line_35 |  | 29 | 44 | 0.026644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_6152-4_0_4_line_36 |  | 30 | 31 | 0.00023643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6152-4_0_4_line_37 |  | 31 | 32 | 0.018126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6152-4_0_4_line_38 |  | 32 | 33 | 0.037791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6152-4_0_4_line_39 |  | 32 | 34 | 0.036412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6152-4_0_4_line_40 |  | 33 | 35 | 0.015717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6152-4_0_4_line_41 |  | 33 | 36 | 0.017854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6152-4_0_4_line_42 |  | 34 | 51 | 0.009737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6152-4_0_4_line_43 |  | 34 | 49 | 0.008721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6152-4_0_4_line_44 |  | 36 | 39 | 0.022529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6152-4_0_4_line_45 |  | 36 | 38 | 0.028905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6152-4_0_4_line_46 |  | 40 | 41 | 0.01285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6152-4_0_4_line_47 |  | 40 | 42 | 0.085324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6152-4_0_4_line_48 |  | 42 | 81 | 0.034752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6152-4_0_4_line_49 |  | 44 | 45 | 0.024721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_6152-4_0_4_line_50 |  | 44 | 46 | 0.036346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6152-4_0_4_line_51 |  | 45 | 52 | 0.017473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6152-4_0_4_line_52 |  | 45 | 53 | 0.035435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_6152-4_0_4_line_53 |  | 47 | 48 | 0.026438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6152-4_0_4_line_54 |  | 47 | 49 | 0.035791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6152-4_0_4_line_55 |  | 48 | 83 | 0.024861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6152-4_0_4_line_56 |  | 49 | 50 | 0.055001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6152-4_0_4_line_57 |  | 53 | 82 | 0.03914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6152-4_0_4_line_58 |  | 53 | 79 | 0.023919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_6152-4_0_4_line_59 |  | 55 | 56 | 0.026358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6152-4_0_4_line_60 |  | 56 | 57 | 0.017969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6152-4_0_4_line_61 |  | 57 | 59 | 0.047523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6152-4_0_4_line_62 |  | 58 | 80 | 0.038067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_6152-4_0_4_line_63 |  | 59 | 60 | 0.028311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6152-4_0_4_line_64 |  | 60 | 66 | 0.12548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6152-4_0_4_line_65 |  | 61 | 62 | 0.016746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6152-4_0_4_line_66 |  | 61 | 63 | 0.001481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6152-4_0_4_line_67 |  | 62 | 64 | 0.022039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6152-4_0_4_line_68 |  | 63 | 65 | 0.0011586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6152-4_0_4_line_69 |  | 64 | 67 | 0.020611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6152-4_0_4_line_70 |  | 65 | 68 | 0.081549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6152-4_0_4_line_71 |  | 65 | 69 | 0.19511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_6152-4_0_4_line_72 |  | 66 | 89 | 0.20519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_6152-4_0_4_line_73 |  | 67 | 70 | 0.0024481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_6152-4_0_4_line_74 |  | 69 | 71 | 0.28074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_6152-4_0_4_line_75 |  | 70 | 74 | 0.013746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_6152-4_0_4_line_76 |  | 71 | 75 | 0.031907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_6152-4_0_4_line_77 |  | 71 | 72 | 0.079445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
78 | LV_6152-4_0_4_line_78 |  | 72 | 73 | 0.071456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_6152-4_0_4_line_79 |  | 75 | 107 | 0.015944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_6152-4_0_4_line_80 |  | 76 | 77 | 0.07634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_6152-4_0_4_line_81 |  | 77 | 78 | 0.069635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_6152-4_0_4_line_82 |  | 77 | 79 | 0.17504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_6152-4_0_4_line_83 |  | 78 | 80 | 0.041595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_6152-4_0_4_line_84 |  | 79 | 81 | 0.018626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_6152-4_0_4_line_85 |  | 84 | 85 | 0.063958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_6152-4_0_4_line_86 |  | 85 | 86 | 0.02113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_6152-4_0_4_line_87 |  | 85 | 87 | 0.031899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_6152-4_0_4_line_88 |  | 86 | 88 | 0.076852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_6152-4_0_4_line_89 |  | 88 | 89 | 0.080252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_6152-4_0_4_line_90 |  | 90 | 91 | 0.062723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_6152-4_0_4_line_91 |  | 91 | 92 | 0.031659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_6152-4_0_4_line_92 |  | 92 | 93 | 0.031046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_6152-4_0_4_line_93 |  | 92 | 94 | 0.016107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_6152-4_0_4_line_94 |  | 92 | 95 | 0.03441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_6152-4_0_4_line_95 |  | 94 | 96 | 0.048572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_6152-4_0_4_line_96 |  | 95 | 97 | 0.058361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_6152-4_0_4_line_97 |  | 96 | 108 | 0.017974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_6152-4_0_4_line_98 |  | 97 | 101 | 0.0064799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_6152-4_0_4_line_99 |  | 98 | 99 | 0.0045762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_6152-4_0_4_line_100 |  | 98 | 100 | 0.012353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_6152-4_0_4_line_101 |  | 99 | 101 | 0.0038384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_6152-4_0_4_line_102 |  | 100 | 102 | 0.017257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_6152-4_0_4_line_103 |  | 102 | 103 | 0.0015165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_6152-4_0_4_line_104 |  | 103 | 104 | 0.011244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_6152-4_0_4_line_105 |  | 104 | 105 | 0.025806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_6152-4_0_4_line_106 |  | 105 | 106 | 0.0032658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_6152-4_0_4_line_107 |  | 106 | 107 | 0.024678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_6152-4_0_4_line_108 |  | 108 | 109 | 0.026301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_6152-4_0_4_line_109 |  | 109 | 110 | 0.25934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6152-4_0_4_trafo_7 | 0.63 MVA 20/0.4 kV | 111 | 17 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2561300.7667 | 1126639.0591 | 2561301.6144 | 1126637.6047 | 2561308.3406 | 1126627.0737
1 | 2561285.051 | 1126657.6767 | 2561288.6955 | 1126653.9736 | 2561290.3417 | 1126652.3067 | 2561294.2586 | 1126650.2249 | 2561300.7667 | 1126639.0591
2 | 2561321.5046 | 1126612.3421 | 2561312.052 | 1126621.2628 | 2561308.3406 | 1126627.0737
3 | 2561276.6235 | 1126649.7934 | 2561285.051 | 1126657.6767
4 | 2561312.3433 | 1126601.7955 | 2561312.3545 | 1126603.5407 | 2561315.0548 | 1126606.4137 | 2561321.5046 | 1126612.3421
5 | 2561229.2678 | 1126605.5417 | 2561276.6235 | 1126649.7934
6 | 2561276.6235 | 1126649.7934 | 2561288.3589 | 1126632.7539 | 2561290.0995 | 1126630.028
7 | 2561312.3433 | 1126601.7955 | 2561312.3307 | 1126599.839 | 2561315.4088 | 1126596.7288 | 2561317.661 | 1126593.4127
8 | 2561312.3433 | 1126601.7955 | 2561310.0752 | 1126602.6326 | 2561308.4512 | 1126603.9301
9 | 2561229.2678 | 1126605.5417 | 2561238.052 | 1126588.5656 | 2561245.5344 | 1126569.6517
10 | 2561339.1276 | 1126708.2222 | 2561328.3107 | 1126729.1021 | 2561289.0338 | 1126805.1148
11 | 2561339.1276 | 1126708.2222 | 2561357.0265 | 1126673.3209
12 | 2561289.0338 | 1126805.1148 | 2561286.6894 | 1126809.6544 | 2561256.8982 | 1126868.6089
13 | 2561372.3891 | 1126643.3652 | 2561357.0265 | 1126673.3209
14 | 2561372.3891 | 1126643.3652 | 2561378.6229 | 1126631.2191 | 2561385.2221 | 1126618.3481
15 | 2561385.2221 | 1126618.3481 | 2561370.4784 | 1126609.7603 | 2561337.6686 | 1126588.5581
16 | 2561385.2221 | 1126618.3481 | 2561404.7913 | 1126580.1924 | 2561407.7969 | 1126574.3448
17 | 2561317.661 | 1126593.4127 | 2561320.1186 | 1126589.695 | 2561322.3536 | 1126583.6999 | 2561324.0012 | 1126582.2441 | 2561327.3072 | 1126582.2229 | 2561332.2885 | 1126585.0813 | 2561337.6686 | 1126588.5581
18 | 2561245.5344 | 1126569.6517 | 2561247.2052 | 1126565.4284 | 2561251.0707 | 1126556.5435 | 2561256.2271 | 1126554.2536 | 2561262.2014 | 1126550.9136 | 2561265.0701 | 1126547.5935 | 2561268.1585 | 1126544.8945 | 2561273.3151 | 1126543.8386 | 2561279.5372 | 1126546.6779 | 2561282.315 | 1126548.7616
19 | 2561256.8982 | 1126868.6089 | 2561206.4084 | 1126843.6429 | 2561190.8016 | 1126835.5118
20 | 2561256.8982 | 1126868.6089 | 2561331.8937 | 1126966.6166
21 | 2561309.2349 | 1126568.9543 | 2561282.315 | 1126548.7616
22 | 2561036.9728 | 1126478.4725 | 2561036.1219 | 1126478.4104
23 | 2561036.1219 | 1126478.4104 | 2561035.2818 | 1126478.349 | 2561022.7138 | 1126471.8561
24 | 2561036.9728 | 1126478.4725 | 2561040.4554 | 1126478.7269 | 2561043.7442 | 1126476.0265 | 2561057.8533 | 1126448.7963
25 | 2561012.0533 | 1126466.3486 | 2561022.7138 | 1126471.8561
26 | 2561066.4807 | 1126434.5143 | 2561063.2381 | 1126438.4038 | 2561057.8533 | 1126448.7963
27 | 2561066.4807 | 1126434.5143 | 2561041.3267 | 1126408.3967
28 | 2561099.3396 | 1126468.753 | 2561066.4807 | 1126434.5143
29 | 2561041.3267 | 1126408.3967 | 2561036.6775 | 1126414.0518 | 2561028.9085 | 1126427.0864
30 | 2560983.504 | 1126349.0513 | 2561015.6138 | 1126381.6937 | 2561041.3267 | 1126408.3967
31 | 2561099.3396 | 1126468.753 | 2561090.2801 | 1126480.0616 | 2561084.884 | 1126491.3666
32 | 2561084.884 | 1126491.3666 | 2561077.2913 | 1126507.2733
33 | 2561070.4566 | 1126521.555 | 2561070.799 | 1126520.8747 | 2561077.2913 | 1126507.2733
34 | 2561070.4566 | 1126521.555 | 2561065.5719 | 1126519.3632 | 2561054.3209 | 1126513.5106
35 | 2561058.4338 | 1126545.3447 | 2561070.4566 | 1126521.555
36 | 2560966.6166 | 1126434.2876 | 2560966.4016 | 1126434.1894
37 | 2560949.9115 | 1126426.6636 | 2560966.4016 | 1126434.1894
38 | 2560965.0468 | 1126392.0258 | 2560956.513 | 1126411.8911 | 2560949.9115 | 1126426.6636
39 | 2560949.9115 | 1126426.6636 | 2560935.037 | 1126459.9101
40 | 2560965.0468 | 1126392.0258 | 2560968.3802 | 1126393.8385 | 2560977.6311 | 1126401.4048
41 | 2560972.0926 | 1126375.6164 | 2560965.0468 | 1126392.0258
42 | 2560935.037 | 1126459.9101 | 2560943.8726 | 1126464.055
43 | 2560931.5437 | 1126467.9034 | 2560935.037 | 1126459.9101
44 | 2560972.0926 | 1126375.6164 | 2560977.9961 | 1126378.0127 | 2560992.5085 | 1126385.2337
45 | 2560983.504 | 1126349.0513 | 2560972.0926 | 1126375.6164
46 | 2560992.7814 | 1126553.7175 | 2560982.9183 | 1126547.9783 | 2560981.6223 | 1126547.3529
47 | 2560972.921 | 1126605.6982 | 2560962.0708 | 1126600.1841 | 2560957.813 | 1126597.2213 | 2560955.3003 | 1126592.4018 | 2560955.9907 | 1126587.1391 | 2560964.8585 | 1126567.7163 | 2560965.1154 | 1126559.7773 | 2560965.886 | 1126551.4347 | 2560968.3407 | 1126547.2945 | 2560970.14 | 1126545.4819 | 2560972.3538 | 1126544.5894 | 2560977.213 | 1126545.2249 | 2560981.6223 | 1126547.3529
48 | 2560972.921 | 1126605.6982 | 2561003.902 | 1126621.4429
49 | 2561058.4338 | 1126545.3447 | 2561047.2784 | 1126567.4168
50 | 2561026.0052 | 1126528.779 | 2561049.3363 | 1126541.1902 | 2561058.4338 | 1126545.3447
51 | 2561047.2784 | 1126567.4168 | 2561031.8731 | 1126559.0898
52 | 2561047.2784 | 1126567.4168 | 2561044.5771 | 1126572.7592 | 2561031.5156 | 1126599.168
53 | 2560916.9707 | 1126500.5933 | 2560906.206 | 1126524.7405
54 | 2560931.5437 | 1126467.9034 | 2560916.9707 | 1126500.5933
55 | 2560896.0833 | 1126547.4476 | 2560906.206 | 1126524.7405
56 | 2560931.5437 | 1126467.9034 | 2560980.8096 | 1126492.3576
57 | 2561031.5156 | 1126599.168 | 2561021.6706 | 1126595.0073 | 2560995.9584 | 1126582.6116
58 | 2561020.9036 | 1126620.6142 | 2561031.5156 | 1126599.168
59 | 2561356.9725 | 1126963.6983 | 2561336.8313 | 1126969.0693 | 2561331.8937 | 1126966.6166
60 | 2561374.3343 | 1126959.0684 | 2561356.9725 | 1126963.6983
61 | 2561374.3343 | 1126959.0684 | 2561377.2646 | 1126961.7844 | 2561416.0503 | 1126981.5415
62 | 2561190.8016 | 1126835.5118 | 2561157.0414 | 1126817.9229
63 | 2561441.3859 | 1126994.1684 | 2561434.9398 | 1126991.1637 | 2561416.0503 | 1126981.5415
64 | 2561441.3859 | 1126994.1684 | 2561371.7454 | 1127098.6558
65 | 2561797.0256 | 1126757.548 | 2561795.6813 | 1126758.7062 | 2561785.2815 | 1126769.4758
66 | 2561798.1475 | 1126756.5813 | 2561797.0256 | 1126757.548
67 | 2561768.1865 | 1126783.2261 | 2561776.4754 | 1126777.882 | 2561783.8757 | 1126770.9316 | 2561785.2815 | 1126769.4758
68 | 2561798.1475 | 1126756.5813 | 2561799.0253 | 1126755.8251
69 | 2561768.1865 | 1126783.2261 | 2561782.8775 | 1126797.6824
70 | 2561799.0253 | 1126755.8251 | 2561812.4359 | 1126744.2706 | 2561822.7046 | 1126733.9114 | 2561825.8023 | 1126732.6579 | 2561827.969 | 1126732.8442 | 2561833.368 | 1126736.0006 | 2561841.0307 | 1126738.8424 | 2561850.6655 | 1126742.7946 | 2561868.3396 | 1126749.5011
71 | 2561799.0253 | 1126755.8251 | 2561720.3484 | 1126577.2799
72 | 2561258.1708 | 1127269.5434 | 2561371.7454 | 1127098.6558
73 | 2561782.8775 | 1126797.6824 | 2561784.6224 | 1126799.3995
74 | 2561475.6924 | 1126439.5912 | 2561720.3484 | 1126577.2799
75 | 2561784.6224 | 1126799.3995 | 2561794.4203 | 1126809.0408
76 | 2561489.275 | 1126410.7255 | 2561485.6901 | 1126418.9714 | 2561482.1226 | 1126426.3313 | 2561475.6924 | 1126439.5912
77 | 2561475.6924 | 1126439.5912 | 2561452.8832 | 1126486.6264 | 2561440.4623 | 1126510.7922
78 | 2561407.7969 | 1126574.3448 | 2561440.4623 | 1126510.7922
79 | 2561489.275 | 1126410.7255 | 2561493.0422 | 1126402.0604 | 2561495.6339 | 1126396.1039
80 | 2561152.3813 | 1126736.1693 | 2561220.5378 | 1126770.5564
81 | 2561152.3813 | 1126736.1693 | 2561120.4909 | 1126798.1061
82 | 2561152.3813 | 1126736.1693 | 2561020.9036 | 1126620.6142
83 | 2561120.4909 | 1126798.1061 | 2561129.0556 | 1126803.3425 | 2561157.0414 | 1126817.9229
84 | 2561020.9036 | 1126620.6142 | 2561015.8606 | 1126623.7372 | 2561012.3519 | 1126624.5825 | 2561008.3156 | 1126623.6859 | 2561003.902 | 1126621.4429
85 | 2561162.054 | 1127419.5205 | 2561146.7244 | 1127460.8402 | 2561140.9572 | 1127479.8721
86 | 2561162.054 | 1127419.5205 | 2561172.3241 | 1127401.0546
87 | 2561162.054 | 1127419.5205 | 2561133.6558 | 1127404.9914
88 | 2561172.3241 | 1127401.0546 | 2561181.3639 | 1127384.8008 | 2561188.7821 | 1127373.6697 | 2561213.6678 | 1127336.3253
89 | 2561213.6678 | 1127336.3253 | 2561249.105 | 1127283.1471 | 2561258.1708 | 1127269.5434
90 | 2561613.5785 | 1126236.5306 | 2561659.5882 | 1126279.1604
91 | 2561589.8764 | 1126215.4707 | 2561613.5785 | 1126236.5306
92 | 2561589.8764 | 1126215.4707 | 2561558.8491 | 1126218.0807
93 | 2561589.8764 | 1126215.4707 | 2561580.3925 | 1126206.3376 | 2561578.1834 | 1126204.3617
94 | 2561589.8764 | 1126215.4707 | 2561584.0919 | 1126225.6905 | 2561572.9763 | 1126245.4443
95 | 2561578.1834 | 1126204.3617 | 2561541.9833 | 1126171.9773
96 | 2561572.9763 | 1126245.4443 | 2561562.7844 | 1126263.5565 | 2561545.8542 | 1126297.1045
97 | 2561541.9833 | 1126171.9773 | 2561528.5873 | 1126159.9932
98 | 2561542.9347 | 1126302.8895 | 2561545.8542 | 1126297.1045
99 | 2561539.1437 | 1126310.4016 | 2561541.2054 | 1126306.3162
100 | 2561539.1437 | 1126310.4016 | 2561533.5781 | 1126321.43
101 | 2561542.9347 | 1126302.8895 | 2561541.2054 | 1126306.3162
102 | 2561525.7735 | 1126336.8214 | 2561528.4295 | 1126331.6322 | 2561533.5781 | 1126321.43
103 | 2561525.0825 | 1126338.1714 | 2561525.7735 | 1126336.8214
104 | 2561525.0825 | 1126338.1714 | 2561519.9595 | 1126348.1804
105 | 2561519.9595 | 1126348.1804 | 2561508.2019 | 1126371.1519
106 | 2561506.7139 | 1126374.059 | 2561508.2019 | 1126371.1519
107 | 2561506.7139 | 1126374.059 | 2561496.7867 | 1126393.4543 | 2561495.6339 | 1126396.1039
108 | 2561508.9854 | 1126142.4574 | 2561528.5873 | 1126159.9932
109 | 2561508.9854 | 1126142.4574 | 2561250.0493 | 1126157.007

## bus_geodata
| x | y | coords
0 | 2561300.7667 | 1126639.0591
1 | 2561308.3406 | 1126627.0737
2 | 2561285.051 | 1126657.6767
3 | 2561321.5046 | 1126612.3421
4 | 2561276.6235 | 1126649.7934
5 | 2561312.3433 | 1126601.7955
6 | 2561229.2678 | 1126605.5417
7 | 2561290.0995 | 1126630.028
8 | 2561339.1276 | 1126708.2222
9 | 2561289.0338 | 1126805.1148
10 | 2561357.0265 | 1126673.3209
11 | 2561372.3891 | 1126643.3652
12 | 2561385.2221 | 1126618.3481
13 | 2561317.661 | 1126593.4127
14 | 2561308.4512 | 1126603.9301
15 | 2561245.5344 | 1126569.6517
16 | 2561256.8982 | 1126868.6089
17 | 2561282.315 | 1126548.7616
18 | 2561309.2349 | 1126568.9543
19 | 2561036.1219 | 1126478.4104
20 | 2561036.9728 | 1126478.4725
21 | 2561022.7138 | 1126471.8561
22 | 2561057.8533 | 1126448.7963
23 | 2561012.0533 | 1126466.3486
24 | 2561066.4807 | 1126434.5143
25 | 2561041.3267 | 1126408.3967
26 | 2561099.3396 | 1126468.753
27 | 2561084.884 | 1126491.3666
28 | 2561077.2913 | 1126507.2733
29 | 2561070.4566 | 1126521.555
30 | 2560966.6166 | 1126434.2876
31 | 2560966.4016 | 1126434.1894
32 | 2560949.9115 | 1126426.6636
33 | 2560965.0468 | 1126392.0258
34 | 2560935.037 | 1126459.9101
35 | 2560977.6311 | 1126401.4048
36 | 2560972.0926 | 1126375.6164
37 | 2561028.9085 | 1126427.0864
38 | 2560983.504 | 1126349.0513
39 | 2560992.5085 | 1126385.2337
40 | 2560981.6223 | 1126547.3529
41 | 2560992.7814 | 1126553.7175
42 | 2560972.921 | 1126605.6982
43 | 2561054.3209 | 1126513.5106
44 | 2561058.4338 | 1126545.3447
45 | 2561047.2784 | 1126567.4168
46 | 2561026.0052 | 1126528.779
47 | 2560916.9707 | 1126500.5933
48 | 2560906.206 | 1126524.7405
49 | 2560931.5437 | 1126467.9034
50 | 2560980.8096 | 1126492.3576
51 | 2560943.8726 | 1126464.055
52 | 2561031.8731 | 1126559.0898
53 | 2561031.5156 | 1126599.168
54 | 2561337.6686 | 1126588.5581
55 | 2561331.8937 | 1126966.6166
56 | 2561356.9725 | 1126963.6983
57 | 2561374.3343 | 1126959.0684
58 | 2561190.8016 | 1126835.5118
59 | 2561416.0503 | 1126981.5415
60 | 2561441.3859 | 1126994.1684
61 | 2561797.0256 | 1126757.548
62 | 2561785.2815 | 1126769.4758
63 | 2561798.1475 | 1126756.5813
64 | 2561768.1865 | 1126783.2261
65 | 2561799.0253 | 1126755.8251
66 | 2561371.7454 | 1127098.6558
67 | 2561782.8775 | 1126797.6824
68 | 2561868.3396 | 1126749.5011
69 | 2561720.3484 | 1126577.2799
70 | 2561784.6224 | 1126799.3995
71 | 2561475.6924 | 1126439.5912
72 | 2561440.4623 | 1126510.7922
73 | 2561407.7969 | 1126574.3448
74 | 2561794.4203 | 1126809.0408
75 | 2561489.275 | 1126410.7255
76 | 2561220.5378 | 1126770.5564
77 | 2561152.3813 | 1126736.1693
78 | 2561120.4909 | 1126798.1061
79 | 2561020.9036 | 1126620.6141
80 | 2561157.0414 | 1126817.9229
81 | 2561003.902 | 1126621.4429
82 | 2560995.9584 | 1126582.6116
83 | 2560896.0833 | 1126547.4476
84 | 2561140.9572 | 1127479.8721
85 | 2561162.054 | 1127419.5205
86 | 2561172.3241 | 1127401.0546
87 | 2561133.6558 | 1127404.9914
88 | 2561213.6678 | 1127336.3253
89 | 2561258.1708 | 1127269.5434
90 | 2561659.5882 | 1126279.1604
91 | 2561613.5785 | 1126236.5306
92 | 2561589.8764 | 1126215.4707
93 | 2561558.8491 | 1126218.0807
94 | 2561578.1834 | 1126204.3617
95 | 2561572.9763 | 1126245.4443
96 | 2561541.9833 | 1126171.9773
97 | 2561545.8542 | 1126297.1045
98 | 2561539.1437 | 1126310.4016
99 | 2561541.2054 | 1126306.3162
100 | 2561533.5781 | 1126321.43
101 | 2561542.9347 | 1126302.8895
102 | 2561525.7735 | 1126336.8214
103 | 2561525.0825 | 1126338.1714
104 | 2561519.9595 | 1126348.1804
105 | 2561508.2019 | 1126371.1519
106 | 2561506.7139 | 1126374.059
107 | 2561495.6339 | 1126396.1039
108 | 2561528.5873 | 1126159.9932
109 | 2561508.9854 | 1126142.4574
110 | 2561250.0493 | 1126157.007
111 | 2561282.315 | 1126548.7616

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1