## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6248-56_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6248-56_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6248-56_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6248-56_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6248-56_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_6248-56_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_6248-56_0_4_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_6248-56_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_6248-56_0_4_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_6248-56_0_4_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_6248-56_0_4_node_36 | 0.4 | n |  | TRUE
11 | bus_LV_6248-56_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_6248-56_0_4_node_50 | 0.4 | n |  | TRUE
13 | bus_LV_6248-56_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_6248-56_0_4_node_49 | 0.4 | n |  | TRUE
15 | bus_LV_6248-56_0_4_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_6248-56_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_6248-56_0_4_node_38 | 0.4 | n |  | TRUE
18 | bus_LV_6248-56_0_4_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_6248-56_0_4_node_37 | 0.4 | n |  | TRUE
20 | bus_LV_6248-56_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_6248-56_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_6248-56_0_4_node_53 | 0.4 | n |  | TRUE
23 | bus_LV_6248-56_0_4_node_51 | 0.4 | n |  | TRUE
24 | bus_LV_6248-56_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_6248-56_0_4_node_42 | 0.4 | n |  | TRUE
26 | bus_LV_6248-56_0_4_node_43 | 0.4 | n |  | TRUE
27 | bus_LV_6248-56_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_6248-56_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_6248-56_0_4_node_40 | 0.4 | n |  | TRUE
30 | bus_LV_6248-56_0_4_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_6248-56_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_6248-56_0_4_node_48 | 0.4 | n |  | TRUE
33 | bus_LV_6248-56_0_4_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_6248-56_0_4_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_6248-56_0_4_node_32 | 0.4 | n |  | TRUE
36 | bus_LV_6248-56_0_4_node_54 | 0.4 | n |  | TRUE
37 | bus_LV_6248-56_0_4_node_52 | 0.4 | n |  | TRUE
38 | bus_LV_6248-56_0_4_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_6248-56_0_4_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_6248-56_0_4_node_39 | 0.4 | n |  | TRUE
41 | bus_LV_6248-56_0_4_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_6248-56_0_4_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_6248-56_0_4_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_6248-56_0_4_node_47 | 0.4 | n |  | TRUE
45 | bus_LV_6248-56_0_4_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_6248-56_0_4_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_6248-56_0_4_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_6248-56_0_4_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_6248-56_0_4_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_6248-56_0_4_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_6248-56_0_4_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_6248-56_0_4_node_57 | 0.4 | n |  | TRUE
53 | bus_LV_6248-56_0_4_node_56 | 0.4 | n |  | TRUE
54 | bus_LV_6248-56_0_4_node_55 | 0.4 | n |  | TRUE
55 | bus_MV_273_0_node_55 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6248-56_0_4_load_0 | 0 | 0.0359 | 0.0089974 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6248-56_0_4_load_1 | 1 | 0.0067027 | 0.0016799 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6248-56_0_4_load_3 | 3 | 0.022901 | 0.0057394 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6248-56_0_4_load_24 | 8 | 0.0063538 | 0.0015924 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6248-56_0_4_load_21 | 9 | 0.0063494 | 0.0015913 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6248-56_0_4_load_36 | 10 | 0.014866 | 0.0037257 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6248-56_0_4_load_50 | 12 | 0.0041188 | 0.0010323 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6248-56_0_4_load_49 | 14 | 0.0046993 | 0.0011778 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6248-56_0_4_load_19 | 15 | 0.0098115 | 0.002459 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6248-56_0_4_load_37 | 19 | 0.014356 | 0.0035979 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6248-56_0_4_load_53 | 22 | 0.006594 | 0.0016526 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6248-56_0_4_load_51 | 23 | 0.0030541 | 0.00076543 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6248-56_0_4_load_43 | 26 | 0.012651 | 0.0031707 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6248-56_0_4_load_40 | 29 | 0.010777 | 0.0027011 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6248-56_0_4_load_35 | 30 | 0.016458 | 0.0041248 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6248-56_0_4_load_20 | 31 | 0.010589 | 0.0026539 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6248-56_0_4_load_48 | 32 | 0.0089946 | 0.0022543 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6248-56_0_4_load_30 | 33 | 0.013004 | 0.0032592 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6248-56_0_4_load_41 | 34 | 0.011952 | 0.0029956 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6248-56_0_4_load_32 | 35 | 0.022671 | 0.0056818 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6248-56_0_4_load_54 | 36 | 0.004036 | 0.0010115 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6248-56_0_4_load_52 | 37 | 0.0024734 | 0.0006199 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6248-56_0_4_load_27 | 38 | 0.0035756 | 0.00089614 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6248-56_0_4_load_26 | 39 | 0.008442 | 0.0021158 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6248-56_0_4_load_39 | 40 | 0.067833 | 0.017001 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6248-56_0_4_load_22 | 41 | 0.011828 | 0.0029644 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6248-56_0_4_load_23 | 42 | 0.020596 | 0.0051618 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6248-56_0_4_load_47 | 44 | 0.050925 | 0.012763 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6248-56_0_4_load_45 | 45 | 0.0061127 | 0.001532 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6248-56_0_4_load_28 | 46 | 0.0054445 | 0.0013645 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6248-56_0_4_load_29 | 47 | 0.0035216 | 0.00088258 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6248-56_0_4_load_46 | 49 | 0.0052834 | 0.0013241 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6248-56_0_4_load_33 | 50 | 0.010479 | 0.0026263 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6248-56_0_4_load_34 | 51 | 0.0095037 | 0.0023819 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6248-56_0_4_load_57 | 52 | 0.0049286 | 0.0012352 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6248-56_0_4_load_56 | 53 | 0.0032939 | 0.00082553 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6248-56_0_4_load_55 | 54 | 0.0045228 | 0.0011335 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6248-56_0_4_line_0 |  | 0 | 1 | 0.022456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_6248-56_0_4_line_1 |  | 0 | 2 | 0.016921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6248-56_0_4_line_2 |  | 1 | 3 | 0.020313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_6248-56_0_4_line_3 |  | 2 | 4 | 0.035201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6248-56_0_4_line_4 |  | 3 | 5 | 0.031986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_6248-56_0_4_line_5 |  | 4 | 10 | 0.010427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6248-56_0_4_line_6 |  | 5 | 6 | 0.033905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_6248-56_0_4_line_7 |  | 6 | 15 | 0.0084481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_6248-56_0_4_line_8 |  | 7 | 8 | 0.022167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6248-56_0_4_line_9 |  | 7 | 9 | 0.016884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6248-56_0_4_line_10 |  | 8 | 25 | 0.035141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6248-56_0_4_line_11 |  | 9 | 31 | 0.016806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_6248-56_0_4_line_12 |  | 10 | 19 | 0.035428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6248-56_0_4_line_13 |  | 11 | 12 | 0.011094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6248-56_0_4_line_14 |  | 11 | 13 | 0.033422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_6248-56_0_4_line_15 |  | 11 | 14 | 0.01184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_6248-56_0_4_line_16 |  | 12 | 20 | 0.010646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6248-56_0_4_line_17 |  | 13 | 15 | 0.0088805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_6248-56_0_4_line_18 |  | 14 | 32 | 0.015069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_6248-56_0_4_line_19 |  | 16 | 17 | 0.025466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6248-56_0_4_line_20 |  | 16 | 18 | 0.002959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6248-56_0_4_line_21 |  | 16 | 19 | 0.01257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6248-56_0_4_line_22 |  | 17 | 34 | 0.02926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6248-56_0_4_line_23 |  | 18 | 35 | 0.030279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6248-56_0_4_line_24 |  | 18 | 33 | 0.0090542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6248-56_0_4_line_25 |  | 20 | 21 | 0.020312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6248-56_0_4_line_26 |  | 20 | 22 | 0.013068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6248-56_0_4_line_27 |  | 21 | 23 | 0.0090621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6248-56_0_4_line_28 |  | 22 | 36 | 0.0084242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6248-56_0_4_line_29 |  | 23 | 37 | 0.0099067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6248-56_0_4_line_30 |  | 24 | 25 | 0.025264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6248-56_0_4_line_31 |  | 24 | 26 | 0.015249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6248-56_0_4_line_32 |  | 25 | 27 | 0.004136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6248-56_0_4_line_33 |  | 27 | 28 | 0.014465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6248-56_0_4_line_34 |  | 27 | 29 | 0.029626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6248-56_0_4_line_35 |  | 28 | 30 | 0.022637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6248-56_0_4_line_36 |  | 29 | 40 | 0.029339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6248-56_0_4_line_37 |  | 31 | 41 | 0.02125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_6248-56_0_4_line_38 |  | 32 | 44 | 0.0056768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_6248-56_0_4_line_39 |  | 35 | 50 | 0.031374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6248-56_0_4_line_40 |  | 36 | 54 | 0.00066112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6248-56_0_4_line_41 |  | 38 | 39 | 0.0022118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6248-56_0_4_line_42 |  | 39 | 46 | 0.0049132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6248-56_0_4_line_43 |  | 41 | 42 | 0.0026742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_6248-56_0_4_line_44 |  | 42 | 43 | 0.024263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_6248-56_0_4_line_45 |  | 43 | 44 | 0.0057742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_6248-56_0_4_line_46 |  | 43 | 45 | 0.0075287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6248-56_0_4_line_47 |  | 46 | 47 | 0.0010559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6248-56_0_4_line_48 |  | 47 | 48 | 0.011506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6248-56_0_4_line_49 |  | 48 | 49 | 0.010235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6248-56_0_4_line_50 |  | 49 | 52 | 0.0033263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6248-56_0_4_line_51 |  | 50 | 51 | 0.00074524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6248-56_0_4_line_52 |  | 52 | 53 | 0.0055122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6248-56_0_4_line_53 |  | 53 | 54 | 0.0026146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6248-56_0_4_trafo_21 | 0.63 MVA 20/0.4 kV | 55 | 9 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2606715.317 | 1126767.0576 | 2606714.0334 | 1126765.279 | 2606702.0686 | 1126748.9264
1 | 2606726.1706 | 1126772.0289 | 2606721.1113 | 1126775.8697 | 2606719.5733 | 1126772.9555 | 2606715.317 | 1126767.0576
2 | 2606702.0686 | 1126748.9264 | 2606696.3284 | 1126741.0811 | 2606689.8754 | 1126732.6823
3 | 2606726.1706 | 1126772.0289 | 2606730.8572 | 1126777.8703 | 2606736.1302 | 1126782.923 | 2606723.8018 | 1126788.8456 | 2606726.2454 | 1126795.1181
4 | 2606670.7969 | 1126707.0143 | 2606679.8301 | 1126719.6081 | 2606689.8754 | 1126732.6823
5 | 2606726.2454 | 1126795.1181 | 2606730.025 | 1126804.8364
6 | 2606648.3805 | 1126692.2938 | 2606649.4923 | 1126697.4086 | 2606650.7882 | 1126703.3907 | 2606653.9715 | 1126702.7383 | 2606657.7562 | 1126701.8198 | 2606660.5308 | 1126701.4671 | 2606663.5284 | 1126701.4703 | 2606665.7398 | 1126701.7618 | 2606667.3031 | 1126702.6862 | 2606668.65 | 1126704.2328 | 2606670.7969 | 1126707.0143
7 | 2606648.3805 | 1126692.2938 | 2606640.106 | 1126693.9974
8 | 2606668.8814 | 1126816.8991 | 2606649.0304 | 1126826.7635
9 | 2606668.8814 | 1126816.8991 | 2606660.9443 | 1126801.9969
10 | 2606618.9323 | 1126844.5472 | 2606621.4317 | 1126842.0376 | 2606625.2336 | 1126839.4404 | 2606629.9144 | 1126836.344 | 2606636.7379 | 1126832.8719 | 2606649.0304 | 1126826.7635
11 | 2606653.044 | 1126787.1639 | 2606660.9443 | 1126801.9969
12 | 2606730.025 | 1126804.8364 | 2606734.844 | 1126817.2272 | 2606737.3054 | 1126839.2233
13 | 2606611.7329 | 1126711.2077 | 2606607.7249 | 1126711.9593 | 2606600.7911 | 1126713.0278
14 | 2606611.7329 | 1126711.2077 | 2606610.606 | 1126705.7705 | 2606625.9986 | 1126702.4856 | 2606624.8871 | 1126697.1262 | 2606627.5694 | 1126696.5844 | 2606631.4079 | 1126695.7882
15 | 2606611.7329 | 1126711.2077 | 2606611.9016 | 1126711.9972 | 2606613.7846 | 1126716.557 | 2606616.8899 | 1126721.8068
16 | 2606590.2296 | 1126714.3193 | 2606595.3315 | 1126713.8691 | 2606600.7911 | 1126713.0278
17 | 2606631.4079 | 1126695.7882 | 2606640.106 | 1126693.9974
18 | 2606624.5618 | 1126734.7772 | 2606616.8899 | 1126721.8068
19 | 2606738.7051 | 1126851.7149 | 2606720.9715 | 1126853.8075 | 2606713.2961 | 1126854.1659
20 | 2606738.7051 | 1126851.7149 | 2606739.0718 | 1126854.6501
21 | 2606738.7051 | 1126851.7149 | 2606738.3312 | 1126848.3907 | 2606737.3054 | 1126839.2233
22 | 2606713.2961 | 1126854.1659 | 2606713.0076 | 1126850.1859 | 2606712.6647 | 1126846.6727 | 2606711.2758 | 1126841.3575 | 2606709.7169 | 1126836.3978 | 2606705.3897 | 1126826.2325
23 | 2606739.0718 | 1126854.6501 | 2606725.4767 | 1126856.3248 | 2606715.7589 | 1126856.9367 | 2606708.9178 | 1126857.1404
24 | 2606739.0718 | 1126854.6501 | 2606740.6132 | 1126854.4628 | 2606748.0582 | 1126853.5444
25 | 2606581.7493 | 1126703.3604 | 2606581.0346 | 1126708.64 | 2606590.282 | 1126708.5833 | 2606590.2296 | 1126714.3193
26 | 2606590.2296 | 1126714.3193 | 2606590.8733 | 1126717.6439 | 2606592.4874 | 1126721.5142 | 2606592.4232 | 1126723.893 | 2606591.5034 | 1126726.4488 | 2606591.4698 | 1126726.8401
27 | 2606581.7493 | 1126703.3604 | 2606576.9484 | 1126703.3552 | 2606572.7161 | 1126702.8603
28 | 2606591.4698 | 1126726.8401 | 2606591.2849 | 1126728.9943 | 2606592.0156 | 1126730.2735 | 2606595.0786 | 1126733.9547
29 | 2606572.7161 | 1126702.8603 | 2606569.9444 | 1126702.5362 | 2606563.0254 | 1126701.5616 | 2606562.8981 | 1126701.5414
30 | 2606618.9323 | 1126844.5472 | 2606614.9451 | 1126840.3853 | 2606612.3061 | 1126836.5806 | 2606603.9817 | 1126824.2322
31 | 2606603.9817 | 1126824.2322 | 2606595.4262 | 1126811.609
32 | 2606618.9323 | 1126844.5472 | 2606616.8324 | 1126848.1133
33 | 2606616.8324 | 1126848.1133 | 2606611.4912 | 1126856.2115 | 2606615.3411 | 1126859.017
34 | 2606616.8324 | 1126848.1133 | 2606625.4983 | 1126851.0908 | 2606634.8275 | 1126853.5911 | 2606645.603 | 1126854.3792
35 | 2606615.3411 | 1126859.017 | 2606616.028 | 1126857.9839 | 2606617.8407 | 1126856.3295 | 2606621.9266 | 1126854.6887 | 2606624.7398 | 1126854.2249 | 2606626.0496 | 1126854.3486 | 2606631.8202 | 1126855.422 | 2606636.3 | 1126855.8774
36 | 2606674.9144 | 1126855.2036 | 2606655.809 | 1126855.1257 | 2606645.603 | 1126854.3792
37 | 2606653.044 | 1126787.1639 | 2606643.0545 | 1126768.4082
38 | 2606627.4519 | 1126739.6632 | 2606624.5618 | 1126734.7772
39 | 2606708.9178 | 1126857.1404 | 2606701.7183 | 1126857.3548 | 2606686.3216 | 1126857.6047 | 2606677.55 | 1126857.7554
40 | 2606595.5015 | 1126734.4629 | 2606595.0786 | 1126733.9547
41 | 2606592.6707 | 1126765.3334 | 2606594.3329 | 1126763.8743
42 | 2606598.0253 | 1126760.6332 | 2606594.3329 | 1126763.8743
43 | 2606641.7974 | 1126766.048 | 2606643.0545 | 1126768.4082
44 | 2606630.3916 | 1126744.6331 | 2606641.7974 | 1126766.048
45 | 2606630.3916 | 1126744.6331 | 2606627.4519 | 1126739.6632
46 | 2606630.3916 | 1126744.6331 | 2606623.9887 | 1126748.5936
47 | 2606598.8189 | 1126759.9366 | 2606598.0253 | 1126760.6332
48 | 2606606.9339 | 1126752.2003 | 2606606.2537 | 1126754.1227 | 2606604.9731 | 1126755.3886 | 2606600.8011 | 1126758.1966 | 2606598.8189 | 1126759.9366
49 | 2606606.9339 | 1126752.2003 | 2606607.0666 | 1126750.6663 | 2606606.6066 | 1126748.4425 | 2606605.1066 | 1126746.0064 | 2606602.827 | 1126743.2669
50 | 2606602.827 | 1126743.2669 | 2606600.6995 | 1126740.7099
51 | 2606676.8049 | 1126857.7682 | 2606677.55 | 1126857.7554
52 | 2606597.1738 | 1126736.4727 | 2606600.6995 | 1126740.7099
53 | 2606597.1738 | 1126736.4727 | 2606595.5015 | 1126734.4629

## bus_geodata
| x | y | coords
0 | 2606715.317 | 1126767.0576
1 | 2606702.0686 | 1126748.9264
2 | 2606726.1706 | 1126772.0289
3 | 2606689.8754 | 1126732.6823
4 | 2606726.2454 | 1126795.1181
5 | 2606670.7969 | 1126707.0143
6 | 2606648.3805 | 1126692.2938
7 | 2606668.8814 | 1126816.8991
8 | 2606649.0304 | 1126826.7635
9 | 2606660.9443 | 1126801.9969
10 | 2606730.025 | 1126804.8364
11 | 2606611.7329 | 1126711.2077
12 | 2606600.7911 | 1126713.0278
13 | 2606631.4079 | 1126695.7882
14 | 2606616.8899 | 1126721.8068
15 | 2606640.106 | 1126693.9974
16 | 2606738.7051 | 1126851.7149
17 | 2606713.2961 | 1126854.1659
18 | 2606739.0718 | 1126854.6501
19 | 2606737.3054 | 1126839.2233
20 | 2606590.2296 | 1126714.3193
21 | 2606581.7493 | 1126703.3604
22 | 2606591.4698 | 1126726.8401
23 | 2606572.7161 | 1126702.8603
24 | 2606603.9817 | 1126824.2322
25 | 2606618.9323 | 1126844.5472
26 | 2606595.4262 | 1126811.609
27 | 2606616.8324 | 1126848.1133
28 | 2606615.3411 | 1126859.017
29 | 2606645.603 | 1126854.3792
30 | 2606636.3 | 1126855.8774
31 | 2606653.044 | 1126787.1639
32 | 2606624.5618 | 1126734.7772
33 | 2606748.0582 | 1126853.5444
34 | 2606705.3897 | 1126826.2325
35 | 2606708.9178 | 1126857.1404
36 | 2606595.0786 | 1126733.9547
37 | 2606562.8981 | 1126701.5414
38 | 2606592.6707 | 1126765.3334
39 | 2606594.3329 | 1126763.8743
40 | 2606674.9144 | 1126855.2036
41 | 2606643.0545 | 1126768.4082
42 | 2606641.7974 | 1126766.048
43 | 2606630.3916 | 1126744.6331
44 | 2606627.4519 | 1126739.6632
45 | 2606623.9887 | 1126748.5936
46 | 2606598.0253 | 1126760.6332
47 | 2606598.8189 | 1126759.9366
48 | 2606606.9339 | 1126752.2003
49 | 2606602.827 | 1126743.2668
50 | 2606677.55 | 1126857.7554
51 | 2606676.8049 | 1126857.7682
52 | 2606600.6995 | 1126740.7099
53 | 2606597.1738 | 1126736.4727
54 | 2606595.5015 | 1126734.4629
55 | 2606668.8814 | 1126816.8991

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1