## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6248-64_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6248-64_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6248-64_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6248-64_0_5_node_42 | 0.4 | n |  | TRUE
4 | bus_LV_6248-64_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_6248-64_0_5_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_6248-64_0_5_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_6248-64_0_5_node_43 | 0.4 | n |  | TRUE
8 | bus_LV_6248-64_0_5_node_41 | 0.4 | n |  | TRUE
9 | bus_LV_6248-64_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_6248-64_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_6248-64_0_5_node_37 | 0.4 | n |  | TRUE
12 | bus_LV_6248-64_0_5_node_38 | 0.4 | n |  | TRUE
13 | bus_LV_6248-64_0_5_node_39 | 0.4 | n |  | TRUE
14 | bus_LV_6248-64_0_5_node_36 | 0.4 | n |  | TRUE
15 | bus_LV_6248-64_0_5_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_6248-64_0_5_node_57 | 0.4 | n |  | TRUE
17 | bus_LV_6248-64_0_5_node_33 | 0.4 | n |  | TRUE
18 | bus_LV_6248-64_0_5_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_6248-64_0_5_node_35 | 0.4 | n |  | TRUE
20 | bus_LV_6248-64_0_5_node_40 | 0.4 | n |  | TRUE
21 | bus_LV_6248-64_0_5_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_6248-64_0_5_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_6248-64_0_5_node_56 | 0.4 | n |  | TRUE
24 | bus_LV_6248-64_0_5_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_6248-64_0_5_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_6248-64_0_5_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_6248-64_0_5_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_6248-64_0_5_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_6248-64_0_5_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_6248-64_0_5_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_6248-64_0_5_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_6248-64_0_5_node_12 | 0.4 | n |  | TRUE
33 | bus_LV_6248-64_0_5_node_13 | 0.4 | n |  | TRUE
34 | bus_LV_6248-64_0_5_node_14 | 0.4 | n |  | TRUE
35 | bus_LV_6248-64_0_5_node_15 | 0.4 | n |  | TRUE
36 | bus_LV_6248-64_0_5_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_6248-64_0_5_node_16 | 0.4 | n |  | TRUE
38 | bus_LV_6248-64_0_5_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_6248-64_0_5_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_6248-64_0_5_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_6248-64_0_5_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_6248-64_0_5_node_45 | 0.4 | n |  | TRUE
43 | bus_LV_6248-64_0_5_node_46 | 0.4 | n |  | TRUE
44 | bus_LV_6248-64_0_5_node_47 | 0.4 | n |  | TRUE
45 | bus_LV_6248-64_0_5_node_48 | 0.4 | n |  | TRUE
46 | bus_LV_6248-64_0_5_node_50 | 0.4 | n |  | TRUE
47 | bus_LV_6248-64_0_5_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_6248-64_0_5_node_55 | 0.4 | n |  | TRUE
49 | bus_LV_6248-64_0_5_node_54 | 0.4 | n |  | TRUE
50 | bus_LV_6248-64_0_5_node_49 | 0.4 | n |  | TRUE
51 | bus_LV_6248-64_0_5_node_51 | 0.4 | n |  | TRUE
52 | bus_LV_6248-64_0_5_node_52 | 0.4 | n |  | TRUE
53 | bus_LV_6248-64_0_5_node_53 | 0.4 | n |  | TRUE
54 | bus_MV_272_1_node_57 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6248-64_0_5_load_0 | 0 | 0.057 | 0.014285 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6248-64_0_5_load_1 | 1 | 0.0094593 | 0.0023707 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6248-64_0_5_load_42 | 3 | 0.0025033 | 0.0006274 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6248-64_0_5_load_3 | 4 | 0.0051983 | 0.0013028 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6248-64_0_5_load_4 | 5 | 0.12963 | 0.032487 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6248-64_0_5_load_5 | 6 | 0.0049911 | 0.0012509 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6248-64_0_5_load_43 | 7 | 0.0051711 | 0.001296 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6248-64_0_5_load_41 | 8 | 0.0020877 | 0.00052322 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6248-64_0_5_load_7 | 9 | 0.0071886 | 0.0018016 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6248-64_0_5_load_8 | 10 | 0.0054081 | 0.0013554 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6248-64_0_5_load_38 | 12 | 0.0069649 | 0.0017456 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6248-64_0_5_load_39 | 13 | 0.0022502 | 0.00056396 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6248-64_0_5_load_36 | 14 | 0.0085224 | 0.0021359 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6248-64_0_5_load_57 | 16 | 0.0057018 | 0.001429 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6248-64_0_5_load_34 | 18 | 0.0055921 | 0.0014015 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6248-64_0_5_load_35 | 19 | 0.0054817 | 0.0013738 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6248-64_0_5_load_40 | 20 | 0.0056528 | 0.0014167 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6248-64_0_5_load_11 | 22 | 0.035108 | 0.0087988 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6248-64_0_5_load_56 | 23 | 0.0053401 | 0.0013384 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6248-64_0_5_load_18 | 25 | 0.014235 | 0.0035677 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6248-64_0_5_load_21 | 27 | 0.0035001 | 0.00087722 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6248-64_0_5_load_17 | 28 | 0.0059338 | 0.0014872 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6248-64_0_5_load_24 | 30 | 0.012884 | 0.0032289 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6248-64_0_5_load_22 | 31 | 0.011671 | 0.0029249 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6248-64_0_5_load_12 | 32 | 0.029582 | 0.0074139 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6248-64_0_5_load_13 | 33 | 0.0071087 | 0.0017816 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6248-64_0_5_load_14 | 34 | 0.046421 | 0.011634 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6248-64_0_5_load_15 | 35 | 0.008694 | 0.0021789 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6248-64_0_5_load_27 | 36 | 0.0087739 | 0.0021989 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6248-64_0_5_load_16 | 37 | 0.0060507 | 0.0015165 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6248-64_0_5_load_32 | 39 | 0.0057339 | 0.001437 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6248-64_0_5_load_30 | 40 | 0.0026141 | 0.00065517 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6248-64_0_5_load_29 | 41 | 0.0074291 | 0.0018619 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6248-64_0_5_load_45 | 42 | 0.0067486 | 0.0016914 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6248-64_0_5_load_46 | 43 | 0.0061989 | 0.0015536 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6248-64_0_5_load_47 | 44 | 0.010531 | 0.0026394 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6248-64_0_5_load_48 | 45 | 0.026671 | 0.0066844 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6248-64_0_5_load_50 | 46 | 0.010322 | 0.002587 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6248-64_0_5_load_44 | 47 | 0.0067442 | 0.0016903 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6248-64_0_5_load_55 | 48 | 0.0051763 | 0.0012973 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6248-64_0_5_load_54 | 49 | 0.0050739 | 0.0012716 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6248-64_0_5_load_49 | 50 | 0.013724 | 0.0034396 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6248-64_0_5_load_51 | 51 | 0.0075732 | 0.001898 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6248-64_0_5_load_52 | 52 | 0.0075456 | 0.0018911 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6248-64_0_5_load_53 | 53 | 0.0077866 | 0.0019515 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6248-64_0_5_line_0 |  | 0 | 1 | 0.01766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6248-64_0_5_line_1 |  | 0 | 2 | 0.058467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6248-64_0_5_line_2 |  | 0 | 3 | 0.062642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6248-64_0_5_line_3 |  | 1 | 4 | 0.052028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6248-64_0_5_line_4 |  | 2 | 5 | 0.027727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_6248-64_0_5_line_5 |  | 2 | 6 | 0.03564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_6248-64_0_5_line_6 |  | 3 | 7 | 0.034192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6248-64_0_5_line_7 |  | 3 | 8 | 0.018774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6248-64_0_5_line_8 |  | 5 | 9 | 0.048815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_6248-64_0_5_line_9 |  | 6 | 10 | 0.0033973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6248-64_0_5_line_10 |  | 7 | 47 | 0.006446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6248-64_0_5_line_11 |  | 8 | 13 | 0.026636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6248-64_0_5_line_12 |  | 9 | 15 | 0.012297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_6248-64_0_5_line_13 |  | 10 | 16 | 0.0051835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6248-64_0_5_line_14 |  | 11 | 12 | 0.017044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6248-64_0_5_line_15 |  | 11 | 13 | 0.010228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6248-64_0_5_line_16 |  | 11 | 14 | 0.013519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6248-64_0_5_line_17 |  | 14 | 19 | 0.0056967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6248-64_0_5_line_18 |  | 15 | 21 | 0.034121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_6248-64_0_5_line_19 |  | 15 | 22 | 0.060667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6248-64_0_5_line_20 |  | 16 | 23 | 0.016241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6248-64_0_5_line_21 |  | 17 | 18 | 0.021841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6248-64_0_5_line_22 |  | 17 | 19 | 0.037482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6248-64_0_5_line_23 |  | 18 | 20 | 0.027245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6248-64_0_5_line_24 |  | 20 | 42 | 0.0056161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6248-64_0_5_line_25 |  | 21 | 24 | 0.025153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6248-64_0_5_line_26 |  | 21 | 25 | 0.029984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6248-64_0_5_line_27 |  | 23 | 48 | 0.0074364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6248-64_0_5_line_28 |  | 24 | 26 | 0.040981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6248-64_0_5_line_29 |  | 24 | 27 | 0.04613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6248-64_0_5_line_30 |  | 25 | 28 | 0.040389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6248-64_0_5_line_31 |  | 26 | 38 | 0.10434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6248-64_0_5_line_32 |  | 26 | 31 | 0.016269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6248-64_0_5_line_33 |  | 27 | 39 | 0.011942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6248-64_0_5_line_34 |  | 28 | 37 | 0.011892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6248-64_0_5_line_35 |  | 29 | 30 | 0.026991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6248-64_0_5_line_36 |  | 29 | 31 | 0.044501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6248-64_0_5_line_37 |  | 32 | 33 | 0.015594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6248-64_0_5_line_38 |  | 32 | 34 | 0.0088812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6248-64_0_5_line_39 |  | 33 | 35 | 0.0081687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6248-64_0_5_line_40 |  | 34 | 36 | 0.15535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6248-64_0_5_line_41 |  | 35 | 37 | 0.015263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6248-64_0_5_line_42 |  | 38 | 40 | 0.10246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6248-64_0_5_line_43 |  | 40 | 41 | 0.052384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6248-64_0_5_line_44 |  | 42 | 43 | 0.015356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6248-64_0_5_line_45 |  | 44 | 45 | 0.023549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6248-64_0_5_line_46 |  | 44 | 46 | 0.052141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6248-64_0_5_line_47 |  | 45 | 50 | 0.024279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6248-64_0_5_line_48 |  | 46 | 51 | 0.023417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6248-64_0_5_line_49 |  | 48 | 49 | 0.0065794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6248-64_0_5_line_50 |  | 49 | 53 | 0.015523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6248-64_0_5_line_51 |  | 51 | 52 | 0.0084229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6248-64_0_5_line_52 |  | 52 | 53 | 0.0068147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6248-64_0_5_trafo_5 | 0.63 MVA 20/0.4 kV | 54 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2607915.1962 | 1126883.4009 | 2607932.3271 | 1126887.6908
1 | 2607860.389 | 1126884.3945 | 2607869.3824 | 1126877.914 | 2607880.8371 | 1126875.0163 | 2607897.9027 | 1126877.2728 | 2607914.0698 | 1126883.1188 | 2607915.1962 | 1126883.4009
2 | 2607915.1962 | 1126883.4009 | 2607937.3558 | 1126824.8095
3 | 2607932.3271 | 1126887.6908 | 2607934.7302 | 1126888.2926 | 2607948.6538 | 1126888.9889 | 2607979.8484 | 1126871.8146
4 | 2607860.389 | 1126884.3945 | 2607852.0583 | 1126896.9232 | 2607843.0617 | 1126905.8604
5 | 2607860.389 | 1126884.3945 | 2607859.2744 | 1126876.3335 | 2607851.6655 | 1126854.8244 | 2607850.3892 | 1126850.3143
6 | 2607937.3558 | 1126824.8095 | 2607937.3558 | 1126824.8095 | 2607930.6246 | 1126821.8993 | 2607911.8071 | 1126802.7347
7 | 2607950.9235 | 1126812.2155 | 2607943.425 | 1126821.2379 | 2607937.3558 | 1126824.8095
8 | 2607843.0617 | 1126905.8604 | 2607843.0617 | 1126905.8604 | 2607830.2595 | 1126908.0895 | 2607810.0483 | 1126901.1157 | 2607797.2816 | 1126894.3699
9 | 2607850.3892 | 1126850.3143 | 2607849.4641 | 1126847.0453
10 | 2607907.2909 | 1126798.1352 | 2607911.8071 | 1126802.7347
11 | 2607967.9486 | 1126791.7305 | 2607950.9235 | 1126812.2155
12 | 2607788.1589 | 1126886.7919 | 2607790.5194 | 1126890.7969 | 2607797.2816 | 1126894.3699
13 | 2607849.4641 | 1126847.0453 | 2607848.0526 | 1126842.0577
14 | 2607974.5596 | 1126783.927 | 2607961.3342 | 1126773.1766
15 | 2607974.5596 | 1126783.927 | 2607969.0722 | 1126790.3785 | 2607967.9486 | 1126791.7305
16 | 2607974.5596 | 1126783.927 | 2607983.3162 | 1126773.6268
17 | 2607987.006 | 1126769.2866 | 2607983.3162 | 1126773.6268
18 | 2607788.1589 | 1126886.7919 | 2607784.0334 | 1126889.0322 | 2607756.6608 | 1126878.003
19 | 2607788.1589 | 1126886.7919 | 2607772.1421 | 1126859.6471 | 2607758.2467 | 1126836.796 | 2607756.6938 | 1126834.9594
20 | 2607843.6302 | 1126826.4304 | 2607848.0526 | 1126842.0577
21 | 2608012.4899 | 1126741.8451 | 2608005.6788 | 1126735.1773 | 2607996.8795 | 1126726.5694
22 | 2608012.4899 | 1126741.8451 | 2607998.5469 | 1126755.7113 | 2607987.006 | 1126769.2866
23 | 2607977.4038 | 1126707.5172 | 2607996.8795 | 1126726.5694
24 | 2607973.3892 | 1126703.59 | 2607977.4038 | 1126707.5172
25 | 2607756.6608 | 1126878.003 | 2607750.3854 | 1126874.1154 | 2607743.9803 | 1126869.2604 | 2607737.5706 | 1126861.882
26 | 2607756.6608 | 1126878.003 | 2607755.3375 | 1126882.359 | 2607752.5801 | 1126893.4609 | 2607750.7971 | 1126907.3388
27 | 2607841.6053 | 1126819.275 | 2607843.6302 | 1126826.4304
28 | 2607737.5706 | 1126861.882 | 2607696.9608 | 1126855.5609
29 | 2607737.5706 | 1126861.882 | 2607731.7165 | 1126872.1685 | 2607728.1057 | 1126887.8382 | 2607717.9784 | 1126901.4765 | 2607717.1402 | 1126902.3723
30 | 2607750.7971 | 1126907.3388 | 2607747.4979 | 1126933.0182 | 2607752.2683 | 1126946.7093
31 | 2607619.6795 | 1126885.4785 | 2607620.8171 | 1126881.6114 | 2607628.7032 | 1126879.1422 | 2607638.9411 | 1126863.3029 | 2607644.6432 | 1126845.0567 | 2607650.4004 | 1126844.3858 | 2607665.4491 | 1126845.0828 | 2607696.9608 | 1126855.5609
32 | 2607696.9608 | 1126855.5609 | 2607698.8772 | 1126839.4055
33 | 2607708.9812 | 1126911.0921 | 2607717.1402 | 1126902.3723
34 | 2607759.012 | 1126955.9663 | 2607754.0778 | 1126951.9024 | 2607752.2683 | 1126946.7093
35 | 2607704.843 | 1126795.3081 | 2607690.6648 | 1126772.341
36 | 2607704.843 | 1126795.3081 | 2607700.3334 | 1126827.1291 | 2607698.8772 | 1126839.4055
37 | 2607781.4535 | 1126949.2256 | 2607796.3887 | 1126944.7396
38 | 2607804.8944 | 1126942.1847 | 2607796.3887 | 1126944.7396
39 | 2607781.4535 | 1126949.2256 | 2607773.63 | 1126951.5755
40 | 2607804.8944 | 1126942.1847 | 2607905.3168 | 1127060.7191
41 | 2607773.63 | 1126951.5755 | 2607759.012 | 1126955.9663 | 2607759.012 | 1126955.9663
42 | 2607619.6795 | 1126885.4785 | 2607623.2224 | 1126886.9058 | 2607629.2522 | 1126890.026 | 2607647.8984 | 1126903.8561 | 2607673.0278 | 1126927.8438 | 2607688.0561 | 1126944.6598 | 2607695.8769 | 1126952.8704
43 | 2607728.3436 | 1126993.8746 | 2607723.7105 | 1126987.459 | 2607705.7713 | 1126963.2579 | 2607695.8769 | 1126952.8704
44 | 2607973.3892 | 1126703.59 | 2607962.4121 | 1126692.8517
45 | 2607851.9661 | 1126715.2349 | 2607855.7143 | 1126720.8309 | 2607867.6048 | 1126732.7187 | 2607867.6048 | 1126732.7187
46 | 2607823.9288 | 1126761.1986 | 2607867.6048 | 1126732.7187
47 | 2607838.4549 | 1126695.0628 | 2607851.9661 | 1126715.2349
48 | 2607823.9288 | 1126761.1986 | 2607827.2871 | 1126774.4205 | 2607829.919 | 1126783.8348
49 | 2607839.8138 | 1126812.9443 | 2607841.6053 | 1126819.275
50 | 2607834.5506 | 1126798.3407 | 2607839.8138 | 1126812.9443 | 2607839.8138 | 1126812.9443
51 | 2607829.919 | 1126783.8348 | 2607831.9816 | 1126791.2125 | 2607832.2401 | 1126791.9297
52 | 2607832.2401 | 1126791.9297 | 2607834.5506 | 1126798.3407

## bus_geodata
| x | y | coords
0 | 2607915.1962 | 1126883.4009
1 | 2607932.3271 | 1126887.6908
2 | 2607860.389 | 1126884.3945
3 | 2607937.3558 | 1126824.8095
4 | 2607979.8484 | 1126871.8146
5 | 2607843.0617 | 1126905.8604
6 | 2607850.3892 | 1126850.3143
7 | 2607911.8071 | 1126802.7347
8 | 2607950.9235 | 1126812.2155
9 | 2607797.2816 | 1126894.3699
10 | 2607849.4641 | 1126847.0453
11 | 2607974.5596 | 1126783.927
12 | 2607961.3342 | 1126773.1766
13 | 2607967.9486 | 1126791.7305
14 | 2607983.3162 | 1126773.6268
15 | 2607788.1589 | 1126886.7919
16 | 2607848.0527 | 1126842.0577
17 | 2608012.4899 | 1126741.8451
18 | 2607996.8795 | 1126726.5694
19 | 2607987.006 | 1126769.2866
20 | 2607977.4038 | 1126707.5172
21 | 2607756.6608 | 1126878.003
22 | 2607756.6938 | 1126834.9594
23 | 2607843.6302 | 1126826.4304
24 | 2607737.5706 | 1126861.882
25 | 2607750.7971 | 1126907.3388
26 | 2607696.9608 | 1126855.5609
27 | 2607717.1402 | 1126902.3723
28 | 2607752.2683 | 1126946.7093
29 | 2607704.843 | 1126795.3081
30 | 2607690.6648 | 1126772.341
31 | 2607698.8772 | 1126839.4055
32 | 2607796.3887 | 1126944.7396
33 | 2607781.4535 | 1126949.2256
34 | 2607804.8944 | 1126942.1847
35 | 2607773.63 | 1126951.5755
36 | 2607905.3168 | 1127060.7191
37 | 2607759.012 | 1126955.9663
38 | 2607619.6795 | 1126885.4785
39 | 2607708.9812 | 1126911.0921
40 | 2607695.8769 | 1126952.8704
41 | 2607728.3436 | 1126993.8746
42 | 2607973.3892 | 1126703.59
43 | 2607962.4121 | 1126692.8517
44 | 2607867.6048 | 1126732.7187
45 | 2607851.9661 | 1126715.2349
46 | 2607823.9288 | 1126761.1986
47 | 2607907.2909 | 1126798.1352
48 | 2607841.6053 | 1126819.275
49 | 2607839.8138 | 1126812.9443
50 | 2607838.4549 | 1126695.0628
51 | 2607829.919 | 1126783.8348
52 | 2607832.2401 | 1126791.9297
53 | 2607834.5506 | 1126798.3407
54 | 2607860.389 | 1126884.3945

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1