## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6248-73_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6248-73_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6248-73_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6248-73_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6248-73_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6248-73_0_6_node_38 | 0.4 | n |  | TRUE
6 | bus_LV_6248-73_0_6_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_6248-73_0_6_node_39 | 0.4 | n |  | TRUE
8 | bus_LV_6248-73_0_6_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_6248-73_0_6_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_6248-73_0_6_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_6248-73_0_6_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_6248-73_0_6_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_6248-73_0_6_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_6248-73_0_6_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_6248-73_0_6_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_6248-73_0_6_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_6248-73_0_6_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_6248-73_0_6_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_6248-73_0_6_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_6248-73_0_6_node_32 | 0.4 | n |  | TRUE
21 | bus_LV_6248-73_0_6_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_6248-73_0_6_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_6248-73_0_6_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_6248-73_0_6_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_6248-73_0_6_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_6248-73_0_6_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_6248-73_0_6_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_6248-73_0_6_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_6248-73_0_6_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_6248-73_0_6_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_6248-73_0_6_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_6248-73_0_6_node_34 | 0.4 | n |  | TRUE
33 | bus_LV_6248-73_0_6_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_6248-73_0_6_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_6248-73_0_6_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_6248-73_0_6_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_6248-73_0_6_node_37 | 0.4 | n |  | TRUE
38 | bus_LV_6248-73_0_6_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_6248-73_0_6_node_40 | 0.4 | n |  | TRUE
40 | bus_MV_272_1_node_82 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6248-73_0_6_load_0 | 0 | 0.059588 | 0.014934 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6248-73_0_6_load_1 | 1 | 0.046805 | 0.01173 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6248-73_0_6_load_2 | 2 | 0.040026 | 0.010032 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6248-73_0_6_load_3 | 3 | 0.031234 | 0.0078279 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6248-73_0_6_load_4 | 4 | 0.038083 | 0.0095446 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6248-73_0_6_load_38 | 5 | 0.0060597 | 0.0015187 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6248-73_0_6_load_39 | 7 | 0.015386 | 0.0038562 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6248-73_0_6_load_7 | 8 | 0.016707 | 0.0041872 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6248-73_0_6_load_5 | 9 | 0.034526 | 0.008653 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6248-73_0_6_load_6 | 10 | 0.011157 | 0.0027961 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6248-73_0_6_load_8 | 11 | 0.0066582 | 0.0016687 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6248-73_0_6_load_13 | 12 | 0.0070304 | 0.001762 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6248-73_0_6_load_11 | 13 | 0.0052637 | 0.0013192 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6248-73_0_6_load_10 | 14 | 0.0048179 | 0.0012075 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6248-73_0_6_load_12 | 15 | 0.0052304 | 0.0013109 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6248-73_0_6_load_14 | 16 | 0.0062697 | 0.0015713 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6248-73_0_6_load_15 | 17 | 0.0092887 | 0.002328 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6248-73_0_6_load_16 | 18 | 0.007447 | 0.0018664 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6248-73_0_6_load_32 | 20 | 0.0093575 | 0.0023452 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6248-73_0_6_load_17 | 22 | 0.0095475 | 0.0023928 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6248-73_0_6_load_18 | 23 | 0.0096291 | 0.0024133 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6248-73_0_6_load_20 | 24 | 0.010999 | 0.0027565 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6248-73_0_6_load_30 | 25 | 0.0048657 | 0.0012195 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6248-73_0_6_load_23 | 26 | 0.0061063 | 0.0015304 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6248-73_0_6_load_24 | 27 | 0.004861 | 0.0012183 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6248-73_0_6_load_25 | 28 | 0.0044541 | 0.0011163 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6248-73_0_6_load_26 | 29 | 0.0046746 | 0.0011716 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6248-73_0_6_load_27 | 30 | 0.064607 | 0.016192 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6248-73_0_6_load_33 | 31 | 0.0043079 | 0.0010797 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6248-73_0_6_load_34 | 32 | 0.0044911 | 0.0011256 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6248-73_0_6_load_28 | 33 | 0.0070015 | 0.0017547 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6248-73_0_6_load_29 | 34 | 0.004389 | 0.0011 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6248-73_0_6_load_37 | 37 | 0.0096609 | 0.0024213 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6248-73_0_6_load_35 | 38 | 0.0068778 | 0.0017237 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6248-73_0_6_load_40 | 39 | 0.0095763 | 0.0024001 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6248-73_0_6_line_0 |  | 0 | 1 | 0.0014681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6248-73_0_6_line_1 |  | 0 | 2 | 0.024338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_6248-73_0_6_line_2 |  | 1 | 3 | 0.0073512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6248-73_0_6_line_3 |  | 2 | 4 | 0.0079633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_6248-73_0_6_line_4 |  | 3 | 5 | 0.021269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6248-73_0_6_line_5 |  | 4 | 6 | 0.036684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_6248-73_0_6_line_6 |  | 5 | 7 | 0.0059769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6248-73_0_6_line_7 |  | 6 | 8 | 0.011914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_6248-73_0_6_line_8 |  | 7 | 39 | 0.027649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6248-73_0_6_line_9 |  | 8 | 9 | 0.0082682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_6248-73_0_6_line_10 |  | 9 | 10 | 0.012467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_6248-73_0_6_line_11 |  | 10 | 11 | 0.01611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_6248-73_0_6_line_12 |  | 11 | 12 | 0.010705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_6248-73_0_6_line_13 |  | 12 | 13 | 0.0022586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_6248-73_0_6_line_14 |  | 13 | 14 | 0.0032389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_6248-73_0_6_line_15 |  | 14 | 15 | 0.0082886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_6248-73_0_6_line_16 |  | 15 | 16 | 0.0037506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_6248-73_0_6_line_17 |  | 16 | 17 | 0.011329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_6248-73_0_6_line_18 |  | 17 | 18 | 0.0073573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_6248-73_0_6_line_19 |  | 18 | 19 | 0.020425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_6248-73_0_6_line_20 |  | 19 | 20 | 0.015889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6248-73_0_6_line_21 |  | 19 | 21 | 0.022085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6248-73_0_6_line_22 |  | 20 | 25 | 0.011516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6248-73_0_6_line_23 |  | 21 | 24 | 0.0079438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6248-73_0_6_line_24 |  | 22 | 23 | 0.022999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6248-73_0_6_line_25 |  | 23 | 24 | 0.031232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6248-73_0_6_line_26 |  | 25 | 33 | 0.0059137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6248-73_0_6_line_27 |  | 26 | 27 | 0.0048852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6248-73_0_6_line_28 |  | 26 | 28 | 4.1552e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6248-73_0_6_line_29 |  | 27 | 29 | 0.0048747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6248-73_0_6_line_30 |  | 28 | 30 | 0.0080204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6248-73_0_6_line_31 |  | 29 | 31 | 0.0050088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6248-73_0_6_line_32 |  | 31 | 32 | 0.002731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6248-73_0_6_line_33 |  | 32 | 38 | 0.0048642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6248-73_0_6_line_34 |  | 33 | 34 | 0.0068481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6248-73_0_6_line_35 |  | 34 | 35 | 0.03337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6248-73_0_6_line_36 |  | 35 | 36 | 0.027935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6248-73_0_6_line_37 |  | 36 | 37 | 0.029929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6248-73_0_6_line_38 |  | 36 | 38 | 0.0037655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6248-73_0_6_trafo_6 | 0.63 MVA 20/0.4 kV | 40 | 10 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2607123.1335 | 1127160.3392 | 2607121.8802 | 1127161.1038
1 | 2607123.1335 | 1127160.3392 | 2607143.9106 | 1127147.6634
2 | 2607121.8802 | 1127161.1038 | 2607117.0477 | 1127164.052 | 2607115.413 | 1127164.4822
3 | 2607150.7086 | 1127143.5161 | 2607143.9106 | 1127147.6634
4 | 2607115.413 | 1127164.4822 | 2607100.9845 | 1127168.2798 | 2607094.6399 | 1127168.0309
5 | 2607186.0864 | 1127140.1101 | 2607172.2855 | 1127140.3495 | 2607157.9855 | 1127139.0765 | 2607150.7086 | 1127143.5161
6 | 2607088.6676 | 1127167.7967 | 2607094.6399 | 1127168.0309
7 | 2607186.0864 | 1127140.1101 | 2607193.8936 | 1127149.1101
8 | 2607088.6676 | 1127167.7967 | 2607081.4134 | 1127167.5122 | 2607061.5927 | 1127162.7314 | 2607061.5927 | 1127162.7314
9 | 2607193.8936 | 1127149.1101 | 2607199.3115 | 1127155.3559
10 | 2607199.3115 | 1127155.3559 | 2607207.4807 | 1127164.7732
11 | 2607218.4574 | 1127176.5191 | 2607215.4123 | 1127173.9167 | 2607207.4807 | 1127164.7732
12 | 2607226.5954 | 1127183.4741 | 2607218.4574 | 1127176.5191
13 | 2607228.3124 | 1127184.9415 | 2607226.5954 | 1127183.4741
14 | 2607228.3124 | 1127184.9415 | 2607230.7746 | 1127187.0458
15 | 2607237.0756 | 1127192.4308 | 2607230.7746 | 1127187.0458
16 | 2607237.0756 | 1127192.4308 | 2607239.9268 | 1127194.8675
17 | 2607248.5391 | 1127202.2278 | 2607239.9268 | 1127194.8675
18 | 2607248.5391 | 1127202.2278 | 2607254.1321 | 1127207.0078
19 | 2607270.638 | 1127218.8263 | 2607263.8152 | 1127215.2832 | 2607254.1321 | 1127207.0078
20 | 2607270.638 | 1127218.8263 | 2607260.7948 | 1127231.2988
21 | 2607270.638 | 1127218.8263 | 2607279.2353 | 1127207.52 | 2607281.7972 | 1127204.4326 | 2607279.9983 | 1127201.0066
22 | 2607253.6605 | 1127240.3389 | 2607253.6605 | 1127240.3389 | 2607260.7948 | 1127231.2988
23 | 2607279.9983 | 1127201.0066 | 2607280.3306 | 1127200.1288 | 2607279.9177 | 1127197.4492 | 2607278.6179 | 1127195.4467 | 2607277.5974 | 1127193.8363
24 | 2607261.429 | 1127167.1278 | 2607261.4145 | 1127167.1013 | 2607257.6097 | 1127159.2151 | 2607254.7747 | 1127152.1972 | 2607252.8164 | 1127146.6477 | 2607252.6163 | 1127145.9153
25 | 2607261.429 | 1127167.1278 | 2607265.082 | 1127173.82 | 2607272.1882 | 1127185.3007 | 2607277.5974 | 1127193.8363
26 | 2607251.5929 | 1127245.8794 | 2607253.6605 | 1127240.3389
27 | 2607199.1005 | 1127257.7562 | 2607203.033 | 1127260.6547
28 | 2607199.0671 | 1127257.7315 | 2607199.1005 | 1127257.7562
29 | 2607203.033 | 1127260.6547 | 2607206.9569 | 1127263.5471
30 | 2607192.611 | 1127252.9728 | 2607199.0671 | 1127257.7315
31 | 2607210.9888 | 1127266.5189 | 2607206.9569 | 1127263.5471
32 | 2607210.9888 | 1127266.5189 | 2607213.1872 | 1127268.1393
33 | 2607213.1872 | 1127268.1393 | 2607217.1027 | 1127271.0254
34 | 2607251.5929 | 1127245.8794 | 2607251.496 | 1127246.1391 | 2607252.3608 | 1127251.1537 | 2607252.8395 | 1127252.5566
35 | 2607246.0807 | 1127283.7955 | 2607252.6392 | 1127269.7186 | 2607254.8272 | 1127263.5293 | 2607254.649 | 1127257.8597 | 2607252.8395 | 1127252.5566
36 | 2607246.0807 | 1127283.7955 | 2607220.1338 | 1127273.2596
37 | 2607220.1338 | 1127273.2596 | 2607212.3139 | 1127278.8753 | 2607205.7731 | 1127277.956 | 2607193.2818 | 1127272.1718
38 | 2607220.1338 | 1127273.2596 | 2607217.1027 | 1127271.0254

## bus_geodata
| x | y | coords
0 | 2607123.1335 | 1127160.3392
1 | 2607121.8802 | 1127161.1038
2 | 2607143.9106 | 1127147.6634
3 | 2607115.413 | 1127164.4822
4 | 2607150.7086 | 1127143.5161
5 | 2607094.6399 | 1127168.0309
6 | 2607186.0864 | 1127140.1101
7 | 2607088.6676 | 1127167.7967
8 | 2607193.8936 | 1127149.1101
9 | 2607199.3115 | 1127155.3559
10 | 2607207.4807 | 1127164.7732
11 | 2607218.4574 | 1127176.5191
12 | 2607226.5954 | 1127183.4741
13 | 2607228.3124 | 1127184.9415
14 | 2607230.7746 | 1127187.0458
15 | 2607237.0756 | 1127192.4308
16 | 2607239.9268 | 1127194.8675
17 | 2607248.5391 | 1127202.2278
18 | 2607254.1321 | 1127207.0078
19 | 2607270.638 | 1127218.8263
20 | 2607260.7948 | 1127231.2988
21 | 2607279.9983 | 1127201.0066
22 | 2607252.6163 | 1127145.9153
23 | 2607261.429 | 1127167.1278
24 | 2607277.5974 | 1127193.8363
25 | 2607253.6605 | 1127240.3389
26 | 2607199.1005 | 1127257.7562
27 | 2607203.033 | 1127260.6547
28 | 2607199.0671 | 1127257.7315
29 | 2607206.9569 | 1127263.5471
30 | 2607192.611 | 1127252.9728
31 | 2607210.9888 | 1127266.5189
32 | 2607213.1872 | 1127268.1393
33 | 2607251.5929 | 1127245.8794
34 | 2607252.8395 | 1127252.5566
35 | 2607246.0807 | 1127283.7955
36 | 2607220.1338 | 1127273.2596
37 | 2607193.2818 | 1127272.1718
38 | 2607217.1027 | 1127271.0254
39 | 2607061.5927 | 1127162.7314
40 | 2607210.2351 | 1127167.9485

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1