## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6248-94_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6248-94_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6248-94_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6248-94_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6248-94_0_3_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_6248-94_0_3_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_6248-94_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_6248-94_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_6248-94_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_6248-94_0_3_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_6248-94_0_3_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_6248-94_0_3_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_6248-94_0_3_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_6248-94_0_3_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_6248-94_0_3_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_6248-94_0_3_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_6248-94_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_6248-94_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_6248-94_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_6248-94_0_3_node_46 | 0.4 | n |  | TRUE
20 | bus_LV_6248-94_0_3_node_63 | 0.4 | n |  | TRUE
21 | bus_LV_6248-94_0_3_node_69 | 0.4 | n |  | TRUE
22 | bus_LV_6248-94_0_3_node_43 | 0.4 | n |  | TRUE
23 | bus_LV_6248-94_0_3_node_64 | 0.4 | n |  | TRUE
24 | bus_LV_6248-94_0_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_6248-94_0_3_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_6248-94_0_3_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_6248-94_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_6248-94_0_3_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_6248-94_0_3_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_6248-94_0_3_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_6248-94_0_3_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_6248-94_0_3_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_6248-94_0_3_node_62 | 0.4 | n |  | TRUE
34 | bus_LV_6248-94_0_3_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_6248-94_0_3_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_6248-94_0_3_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_6248-94_0_3_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_6248-94_0_3_node_38 | 0.4 | n |  | TRUE
39 | bus_LV_6248-94_0_3_node_39 | 0.4 | n |  | TRUE
40 | bus_LV_6248-94_0_3_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_6248-94_0_3_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_6248-94_0_3_node_31 | 0.4 | n |  | TRUE
43 | bus_LV_6248-94_0_3_node_32 | 0.4 | n |  | TRUE
44 | bus_LV_6248-94_0_3_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_6248-94_0_3_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_6248-94_0_3_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_6248-94_0_3_node_60 | 0.4 | n |  | TRUE
48 | bus_LV_6248-94_0_3_node_58 | 0.4 | n |  | TRUE
49 | bus_LV_6248-94_0_3_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_6248-94_0_3_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_6248-94_0_3_node_44 | 0.4 | n |  | TRUE
52 | bus_LV_6248-94_0_3_node_45 | 0.4 | n |  | TRUE
53 | bus_LV_6248-94_0_3_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_6248-94_0_3_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_6248-94_0_3_node_66 | 0.4 | n |  | TRUE
56 | bus_LV_6248-94_0_3_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_6248-94_0_3_node_67 | 0.4 | n |  | TRUE
58 | bus_LV_6248-94_0_3_node_50 | 0.4 | n |  | TRUE
59 | bus_LV_6248-94_0_3_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_6248-94_0_3_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_6248-94_0_3_node_53 | 0.4 | n |  | TRUE
62 | bus_LV_6248-94_0_3_node_55 | 0.4 | n |  | TRUE
63 | bus_LV_6248-94_0_3_node_56 | 0.4 | n |  | TRUE
64 | bus_LV_6248-94_0_3_node_54 | 0.4 | n |  | TRUE
65 | bus_LV_6248-94_0_3_node_70 | 0.4 | n |  | TRUE
66 | bus_LV_6248-94_0_3_node_57 | 0.4 | n |  | TRUE
67 | bus_LV_6248-94_0_3_node_59 | 0.4 | n |  | TRUE
68 | bus_LV_6248-94_0_3_node_61 | 0.4 | n |  | TRUE
69 | bus_LV_6248-94_0_3_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_6248-94_0_3_node_68 | 0.4 | n |  | TRUE
71 | bus_MV_113_1_node_152 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6248-94_0_3_load_0 | 0 | 0.0022882 | 0.00057348 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6248-94_0_3_load_1 | 1 | 0.0026963 | 0.00067576 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6248-94_0_3_load_2 | 2 | 0.0053283 | 0.0013354 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6248-94_0_3_load_3 | 3 | 0.0023674 | 0.00059334 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6248-94_0_3_load_7 | 4 | 0.0028212 | 0.00070705 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6248-94_0_3_load_4 | 6 | 0.0046209 | 0.0011581 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6248-94_0_3_load_5 | 7 | 0.0056038 | 0.0014044 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6248-94_0_3_load_9 | 10 | 0.0058141 | 0.0014572 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6248-94_0_3_load_17 | 11 | 0.0047755 | 0.0011968 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6248-94_0_3_load_10 | 12 | 0.0054912 | 0.0013762 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6248-94_0_3_load_15 | 13 | 0.0046678 | 0.0011699 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6248-94_0_3_load_18 | 15 | 0.0043671 | 0.0010945 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6248-94_0_3_load_12 | 16 | 0.0065406 | 0.0016392 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6248-94_0_3_load_14 | 17 | 0.0089448 | 0.0022418 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6248-94_0_3_load_63 | 20 | 0.0083917 | 0.0021032 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6248-94_0_3_load_69 | 21 | 0.0044709 | 0.0011205 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6248-94_0_3_load_19 | 24 | 0.0038326 | 0.00096055 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6248-94_0_3_load_30 | 25 | 0.0033843 | 0.00084818 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6248-94_0_3_load_28 | 26 | 0.0039026 | 0.00097808 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6248-94_0_3_load_20 | 27 | 0.0036851 | 0.00092358 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6248-94_0_3_load_21 | 28 | 0.0038131 | 0.00095566 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6248-94_0_3_load_22 | 29 | 0.0059997 | 0.0015037 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6248-94_0_3_load_23 | 30 | 0.003159 | 0.00079172 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6248-94_0_3_load_62 | 33 | 0.0038866 | 0.00097408 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6248-94_0_3_load_36 | 34 | 0.0031523 | 0.00079004 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6248-94_0_3_load_25 | 35 | 0.0040735 | 0.0010209 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6248-94_0_3_load_26 | 36 | 0.0073023 | 0.0018301 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6248-94_0_3_load_27 | 37 | 0.010865 | 0.0027231 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6248-94_0_3_load_38 | 38 | 0.007613 | 0.001908 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6248-94_0_3_load_39 | 39 | 0.0034764 | 0.00087127 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6248-94_0_3_load_40 | 40 | 0.0027447 | 0.00068789 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6248-94_0_3_load_31 | 42 | 0.0025808 | 0.0006468 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6248-94_0_3_load_32 | 43 | 0.00324 | 0.00081202 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6248-94_0_3_load_34 | 44 | 0.0022999 | 0.0005764 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6248-94_0_3_load_37 | 46 | 0.00306 | 0.00076692 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6248-94_0_3_load_60 | 47 | 0.0034755 | 0.00087103 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6248-94_0_3_load_58 | 48 | 0.0031875 | 0.00079886 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6248-94_0_3_load_41 | 49 | 0.0068845 | 0.0017254 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6248-94_0_3_load_44 | 51 | 0.0066616 | 0.0016696 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6248-94_0_3_load_45 | 52 | 0.0035406 | 0.00088735 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6248-94_0_3_load_47 | 53 | 0.01008 | 0.0025263 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6248-94_0_3_load_48 | 54 | 0.0065342 | 0.0016376 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6248-94_0_3_load_66 | 55 | 0.0074482 | 0.0018667 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6248-94_0_3_load_49 | 56 | 0.0070114 | 0.0017572 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6248-94_0_3_load_67 | 57 | 0.0042335 | 0.001061 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6248-94_0_3_load_50 | 58 | 0.009486 | 0.0023774 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6248-94_0_3_load_52 | 60 | 0.013298 | 0.0033327 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6248-94_0_3_load_56 | 63 | 0.0098807 | 0.0024763 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6248-94_0_3_load_54 | 64 | 0.0058252 | 0.0014599 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6248-94_0_3_load_70 | 65 | 0.0065545 | 0.0016427 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6248-94_0_3_load_57 | 66 | 0.0029048 | 0.00072802 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6248-94_0_3_load_59 | 67 | 0.0030873 | 0.00077376 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6248-94_0_3_load_61 | 68 | 0.012363 | 0.0030986 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6248-94_0_3_load_65 | 69 | 0.0056402 | 0.0014136 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6248-94_0_3_load_68 | 70 | 0.0051844 | 0.0012993 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 35 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6248-94_0_3_line_0 |  | 0 | 1 | 0.021497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6248-94_0_3_line_1 |  | 0 | 2 | 0.023811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6248-94_0_3_line_2 |  | 1 | 3 | 0.010423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6248-94_0_3_line_3 |  | 3 | 4 | 0.010609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6248-94_0_3_line_4 |  | 4 | 5 | 0.012406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6248-94_0_3_line_5 |  | 5 | 12 | 0.01224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_6248-94_0_3_line_6 |  | 5 | 10 | 0.0061425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_6248-94_0_3_line_7 |  | 6 | 7 | 0.01711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6248-94_0_3_line_8 |  | 7 | 8 | 0.025342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6248-94_0_3_line_9 |  | 8 | 9 | 0.002751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_6248-94_0_3_line_10 |  | 8 | 10 | 0.036697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_6248-94_0_3_line_11 |  | 9 | 11 | 0.013664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_6248-94_0_3_line_12 |  | 11 | 15 | 0.014001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_6248-94_0_3_line_13 |  | 12 | 13 | 0.014071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_6248-94_0_3_line_14 |  | 13 | 14 | 0.011654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_6248-94_0_3_line_15 |  | 14 | 18 | 0.018454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6248-94_0_3_line_16 |  | 14 | 16 | 0.01576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6248-94_0_3_line_17 |  | 15 | 24 | 0.0073565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_6248-94_0_3_line_18 |  | 16 | 17 | 0.042729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6248-94_0_3_line_19 |  | 18 | 19 | 0.020499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6248-94_0_3_line_20 |  | 18 | 20 | 0.0082167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6248-94_0_3_line_21 |  | 19 | 21 | 0.008964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6248-94_0_3_line_22 |  | 19 | 22 | 0.006445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6248-94_0_3_line_23 |  | 20 | 23 | 0.027824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6248-94_0_3_line_24 |  | 22 | 53 | 0.01451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6248-94_0_3_line_25 |  | 22 | 49 | 0.011099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6248-94_0_3_line_26 |  | 23 | 69 | 0.007223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6248-94_0_3_line_27 |  | 24 | 25 | 0.015601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_6248-94_0_3_line_28 |  | 25 | 26 | 0.0036351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_6248-94_0_3_line_29 |  | 26 | 31 | 0.015178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_6248-94_0_3_line_30 |  | 27 | 28 | 0.015789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6248-94_0_3_line_31 |  | 27 | 29 | 0.0054821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6248-94_0_3_line_32 |  | 28 | 30 | 0.00086961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6248-94_0_3_line_33 |  | 30 | 31 | 0.028611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6248-94_0_3_line_34 |  | 31 | 32 | 0.03416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_6248-94_0_3_line_35 |  | 32 | 33 | 0.013645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_6248-94_0_3_line_36 |  | 32 | 34 | 0.014082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6248-94_0_3_line_37 |  | 33 | 40 | 0.010328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_6248-94_0_3_line_38 |  | 34 | 41 | 0.0011014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6248-94_0_3_line_39 |  | 35 | 36 | 0.013414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_6248-94_0_3_line_40 |  | 36 | 37 | 0.0081942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_6248-94_0_3_line_41 |  | 37 | 38 | 0.0061457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_6248-94_0_3_line_42 |  | 38 | 39 | 0.017881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_6248-94_0_3_line_43 |  | 39 | 40 | 0.010308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_6248-94_0_3_line_44 |  | 41 | 45 | 0.034745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6248-94_0_3_line_45 |  | 41 | 42 | 0.018271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6248-94_0_3_line_46 |  | 42 | 43 | 0.0014781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6248-94_0_3_line_47 |  | 43 | 44 | 0.0089579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6248-94_0_3_line_48 |  | 44 | 46 | 0.049756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6248-94_0_3_line_49 |  | 45 | 47 | 0.013781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6248-94_0_3_line_50 |  | 47 | 48 | 0.0080503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6248-94_0_3_line_51 |  | 48 | 66 | 0.014316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6248-94_0_3_line_52 |  | 49 | 50 | 0.032925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6248-94_0_3_line_53 |  | 50 | 51 | 0.011216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6248-94_0_3_line_54 |  | 50 | 52 | 0.015886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6248-94_0_3_line_55 |  | 51 | 54 | 0.0033334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6248-94_0_3_line_56 |  | 52 | 55 | 0.0005303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6248-94_0_3_line_57 |  | 54 | 56 | 0.025335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6248-94_0_3_line_58 |  | 55 | 57 | 0.0099762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6248-94_0_3_line_59 |  | 56 | 58 | 0.0038329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6248-94_0_3_line_60 |  | 57 | 70 | 0.016647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6248-94_0_3_line_61 |  | 58 | 59 | 0.010264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6248-94_0_3_line_62 |  | 59 | 60 | 0.047038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6248-94_0_3_line_63 |  | 59 | 61 | 0.021726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6248-94_0_3_line_64 |  | 61 | 62 | 0.01585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6248-94_0_3_line_65 |  | 61 | 63 | 0.056189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6248-94_0_3_line_66 |  | 61 | 64 | 0.014747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6248-94_0_3_line_67 |  | 62 | 65 | 0.008713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6248-94_0_3_line_68 |  | 66 | 67 | 0.013866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6248-94_0_3_line_69 |  | 67 | 68 | 0.0089628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6248-94_0_3_trafo_25 | 0.63 MVA 20/0.4 kV | 71 | 35 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2602010.0102 | 1122814.4892 | 2601998.3196 | 1122813.2538 | 2601988.6756 | 1122811.8794
1 | 2602010.0102 | 1122814.4892 | 2602033.689 | 1122816.9916
2 | 2601988.6756 | 1122811.8794 | 2601978.3568 | 1122810.4088
3 | 2601967.8538 | 1122808.9119 | 2601978.3568 | 1122810.4088
4 | 2601955.5172 | 1122807.7376 | 2601961.6552 | 1122808.0285 | 2601967.8538 | 1122808.9119
5 | 2601955.5172 | 1122807.7376 | 2601954.9814 | 1122819.9661
6 | 2601955.5172 | 1122807.7376 | 2601955.8796 | 1122801.6058
7 | 2601994.1901 | 1122776.4275 | 2601994.3998 | 1122772.6994 | 2601993.4984 | 1122770.1868 | 2601991.5248 | 1122768.9411 | 2601983.2105 | 1122767.9557
8 | 2601958.0444 | 1122764.9731 | 2601983.2105 | 1122767.9557
9 | 2601958.2072 | 1122762.2273 | 2601958.0444 | 1122764.9731
10 | 2601958.0444 | 1122764.9731 | 2601955.8796 | 1122801.6058
11 | 2601958.2072 | 1122762.2273 | 2601949.5478 | 1122761.4465 | 2601944.633 | 1122760.7129
12 | 2601930.7858 | 1122758.6459 | 2601944.633 | 1122760.7129
13 | 2601954.3654 | 1122834.0237 | 2601954.9814 | 1122819.9661
14 | 2601953.8553 | 1122845.6667 | 2601954.3654 | 1122834.0237
15 | 2601953.0322 | 1122864.0977 | 2601953.8553 | 1122845.6667
16 | 2601953.8553 | 1122845.6667 | 2601957.541 | 1122845.9458 | 2601969.4726 | 1122847.7288
17 | 2601930.7858 | 1122758.6459 | 2601923.51 | 1122757.5599
18 | 2602003.7386 | 1122843.0923 | 2602003.7363 | 1122850.3514 | 2602002.3863 | 1122852.0407 | 2602000.8517 | 1122852.4181 | 2601969.4726 | 1122847.7288
19 | 2601953.0322 | 1122864.0977 | 2601949.2154 | 1122863.5073 | 2601944.9288 | 1122861.3605 | 2601938.3137 | 1122858.3459 | 2601933.8957 | 1122856.9772
20 | 2601953.0322 | 1122864.0977 | 2601952.8169 | 1122872.3115
21 | 2601932.6284 | 1122865.8366 | 2601932.9689 | 1122861.7903 | 2601933.8957 | 1122856.9772
22 | 2601927.5731 | 1122855.6746 | 2601932.5695 | 1122856.5766 | 2601933.8957 | 1122856.9772
23 | 2601952.0879 | 1122900.1261 | 2601952.8169 | 1122872.3115
24 | 2601927.4144 | 1122870.1594 | 2601927.1473 | 1122860.977 | 2601927.5731 | 1122855.6746
25 | 2601927.5731 | 1122855.6746 | 2601921.6511 | 1122855.3948 | 2601916.4999 | 1122855.8382
26 | 2601944.8629 | 1122899.6013 | 2601952.0879 | 1122900.1261
27 | 2601923.51 | 1122757.5599 | 2601908.0797 | 1122755.2566
28 | 2601904.4845 | 1122754.72 | 2601908.0797 | 1122755.2566
29 | 2601889.4732 | 1122752.4793 | 2601904.4845 | 1122754.72
30 | 2601890.1199 | 1122797.745 | 2601889.8944 | 1122781.9572
31 | 2601890.1982 | 1122803.2265 | 2601890.1199 | 1122797.745
32 | 2601889.8944 | 1122781.9572 | 2601889.882 | 1122781.0876
33 | 2601889.4732 | 1122752.4793 | 2601889.882 | 1122781.0876
34 | 2601855.4143 | 1122748.7785 | 2601889.4732 | 1122752.4793
35 | 2601855.4143 | 1122748.7785 | 2601855.1446 | 1122762.4204
36 | 2601855.4143 | 1122748.7785 | 2601841.4474 | 1122746.9804
37 | 2601854.9405 | 1122772.7464 | 2601855.1446 | 1122762.4204
38 | 2601840.355 | 1122746.8398 | 2601841.4474 | 1122746.9804
39 | 2601878.0031 | 1122809.3334 | 2601864.6493 | 1122810.6003 | 2601864.6493 | 1122810.6003
40 | 2601857.4329 | 1122806.7185 | 2601857.4329 | 1122806.7185 | 2601864.6493 | 1122810.6003
41 | 2601855.431 | 1122800.9079 | 2601857.4329 | 1122806.7185
42 | 2601855.431 | 1122800.9079 | 2601855.3989 | 1122800.815 | 2601854.6628 | 1122786.7968 | 2601854.7368 | 1122783.0521
43 | 2601854.9405 | 1122772.7464 | 2601854.7368 | 1122783.0521
44 | 2601805.795 | 1122742.3831 | 2601840.355 | 1122746.8398
45 | 2601840.355 | 1122746.8398 | 2601840.5328 | 1122745.4502 | 2601841.3597 | 1122739.014 | 2601842.6868 | 1122728.7183
46 | 2601842.6868 | 1122728.7183 | 2601842.8758 | 1122727.2524
47 | 2601842.8758 | 1122727.2524 | 2601844.021 | 1122718.368
48 | 2601871.4061 | 1122726.4056 | 2601872.1423 | 1122714.2221 | 2601854.8946 | 1122706.869 | 2601849.4659 | 1122707.0119 | 2601846.5813 | 1122708.8564 | 2601844.6754 | 1122713.2913 | 2601844.021 | 1122718.368
49 | 2601805.795 | 1122742.3831 | 2601806.031 | 1122756.1625
50 | 2601806.031 | 1122756.1625 | 2601806.1666 | 1122764.0827 | 2601806.1659 | 1122764.2116
51 | 2601806.0907 | 1122778.5278 | 2601806.1659 | 1122764.2116
52 | 2601884.1583 | 1122861.9867 | 2601911.0404 | 1122856.6922 | 2601916.2456 | 1122855.8601 | 2601916.4999 | 1122855.8382
53 | 2601884.1583 | 1122861.9867 | 2601873.1668 | 1122864.2193
54 | 2601884.1583 | 1122861.9867 | 2601885.0209 | 1122865.2552 | 2601888.0471 | 1122877.3888
55 | 2601869.9001 | 1122864.8829 | 2601873.1668 | 1122864.2193
56 | 2601888.1755 | 1122877.9033 | 2601888.0471 | 1122877.3888
57 | 2601869.9001 | 1122864.8829 | 2601845.0723 | 1122869.9259
58 | 2601888.1755 | 1122877.9033 | 2601890.5896 | 1122887.583
59 | 2601841.3161 | 1122870.6888 | 2601845.0723 | 1122869.9259
60 | 2601904.6603 | 1122892.2743 | 2601899.6943 | 1122892.8842 | 2601895.8697 | 1122892.8831 | 2601893.5952 | 1122891.8486 | 2601892.2539 | 1122890.6142 | 2601890.8049 | 1122888.4461 | 2601890.5896 | 1122887.583
61 | 2601831.2578 | 1122872.7319 | 2601841.3161 | 1122870.6888
62 | 2601850.2688 | 1122913.2461 | 2601849.7994 | 1122910.1889 | 2601848.1962 | 1122907.9318 | 2601844.9968 | 1122905.7298 | 2601841.327 | 1122903.6055 | 2601838.9912 | 1122901.337 | 2601837.3881 | 1122898.8131 | 2601836.1245 | 1122895.4889 | 2601831.2578 | 1122872.7319
63 | 2601809.9048 | 1122877.0612 | 2601831.2578 | 1122872.7319
64 | 2601809.9048 | 1122877.0612 | 2601794.3278 | 1122880.2249
65 | 2601809.9048 | 1122877.0612 | 2601812.5694 | 1122889.1567 | 2601814.1026 | 1122893.4148 | 2601817.1701 | 1122898.407 | 2601822.6425 | 1122906.6571 | 2601826.0409 | 1122914.0394 | 2601828.1059 | 1122919.2314 | 2601829.507 | 1122927.1468 | 2601829.1749 | 1122928.8809
66 | 2601809.9048 | 1122877.0612 | 2601809.1738 | 1122871.9029 | 2601809.5243 | 1122862.3721
67 | 2601794.0912 | 1122871.5428 | 2601793.9124 | 1122876.8231 | 2601794.3278 | 1122880.2249
68 | 2601806.0907 | 1122778.5278 | 2601806.0179 | 1122792.3937
69 | 2601805.9708 | 1122801.3564 | 2601806.0179 | 1122792.3937

## bus_geodata
| x | y | coords
0 | 2602010.0102 | 1122814.4892
1 | 2601988.6756 | 1122811.8794
2 | 2602033.689 | 1122816.9916
3 | 2601978.3568 | 1122810.4088
4 | 2601967.8538 | 1122808.9119
5 | 2601955.5172 | 1122807.7376
6 | 2601994.1901 | 1122776.4275
7 | 2601983.2105 | 1122767.9557
8 | 2601958.0444 | 1122764.9731
9 | 2601958.2072 | 1122762.2273
10 | 2601955.8796 | 1122801.6058
11 | 2601944.633 | 1122760.7128
12 | 2601954.9814 | 1122819.9661
13 | 2601954.3654 | 1122834.0237
14 | 2601953.8553 | 1122845.6667
15 | 2601930.7858 | 1122758.6459
16 | 2601969.4726 | 1122847.7288
17 | 2602003.7386 | 1122843.0923
18 | 2601953.0322 | 1122864.0977
19 | 2601933.8957 | 1122856.9772
20 | 2601952.8169 | 1122872.3115
21 | 2601932.6284 | 1122865.8366
22 | 2601927.5731 | 1122855.6746
23 | 2601952.0879 | 1122900.1261
24 | 2601923.51 | 1122757.5599
25 | 2601908.0797 | 1122755.2566
26 | 2601904.4845 | 1122754.72
27 | 2601890.1199 | 1122797.745
28 | 2601889.8944 | 1122781.9572
29 | 2601890.1982 | 1122803.2265
30 | 2601889.882 | 1122781.0876
31 | 2601889.4732 | 1122752.4793
32 | 2601855.4143 | 1122748.7785
33 | 2601855.1446 | 1122762.4204
34 | 2601841.4474 | 1122746.9804
35 | 2601878.0031 | 1122809.3334
36 | 2601864.6493 | 1122810.6003
37 | 2601857.4329 | 1122806.7185
38 | 2601855.431 | 1122800.9079
39 | 2601854.7368 | 1122783.0521
40 | 2601854.9405 | 1122772.7464
41 | 2601840.355 | 1122746.8398
42 | 2601842.6868 | 1122728.7183
43 | 2601842.8758 | 1122727.2524
44 | 2601844.021 | 1122718.368
45 | 2601805.795 | 1122742.3831
46 | 2601871.4061 | 1122726.4056
47 | 2601806.031 | 1122756.1625
48 | 2601806.1659 | 1122764.2116
49 | 2601916.4999 | 1122855.8382
50 | 2601884.1583 | 1122861.9867
51 | 2601873.1668 | 1122864.2193
52 | 2601888.0471 | 1122877.3888
53 | 2601927.4144 | 1122870.1594
54 | 2601869.9001 | 1122864.8829
55 | 2601888.1755 | 1122877.9033
56 | 2601845.0723 | 1122869.9259
57 | 2601890.5896 | 1122887.583
58 | 2601841.3161 | 1122870.6888
59 | 2601831.2578 | 1122872.7319
60 | 2601850.2688 | 1122913.2461
61 | 2601809.9048 | 1122877.0612
62 | 2601794.3278 | 1122880.2249
63 | 2601829.1749 | 1122928.8809
64 | 2601809.5243 | 1122862.3721
65 | 2601794.0912 | 1122871.5428
66 | 2601806.0907 | 1122778.5278
67 | 2601806.0179 | 1122792.3937
68 | 2601805.9708 | 1122801.3564
69 | 2601944.8629 | 1122899.6013
70 | 2601904.6603 | 1122892.2743
71 | 2601882.0536 | 1122808.9491

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1