## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6253-4_0_1_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6253-4_0_1_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6253-4_0_1_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6253-4_0_1_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6253-4_0_1_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_6253-4_0_1_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_6253-4_0_1_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_6253-4_0_1_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_6253-4_0_1_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_6253-4_0_1_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_6253-4_0_1_node_21 | 0.4 | n |  | TRUE
11 | bus_LV_6253-4_0_1_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_6253-4_0_1_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_6253-4_0_1_node_24 | 0.4 | n |  | TRUE
14 | bus_LV_6253-4_0_1_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_6253-4_0_1_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_6253-4_0_1_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_6253-4_0_1_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_6253-4_0_1_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_6253-4_0_1_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_6253-4_0_1_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_6253-4_0_1_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_6253-4_0_1_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_6253-4_0_1_node_18 | 0.4 | n |  | TRUE
24 | bus_MV_0_node_21 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6253-4_0_1_load_0 | 0 | 0.00029877 | 7.4879e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6253-4_0_1_load_19 | 5 | 0.00061047 | 0.000153 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6253-4_0_1_load_16 | 6 | 0.00060296 | 0.00015112 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6253-4_0_1_load_21 | 10 | 0.00071099 | 0.00017819 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6253-4_0_1_load_15 | 12 | 0.0045217 | 0.0011332 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6253-4_0_1_load_24 | 13 | 0.00031069 | 7.7865e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6253-4_0_1_load_10 | 14 | 0.015332 | 0.0038426 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6253-4_0_1_load_12 | 17 | 0.00048352 | 0.00012118 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6253-4_0_1_load_23 | 19 | 0.0012616 | 0.00031618 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6253-4_0_1_load_14 | 20 | 0.0011177 | 0.00028012 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6253-4_0_1_load_11 | 21 | 0.00038536 | 9.6579e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6253-4_0_1_load_13 | 22 | 0.00098443 | 0.00024672 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6253-4_0_1_load_18 | 23 | 0.00073898 | 0.0001852 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6253-4_0_1_line_0 |  | 0 | 1 | 0.10314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6253-4_0_1_line_1 |  | 0 | 2 | 0.35693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6253-4_0_1_line_2 |  | 1 | 3 | 0.89098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6253-4_0_1_line_3 |  | 2 | 4 | 1.3597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6253-4_0_1_line_4 |  | 3 | 5 | 0.069075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6253-4_0_1_line_5 |  | 3 | 6 | 0.13227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6253-4_0_1_line_6 |  | 4 | 13 | 0.10152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6253-4_0_1_line_7 |  | 4 | 7 | 1.0932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6253-4_0_1_line_8 |  | 4 | 11 | 0.13157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6253-4_0_1_line_9 |  | 6 | 18 | 0.10875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6253-4_0_1_line_10 |  | 7 | 8 | 0.83437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6253-4_0_1_line_11 |  | 7 | 9 | 0.058608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6253-4_0_1_line_12 |  | 7 | 10 | 0.061027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6253-4_0_1_line_13 |  | 8 | 19 | 0.18002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6253-4_0_1_line_14 |  | 9 | 14 | 0.038644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6253-4_0_1_line_15 |  | 11 | 12 | 0.087949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6253-4_0_1_line_16 |  | 12 | 20 | 0.012859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6253-4_0_1_line_17 |  | 14 | 15 | 0.0076389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6253-4_0_1_line_18 |  | 15 | 16 | 0.037221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6253-4_0_1_line_19 |  | 16 | 17 | 0.072402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6253-4_0_1_line_20 |  | 17 | 21 | 0.0086212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6253-4_0_1_line_21 |  | 18 | 23 | 0.16179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6253-4_0_1_line_22 |  | 20 | 22 | 0.022381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6253-4_0_1_trafo_21 | 0.63 MVA 20/0.4 kV | 24 | 10 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48 | x49 | y49 | x50 | y50 | x51 | y51 | x52 | y52 | x53 | y53 | x54 | y54 | x55 | y55 | x56 | y56 | x57 | y57 | x58 | y58 | x59 | y59 | x60 | y60 | x61 | y61 | x62 | y62 | x63 | y63 | x64 | y64 | x65 | y65 | x66 | y66 | x67 | y67 | x68 | y68 | x69 | y69 | x70 | y70 | x71 | y71 | x72 | y72 | x73 | y73 | x74 | y74 | x75 | y75 | x76 | y76 | x77 | y77 | x78 | y78 | x79 | y79 | x80 | y80 | x81 | y81 | x82 | y82 | x83 | y83 | x84 | y84 | x85 | y85
0 | 2605322.1404 | 1132781.7387 | 2605319.4257 | 1132778.4347 | 2605315.3071 | 1132778.4089 | 2605296.8086 | 1132777.7259 | 2605286.7024 | 1132775.7273 | 2605263.0615 | 1132765.9132 | 2605259.4149 | 1132763.0754 | 2605256.1927 | 1132759.193 | 2605254.8882 | 1132754.2228 | 2605254.3759 | 1132750.1314 | 2605257.7967 | 1132728.9998
1 | 2605156.7515 | 1132578.0425 | 2605166.2384 | 1132584.4759 | 2605169.7483 | 1132585.257 | 2605173.1583 | 1132585.8824 | 2605177.2307 | 1132586.0415 | 2605181.9583 | 1132585.2228 | 2605188.1652 | 1132583.1048 | 2605198.9097 | 1132577.2111 | 2605200.5192 | 1132576.6233 | 2605202.2284 | 1132576.4913 | 2605202.936 | 1132577.2923 | 2605202.9814 | 1132578.2595 | 2605202.4722 | 1132579.5597 | 2605200.6609 | 1132582.0705 | 2605199.2113 | 1132584.7483 | 2605196.7045 | 1132590.2822 | 2605194.1351 | 1132597.1056 | 2605191.5596 | 1132602.0614 | 2605188.8695 | 1132605.9499 | 2605184.9085 | 1132610.5599 | 2605180.4403 | 1132614.1356 | 2605177.2825 | 1132615.7782 | 2605170.2513 | 1132618.6625 | 2605165.4071 | 1132620.8818 | 2605161.6711 | 1132623.4799 | 2605155.2226 | 1132629.1994 | 2605146.5848 | 1132638.3744 | 2605142.2762 | 1132644.4293 | 2605140.3477 | 1132649.1411 | 2605138.8332 | 1132655.7319 | 2605137.7417 | 1132662.8678 | 2605135.7949 | 1132671.0257 | 2605131.0038 | 1132683.2721 | 2605126.6166 | 1132691.4724 | 2605126.052 | 1132694.5067 | 2605126.1663 | 1132695.9186 | 2605127.0355 | 1132696.7864 | 2605128.1438 | 1132697.1764 | 2605130.7844 | 1132697.0453 | 2605135.9665 | 1132695.8379 | 2605138.8766 | 1132695.7848 | 2605140.9163 | 1132696.2534 | 2605147.4195 | 1132698.5488 | 2605153.33 | 1132700.8549 | 2605157.3788 | 1132701.5253 | 2605161.9749 | 1132701.3291 | 2605165.5625 | 1132701.1987 | 2605183.8176 | 1132698.7574 | 2605192.0544 | 1132699.4203 | 2605201.6699 | 1132699.2617 | 2605214.0254 | 1132699.8503 | 2605253.3071 | 1132703.7969 | 2605256.6704 | 1132704.8781 | 2605258.4551 | 1132706.4915 | 2605259.8462 | 1132709.1162 | 2605260.5133 | 1132712.2183 | 2605257.7967 | 1132728.9998
2 | 2605322.1404 | 1132781.7387 | 2605313.8757 | 1132786.6784 | 2605306.4295 | 1132797.7773 | 2605291.3291 | 1132820.2529 | 2605273.7869 | 1132844.494 | 2605273.3669 | 1132849.4516 | 2605277.4759 | 1132851.6785 | 2605284.0841 | 1132847.9824 | 2605303.5056 | 1132840.5845 | 2605316.3145 | 1132832.7807 | 2605325.4017 | 1132829.0868 | 2605332.0079 | 1132827.8586 | 2605339.8525 | 1132827.8655 | 2605345.6539 | 1132831.4056 | 2605359.2704 | 1132842.1227 | 2605369.5746 | 1132846.4116 | 2605376.5954 | 1132846.4178 | 2605383.6188 | 1132843.5448 | 2605387.3326 | 1132839.8351 | 2605394.3679 | 1132823.3777 | 2605400.1552 | 1132816.8019 | 2605405.115 | 1132814.3384 | 2605411.7202 | 1132814.3442 | 2605417.1044 | 1132819.5293 | 2605419.5774 | 1132826.1236 | 2605421.8535 | 1132829.0159 | 2605424.9468 | 1132830.6528 | 2605430.742 | 1132832.4699 | 2605435.9539 | 1132832.2411 | 2605441.444 | 1132830.8342 | 2605458.7941 | 1132824.2575 | 2605467.8468 | 1132824.8214 | 2605476.7189 | 1132829.3538 | 2605484.3577 | 1132835.5303 | 2605504.6268 | 1132853.2016 | 2605513.6879 | 1132861.3581 | 2605516.155 | 1132865.8848 | 2605514.9111 | 1132870.8305 | 2605504.1724 | 1132879.0471 | 2605501.2948 | 1132885.8811 | 2605503.8391 | 1132890.141 | 2605510.0796 | 1132893.1148 | 2605519.0017 | 1132893.2673 | 2605524.6606 | 1132892.4609 | 2605531.411 | 1132893.4787 | 2605546.274 | 1132895.96 | 2605554.9517 | 1132893.9113 | 2605563.624 | 1132889.3948 | 2605581.8096 | 1132878.2948 | 2605587.1801 | 1132872.9527 | 2605594.2077 | 1132865.5444 | 2605604.1313 | 1132856.5046 | 2605616.9414 | 1132847.8677 | 2605629.3324 | 1132842.9434 | 2605641.3132 | 1132840.4755 | 2605651.2239 | 1132837.1941 | 2605666.9256 | 1132831.8616 | 2605696.661 | 1132826.9424 | 2605709.59 | 1132823.0415 | 2605718.5384 | 1132819.8149 | 2605736.729 | 1132812.1616 | 2605743.7545 | 1132807.2324 | 2605747.479 | 1132800.6549 | 2605752.0279 | 1132793.2445 | 2605755.1417 | 1132789.3789 | 2605763.5994 | 1132784.1954 | 2605772.9712 | 1132781.0806 | 2605776.7305 | 1132778.3717 | 2605778.0658 | 1132774.7489 | 2605781.7881 | 1132770.506 | 2605785.5037 | 1132765.1624 | 2605790.0491 | 1132761.6984 | 2605797.9042 | 1132758.7044 | 2605815.2522 | 1132755.0191 | 2605824.9788 | 1132751.2153 | 2605833.689 | 1132747.7553 | 2605843.8458 | 1132745.0192 | 2605852.4297 | 1132744.7606 | 2605859.4542 | 1132741.0656 | 2605865.65 | 1132734.4905 | 2605878.0591 | 1132719.2617 | 2605878.8864 | 1132715.5607 | 2605880.1306 | 1132710.6262 | 2605883.8565 | 1132702.8037 | 2605899.5638 | 1132684.2988 | 2605904.1079 | 1132682.2466
3 | 2604717.9726 | 1131604.3042 | 2604727.4392 | 1131629.6905 | 2604737.4859 | 1131641.6374 | 2604752.9002 | 1131662.4705 | 2604753.4979 | 1131686.0047 | 2604760.7017 | 1131709.8886 | 2604759.3007 | 1131729.2524 | 2604755.9805 | 1131731.362 | 2604749.9063 | 1131740.2394 | 2604747.1719 | 1131751.4538 | 2604754.6138 | 1131766.1112 | 2604808.1111 | 1131834.4639 | 2604826.3436 | 1131863.8926 | 2604837.6533 | 1131894.1607 | 2604865.4677 | 1132005.6703 | 2604878.0454 | 1132028.6914 | 2604891.5332 | 1132049.668 | 2604897.4422 | 1132054.8196 | 2604906.8287 | 1132063.0089 | 2604958.9737 | 1132084.5614 | 2604963.5233 | 1132075.883 | 2604970.4012 | 1132072.8427 | 2604984.4405 | 1132077.8343 | 2604995.1209 | 1132075.9865 | 2605035.3211 | 1132063.6579 | 2605043.0807 | 1132065.0761 | 2605048.5891 | 1132070.3387 | 2605078.3629 | 1132106.4809 | 2605083.5125 | 1132117.1348 | 2605079.1198 | 1132159.2628 | 2605079.5842 | 1132174.8263 | 2605093.1696 | 1132216.1243 | 2605094.8559 | 1132234.4124 | 2605092.1916 | 1132253.4417 | 2605088.0293 | 1132268.5345 | 2605080.8332 | 1132284.1472 | 2605074.3698 | 1132298.1709 | 2605070.5252 | 1132310.9072 | 2605062.4633 | 1132377.4218 | 2605041.9581 | 1132484.0679 | 2605035.8021 | 1132536.6328 | 2605038.4987 | 1132571.4742 | 2605052.1246 | 1132600.2772 | 2605060.1056 | 1132612.5342 | 2605073.6097 | 1132620.716 | 2605081.7676 | 1132623.8132 | 2605086.6737 | 1132621.2494 | 2605107.7241 | 1132599.712 | 2605121.5815 | 1132590.5191 | 2605156.7515 | 1132578.0425
4 | 2605904.1079 | 1132682.2466 | 2605896.849 | 1132665.4536 | 2605898.5203 | 1132640.7543 | 2605896.4822 | 1132614.8175
5 | 2605904.1079 | 1132682.2466 | 2605909.0669 | 1132681.0063 | 2605914.0709 | 1132680.9778 | 2605923.0362 | 1132684.466 | 2605930.1056 | 1132690.1867 | 2605935.9211 | 1132694.8724 | 2605943.3168 | 1132705.3292 | 2605949.1075 | 1132719.5862 | 2605951.1547 | 1132736.0517 | 2605951.5475 | 1132759.5191 | 2605953.9907 | 1132772.4389 | 2605958.7805 | 1132786.193
6 | 2604717.9726 | 1131604.3042 | 2604725.688 | 1131604.0433 | 2604734.1532 | 1131600.1368 | 2604741.5974 | 1131592.1165 | 2604762.2745 | 1131558.5828 | 2604767.6448 | 1131554.0515 | 2604774.668 | 1131553.0342 | 2604794.7012 | 1131555.5177
7 | 2604717.9726 | 1131604.3042 | 2604727.4392 | 1131629.6905 | 2604737.4859 | 1131641.6374 | 2604752.9002 | 1131662.4705 | 2604753.4979 | 1131686.0047 | 2604760.7017 | 1131709.8886 | 2604759.3007 | 1131729.2524 | 2604755.9805 | 1131731.362 | 2604749.9063 | 1131740.2394 | 2604747.1719 | 1131751.4538 | 2604754.6138 | 1131766.1112 | 2604808.1111 | 1131834.4639 | 2604826.3436 | 1131863.8926 | 2604837.6533 | 1131894.1607 | 2604865.4677 | 1132005.6703 | 2604878.0454 | 1132028.6914 | 2604891.5332 | 1132049.668 | 2604897.4422 | 1132054.8196 | 2604901.057 | 1132088.5056 | 2604895.4479 | 1132112.8463 | 2604904.5387 | 1132124.9372 | 2604917.1066 | 1132140.4548 | 2604919.7702 | 1132150.4507 | 2604908.5447 | 1132160.3354 | 2604898.498 | 1132178.7141 | 2604896.4187 | 1132198.6332 | 2604902.2201 | 1132222.5161 | 2604898.5107 | 1132239.8661 | 2604843.1646 | 1132344.2062 | 2604836.4155 | 1132369.7688 | 2604806.5 | 1132376.7376 | 2604796.2075 | 1132375.629 | 2604771.0266 | 1132382.8684 | 2604756.4844 | 1132391.6169 | 2604745.6961 | 1132394.4988 | 2604718.1332 | 1132405.8386 | 2604716.7244 | 1132405.7042 | 2604712.7474 | 1132391.472 | 2604710.769 | 1132391.2259 | 2604686.2785 | 1132411.9728 | 2604684.754 | 1132412.1717 | 2604683.908 | 1132411.0372 | 2604674.047 | 1132369.0648 | 2604675.5155 | 1132351.4684
8 | 2604717.9726 | 1131604.3042 | 2604711.9791 | 1131588.2362 | 2604679.9246 | 1131537.7315 | 2604669.9221 | 1131528.0636 | 2604650.4006 | 1131520.7341 | 2604644.507 | 1131514.6823 | 2604642.8755 | 1131503.2866
9 | 2605979.7872 | 1132891.0996 | 2605974.6346 | 1132885.7919 | 2605973.0675 | 1132882.3665 | 2605965.1109 | 1132823.7413 | 2605965.1086 | 1132810.3237 | 2605962.251 | 1132796.1585 | 2605958.7805 | 1132786.193
10 | 2604675.5155 | 1132351.4684 | 2604659.7545 | 1132333.1031 | 2604608.9402 | 1132273.5802 | 2604598.5858 | 1132262.3558 | 2604575.5993 | 1132238.049 | 2604552.7396 | 1132198.2794 | 2604538.8302 | 1132184.0288 | 2604526.6562 | 1132176.0159 | 2604490.6722 | 1132152.6781 | 2604391.9219 | 1132057.427 | 2604379.8923 | 1132051.3599 | 2604358.7607 | 1132047.3095 | 2604338.9449 | 1132044.3052 | 2604297.2654 | 1132027.0675 | 2604256.0171 | 1132009.4079 | 2604206.9347 | 1131996.9792 | 2604167.8115 | 1131978.4991 | 2604142.3115 | 1131966.7206 | 2604092.8498 | 1131956.4157 | 2604054.1614 | 1131943.1726 | 2604041.7335 | 1131933.1039 | 2604025.3051 | 1131906.3913 | 2604022.7608 | 1131888.114
11 | 2604675.5155 | 1132351.4684 | 2604660.1316 | 1132363.6627 | 2604646.8346 | 1132375.1582 | 2604638.8587 | 1132385.2348 | 2604635.5345 | 1132393.1917
12 | 2604730.0742 | 1132325.9201 | 2604700.4337 | 1132345.5624 | 2604675.5155 | 1132351.4684
13 | 2604022.7608 | 1131888.114 | 2604023.317 | 1131873.5851 | 2604024.9537 | 1131866.794 | 2604029.7943 | 1131858.7155 | 2604043.3401 | 1131843.428 | 2604059.8193 | 1131828.4761 | 2604080.1779 | 1131815.3387 | 2604094.927 | 1131808.7342 | 2604113.5556 | 1131803.8442 | 2604119.5086 | 1131801.9584 | 2604125.4622 | 1131799.2166 | 2604156.8551 | 1131785.4756
14 | 2604635.5345 | 1132393.1917 | 2604631.3519 | 1132395.9232 | 2604625.0378 | 1132397.3191 | 2604606.6329 | 1132393.4256 | 2604598.373 | 1132392.0743
15 | 2604642.8755 | 1131503.2866 | 2604631.0318 | 1131494.6512 | 2604617.1957 | 1131493.6292 | 2604568.3459 | 1131495.1823 | 2604558.2789 | 1131498.3163
16 | 2604546.0013 | 1131502.1385 | 2604558.2789 | 1131498.3163
17 | 2604590.7432 | 1132392.4466 | 2604598.373 | 1132392.0743
18 | 2604584.1088 | 1132420.6442 | 2604583.0376 | 1132391.2291 | 2604590.7432 | 1132392.4466
19 | 2604584.1088 | 1132420.6442 | 2604585.4403 | 1132431.5394 | 2604581.5087 | 1132448.8226 | 2604586.0406 | 1132462.6216 | 2604598.9974 | 1132473.192 | 2604607.0455 | 1132482.6977
20 | 2604612.6163 | 1132489.2773 | 2604607.0455 | 1132482.6977
21 | 2605979.7872 | 1132891.0996 | 2605968.3253 | 1132890.3991 | 2605955.9467 | 1132882.3498 | 2605945.6326 | 1132872.8796 | 2605926.6579 | 1132855.575 | 2605920.8861 | 1132845.6868 | 2605911.8157 | 1132831.6823 | 2605897.3707 | 1132818.9066 | 2605884.9909 | 1132811.8912 | 2605866.8183 | 1132808.5833 | 2605851.1802 | 1132806.7979
22 | 2604525.4523 | 1131510.9302 | 2604541.6285 | 1131503.4998 | 2604546.0013 | 1131502.1385

## bus_geodata
| x | y | coords
0 | 2605257.7967 | 1132728.9998
1 | 2605322.1404 | 1132781.7387
2 | 2605156.7515 | 1132578.0425
3 | 2605904.1079 | 1132682.2466
4 | 2604717.9726 | 1131604.3042
5 | 2605896.4822 | 1132614.8175
6 | 2605958.7805 | 1132786.193
7 | 2604675.5155 | 1132351.4684
8 | 2604022.7608 | 1131888.114
9 | 2604635.5345 | 1132393.1917
10 | 2604730.0742 | 1132325.9201
11 | 2604642.8755 | 1131503.2866
12 | 2604558.2789 | 1131498.3163
13 | 2604794.7012 | 1131555.5177
14 | 2604598.373 | 1132392.0743
15 | 2604590.7432 | 1132392.4466
16 | 2604584.1088 | 1132420.6442
17 | 2604607.0455 | 1132482.6977
18 | 2605979.7872 | 1132891.0996
19 | 2604156.8551 | 1131785.4756
20 | 2604546.0013 | 1131502.1385
21 | 2604612.6163 | 1132489.2773
22 | 2604525.4523 | 1131510.9302
23 | 2605851.1802 | 1132806.7979
24 | 2604730.0742 | 1132325.9201

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1