## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6266-190_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6266-190_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6266-190_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6266-190_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6266-190_0_6_node_21 | 0.4 | n |  | TRUE
5 | bus_LV_6266-190_0_6_node_27 | 0.4 | n |  | TRUE
6 | bus_LV_6266-190_0_6_node_43 | 0.4 | n |  | TRUE
7 | bus_LV_6266-190_0_6_node_89 | 0.4 | n |  | TRUE
8 | bus_LV_6266-190_0_6_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_6266-190_0_6_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_6266-190_0_6_node_44 | 0.4 | n |  | TRUE
11 | bus_LV_6266-190_0_6_node_4 | 0.4 | n |  | TRUE
12 | bus_LV_6266-190_0_6_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_6266-190_0_6_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_6266-190_0_6_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_6266-190_0_6_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_6266-190_0_6_node_58 | 0.4 | n |  | TRUE
17 | bus_LV_6266-190_0_6_node_50 | 0.4 | n |  | TRUE
18 | bus_LV_6266-190_0_6_node_51 | 0.4 | n |  | TRUE
19 | bus_LV_6266-190_0_6_node_49 | 0.4 | n |  | TRUE
20 | bus_LV_6266-190_0_6_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_6266-190_0_6_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_6266-190_0_6_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_6266-190_0_6_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_6266-190_0_6_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_6266-190_0_6_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_6266-190_0_6_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_6266-190_0_6_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_6266-190_0_6_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_6266-190_0_6_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_6266-190_0_6_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_6266-190_0_6_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_6266-190_0_6_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_6266-190_0_6_node_57 | 0.4 | n |  | TRUE
34 | bus_LV_6266-190_0_6_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_6266-190_0_6_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_6266-190_0_6_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_6266-190_0_6_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_6266-190_0_6_node_54 | 0.4 | n |  | TRUE
39 | bus_LV_6266-190_0_6_node_56 | 0.4 | n |  | TRUE
40 | bus_LV_6266-190_0_6_node_53 | 0.4 | n |  | TRUE
41 | bus_LV_6266-190_0_6_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_6266-190_0_6_node_31 | 0.4 | n |  | TRUE
43 | bus_LV_6266-190_0_6_node_32 | 0.4 | n |  | TRUE
44 | bus_LV_6266-190_0_6_node_55 | 0.4 | n |  | TRUE
45 | bus_LV_6266-190_0_6_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_6266-190_0_6_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_6266-190_0_6_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_6266-190_0_6_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_6266-190_0_6_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_6266-190_0_6_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_6266-190_0_6_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_6266-190_0_6_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_6266-190_0_6_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_6266-190_0_6_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_6266-190_0_6_node_52 | 0.4 | n |  | TRUE
56 | bus_LV_6266-190_0_6_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_6266-190_0_6_node_46 | 0.4 | n |  | TRUE
58 | bus_MV_96_0_node_127 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6266-190_0_6_load_0 | 0 | 0.0091444 | 0.0022918 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6266-190_0_6_load_3 | 3 | 0.013346 | 0.0033449 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6266-190_0_6_load_27 | 5 | 0.009452 | 0.0023689 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6266-190_0_6_load_43 | 6 | 0.017377 | 0.004355 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6266-190_0_6_load_89 | 7 | 0.015256 | 0.0038236 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6266-190_0_6_load_19 | 8 | 0.0096767 | 0.0024252 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6266-190_0_6_load_28 | 9 | 0.010989 | 0.002754 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6266-190_0_6_load_44 | 10 | 0.0057487 | 0.0014408 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6266-190_0_6_load_4 | 11 | 0.0038434 | 0.00096325 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6266-190_0_6_load_6 | 13 | 0.0028504 | 0.00071439 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6266-190_0_6_load_7 | 14 | 0.0042124 | 0.0010557 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6266-190_0_6_load_8 | 15 | 0.006977 | 0.0017486 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6266-190_0_6_load_58 | 16 | 0.0041419 | 0.0010381 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6266-190_0_6_load_51 | 18 | 0.0067687 | 0.0016964 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6266-190_0_6_load_49 | 19 | 0.0050081 | 0.0012551 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6266-190_0_6_load_9 | 20 | 0.0079088 | 0.0019821 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6266-190_0_6_load_11 | 22 | 0.013259 | 0.003323 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6266-190_0_6_load_12 | 23 | 0.011215 | 0.0028107 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6266-190_0_6_load_13 | 24 | 0.005446 | 0.0013649 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6266-190_0_6_load_16 | 25 | 0.0085028 | 0.002131 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6266-190_0_6_load_17 | 27 | 0.010502 | 0.0026319 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6266-190_0_6_load_18 | 29 | 0.010071 | 0.0025241 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6266-190_0_6_load_20 | 30 | 0.010946 | 0.0027434 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6266-190_0_6_load_22 | 31 | 0.0054422 | 0.0013639 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6266-190_0_6_load_30 | 32 | 0.0059181 | 0.0014832 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6266-190_0_6_load_57 | 33 | 0.0054084 | 0.0013555 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6266-190_0_6_load_23 | 34 | 0.015984 | 0.0040059 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6266-190_0_6_load_24 | 35 | 0.0070552 | 0.0017682 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6266-190_0_6_load_25 | 36 | 0.01547 | 0.0038772 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6266-190_0_6_load_56 | 39 | 0.0043168 | 0.0010819 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6266-190_0_6_load_29 | 41 | 0.013531 | 0.0033912 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6266-190_0_6_load_31 | 42 | 0.011069 | 0.0027741 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6266-190_0_6_load_55 | 44 | 0.015059 | 0.0037741 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6266-190_0_6_load_35 | 45 | 0.036244 | 0.0090836 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6266-190_0_6_load_36 | 46 | 0.012501 | 0.003133 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6266-190_0_6_load_33 | 47 | 0.012201 | 0.0030579 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6266-190_0_6_load_34 | 48 | 0.01061 | 0.0026591 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6266-190_0_6_load_37 | 49 | 0.0080031 | 0.0020058 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6266-190_0_6_load_38 | 50 | 0.0095459 | 0.0023924 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6266-190_0_6_load_39 | 51 | 0.0098072 | 0.0024579 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6266-190_0_6_load_40 | 52 | 0.0087657 | 0.0021969 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6266-190_0_6_load_41 | 53 | 0.013573 | 0.0034017 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6266-190_0_6_load_42 | 54 | 0.0047741 | 0.0011965 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6266-190_0_6_load_52 | 55 | 0.020231 | 0.0050705 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6266-190_0_6_load_46 | 57 | 0.0051419 | 0.0012887 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 43 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6266-190_0_6_line_0 |  | 0 | 1 | 0.020568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6266-190_0_6_line_1 |  | 1 | 2 | 0.02923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6266-190_0_6_line_2 |  | 1 | 3 | 0.0084669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6266-190_0_6_line_3 |  | 2 | 4 | 0.05923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_6266-190_0_6_line_4 |  | 2 | 5 | 0.018658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_6266-190_0_6_line_5 |  | 3 | 6 | 0.026158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6266-190_0_6_line_6 |  | 4 | 7 | 0.042873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6266-190_0_6_line_7 |  | 4 | 8 | 0.015849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_6266-190_0_6_line_8 |  | 5 | 9 | 0.0056595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_6266-190_0_6_line_9 |  | 6 | 10 | 0.017943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6266-190_0_6_line_10 |  | 7 | 28 | 0.028409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6266-190_0_6_line_11 |  | 8 | 29 | 0.035415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_6266-190_0_6_line_12 |  | 9 | 41 | 0.035361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_6266-190_0_6_line_13 |  | 10 | 56 | 0.00024266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6266-190_0_6_line_14 |  | 11 | 12 | 0.03817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6266-190_0_6_line_15 |  | 11 | 13 | 0.013771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6266-190_0_6_line_16 |  | 12 | 14 | 0.012471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6266-190_0_6_line_17 |  | 12 | 15 | 0.0094372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6266-190_0_6_line_18 |  | 14 | 16 | 0.026483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6266-190_0_6_line_19 |  | 15 | 17 | 0.035324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6266-190_0_6_line_20 |  | 17 | 18 | 0.026872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6266-190_0_6_line_21 |  | 17 | 19 | 0.036914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6266-190_0_6_line_22 |  | 18 | 55 | 0.027977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6266-190_0_6_line_23 |  | 20 | 21 | 0.065111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6266-190_0_6_line_24 |  | 21 | 22 | 0.0094828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6266-190_0_6_line_25 |  | 21 | 23 | 0.025223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6266-190_0_6_line_26 |  | 22 | 24 | 0.024789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6266-190_0_6_line_27 |  | 23 | 25 | 0.00042587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6266-190_0_6_line_28 |  | 24 | 26 | 0.017684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6266-190_0_6_line_29 |  | 25 | 27 | 0.0037869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6266-190_0_6_line_30 |  | 26 | 28 | 0.010927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6266-190_0_6_line_31 |  | 29 | 30 | 0.01331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_6266-190_0_6_line_32 |  | 30 | 31 | 0.0074487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_6266-190_0_6_line_33 |  | 31 | 32 | 0.018747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_6266-190_0_6_line_34 |  | 32 | 33 | 0.017015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_6266-190_0_6_line_35 |  | 33 | 44 | 0.052393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_6266-190_0_6_line_36 |  | 34 | 35 | 0.049453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6266-190_0_6_line_37 |  | 34 | 36 | 0.041839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6266-190_0_6_line_38 |  | 36 | 37 | 0.013546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6266-190_0_6_line_39 |  | 37 | 38 | 0.035713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6266-190_0_6_line_40 |  | 38 | 39 | 0.02044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_6266-190_0_6_line_41 |  | 38 | 40 | 0.026274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_6266-190_0_6_line_42 |  | 39 | 44 | 0.0059915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_6266-190_0_6_line_43 |  | 40 | 55 | 0.062251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_6266-190_0_6_line_44 |  | 40 | 52 | 0.018555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6266-190_0_6_line_45 |  | 41 | 42 | 0.0018657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_6266-190_0_6_line_46 |  | 42 | 43 | 0.013811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_6266-190_0_6_line_47 |  | 43 | 45 | 0.02112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6266-190_0_6_line_48 |  | 43 | 46 | 0.019735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6266-190_0_6_line_49 |  | 43 | 47 | 0.03608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6266-190_0_6_line_50 |  | 47 | 48 | 0.0042528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6266-190_0_6_line_51 |  | 49 | 50 | 0.02794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6266-190_0_6_line_52 |  | 49 | 51 | 0.031261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6266-190_0_6_line_53 |  | 50 | 52 | 0.013802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6266-190_0_6_line_54 |  | 51 | 53 | 0.012872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6266-190_0_6_line_55 |  | 53 | 54 | 0.047631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6266-190_0_6_line_56 |  | 56 | 57 | 0.025043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6266-190_0_6_trafo_32 | 0.63 MVA 20/0.4 kV | 58 | 43 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2598061.7397 | 1121872.2102 | 2598066.1402 | 1121852.1186
1 | 2598033.179 | 1121865.6165 | 2598061.7397 | 1121872.2102
2 | 2598061.7397 | 1121872.2102 | 2598069.9901 | 1121874.1127
3 | 2597975.3016 | 1121852.2742 | 2598033.179 | 1121865.6165
4 | 2598033.179 | 1121865.6165 | 2598029.4451 | 1121883.897
5 | 2598095.4791 | 1121879.9905 | 2598069.9901 | 1121874.1127
6 | 2597975.3016 | 1121852.2742 | 2597933.3931 | 1121843.2293
7 | 2597975.3016 | 1121852.2742 | 2597974.2878 | 1121868.0909
8 | 2598029.4451 | 1121883.897 | 2598028.3125 | 1121889.442
9 | 2598095.4791 | 1121879.9905 | 2598112.9632 | 1121884.0224
10 | 2597905.6235 | 1121837.2359 | 2597933.3931 | 1121843.2293
11 | 2597972.985 | 1121903.4711 | 2597973.2765 | 1121883.8681 | 2597974.2878 | 1121868.0909
12 | 2598020.7 | 1121923.9716 | 2598026.2032 | 1121899.7689 | 2598028.3125 | 1121889.442
13 | 2598112.9632 | 1121884.0224 | 2598113.1996 | 1121884.0769
14 | 2598137.9827 | 1122015.9667 | 2598154.1653 | 1122000.3428 | 2598157.912 | 1121995.9283 | 2598151.4997 | 1121988.4049
15 | 2598142.5669 | 1121977.9244 | 2598151.4997 | 1121988.4049
16 | 2598137.9827 | 1122015.9667 | 2598131.1625 | 1122007.4758 | 2598130.1071 | 1122006.3003
17 | 2598137.9827 | 1122015.9667 | 2598134.6732 | 1122024.8046
18 | 2598112.4154 | 1121986.5939 | 2598130.1071 | 1122006.3003
19 | 2598123.621 | 1122058.3475 | 2598132.1959 | 1122031.4205 | 2598134.6732 | 1122024.8046
20 | 2598123.621 | 1122058.3475 | 2598097.3891 | 1122052.5187
21 | 2598123.621 | 1122058.3475 | 2598159.3847 | 1122067.491
22 | 2598070.0016 | 1122046.827 | 2598081.009 | 1122048.879 | 2598097.3891 | 1122052.5187
23 | 2597887.6286 | 1121895.5153 | 2597857.6023 | 1121888.256 | 2597824.3319 | 1121880.2506
24 | 2597887.6286 | 1121895.5153 | 2597889.5537 | 1121886.2299
25 | 2597887.6286 | 1121895.5153 | 2597883.7915 | 1121920.4451
26 | 2597894.5861 | 1121861.9575 | 2597889.5537 | 1121886.2299
27 | 2597883.7915 | 1121920.4451 | 2597883.7267 | 1121920.8661
28 | 2597898.1761 | 1121844.6422 | 2597894.5861 | 1121861.9575
29 | 2597883.1506 | 1121924.6089 | 2597883.7267 | 1121920.8661
30 | 2597905.6235 | 1121837.2359 | 2597904.0745 | 1121840.5381 | 2597901.4841 | 1121843.1069 | 2597898.1761 | 1121844.6422
31 | 2597972.7871 | 1121916.7799 | 2597972.985 | 1121903.4711
32 | 2597972.7871 | 1121916.7799 | 2597972.7791 | 1121917.318 | 2597972.7193 | 1121924.2283
33 | 2597972.7193 | 1121924.2283 | 2597972.5571 | 1121942.9748
34 | 2597972.668 | 1121959.9849 | 2597972.4528 | 1121955.0254 | 2597972.5571 | 1121942.9748
35 | 2597979.9452 | 1122010.2763 | 2597973.4852 | 1121996.2897 | 2597971.6098 | 1121992.444 | 2597973.6734 | 1121983.161 | 2597972.668 | 1121959.9849
36 | 2597897.7118 | 1122003.6473 | 2597849.5677 | 1121992.3459
37 | 2597938.1534 | 1122014.0546 | 2597936.2956 | 1122012.9997 | 2597917.7387 | 1122008.3485 | 2597897.7118 | 1122003.6473
38 | 2597949.9333 | 1122020.7431 | 2597938.1534 | 1122014.0546
39 | 2597949.9333 | 1122020.7431 | 2597969.1938 | 1122030.8414 | 2597982.4524 | 1122035.4946
40 | 2597982.4524 | 1122035.4946 | 2597984.908 | 1122022.2651 | 2597982.2551 | 1122015.8039
41 | 2598008.8045 | 1122035.4188 | 2597982.4524 | 1122035.4946
42 | 2597979.9452 | 1122010.2763 | 2597980.3078 | 1122011.0612 | 2597982.2551 | 1122015.8039
43 | 2598008.8045 | 1122035.4188 | 2598070.0016 | 1122046.827
44 | 2598008.8045 | 1122035.4188 | 2598022.7977 | 1122023.2333
45 | 2598020.7 | 1121923.9716 | 2598020.2863 | 1121925.7909
46 | 2598017.2242 | 1121939.2579 | 2598020.2863 | 1121925.7909
47 | 2598017.2242 | 1121939.2579 | 2598037.5015 | 1121945.3651
48 | 2598017.2242 | 1121939.2579 | 2597998.1403 | 1121934.2295
49 | 2598017.2242 | 1121939.2579 | 2598013.7911 | 1121958.524 | 2598010.2272 | 1121974.6454
50 | 2598010.2272 | 1121974.6454 | 2598009.3093 | 1121978.7979
51 | 2598054.4651 | 1121996.0747 | 2598052.7735 | 1121997.1297 | 2598033.2061 | 1122014.1694
52 | 2598054.4651 | 1121996.0747 | 2598066.3979 | 1121988.6322 | 2598080.9333 | 1121979.4404
53 | 2598033.2061 | 1122014.1694 | 2598022.7977 | 1122023.2333
54 | 2598091.8126 | 1121972.5606 | 2598080.9333 | 1121979.4404
55 | 2598091.8126 | 1121972.5606 | 2598116.6474 | 1121956.8558 | 2598131.8554 | 1121946.7722
56 | 2598113.1996 | 1121884.0769 | 2598137.6029 | 1121889.7018

## bus_geodata
| x | y | coords
0 | 2598066.1402 | 1121852.1186
1 | 2598061.7397 | 1121872.2102
2 | 2598033.179 | 1121865.6165
3 | 2598069.9901 | 1121874.1127
4 | 2597975.3016 | 1121852.2742
5 | 2598029.4451 | 1121883.897
6 | 2598095.4791 | 1121879.9905
7 | 2597933.3931 | 1121843.2293
8 | 2597974.2878 | 1121868.0909
9 | 2598028.3125 | 1121889.442
10 | 2598112.9632 | 1121884.0224
11 | 2598151.4997 | 1121988.4049
12 | 2598137.9827 | 1122015.9667
13 | 2598142.5669 | 1121977.9244
14 | 2598130.1071 | 1122006.3003
15 | 2598134.6732 | 1122024.8046
16 | 2598112.4154 | 1121986.5939
17 | 2598123.621 | 1122058.3475
18 | 2598097.3891 | 1122052.5187
19 | 2598159.3847 | 1122067.491
20 | 2597824.3319 | 1121880.2506
21 | 2597887.6286 | 1121895.5153
22 | 2597889.5537 | 1121886.2299
23 | 2597883.7915 | 1121920.4451
24 | 2597894.5861 | 1121861.9575
25 | 2597883.7267 | 1121920.8661
26 | 2597898.1761 | 1121844.6422
27 | 2597883.1506 | 1121924.6089
28 | 2597905.6235 | 1121837.2359
29 | 2597972.985 | 1121903.4711
30 | 2597972.7871 | 1121916.7799
31 | 2597972.7193 | 1121924.2283
32 | 2597972.5571 | 1121942.9748
33 | 2597972.668 | 1121959.9849
34 | 2597897.7118 | 1122003.6473
35 | 2597849.5677 | 1121992.3459
36 | 2597938.1534 | 1122014.0546
37 | 2597949.9333 | 1122020.7431
38 | 2597982.4524 | 1122035.4946
39 | 2597982.2551 | 1122015.8039
40 | 2598008.8045 | 1122035.4188
41 | 2598020.7 | 1121923.9716
42 | 2598020.2863 | 1121925.7909
43 | 2598017.2242 | 1121939.2579
44 | 2597979.9452 | 1122010.2763
45 | 2598037.5015 | 1121945.3651
46 | 2597998.1403 | 1121934.2295
47 | 2598010.2272 | 1121974.6454
48 | 2598009.3093 | 1121978.7979
49 | 2598054.4651 | 1121996.0747
50 | 2598033.2061 | 1122014.1694
51 | 2598080.9333 | 1121979.4404
52 | 2598022.7977 | 1122023.2333
53 | 2598091.8126 | 1121972.5606
54 | 2598131.8554 | 1121946.7722
55 | 2598070.0016 | 1122046.827
56 | 2598113.1996 | 1121884.0769
57 | 2598137.6029 | 1121889.7018
58 | 2597997.2942 | 1121934.0066

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1