## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6266-196_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6266-196_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6266-196_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6266-196_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6266-196_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6266-196_0_4_node_51 | 0.4 | n |  | TRUE
6 | bus_LV_6266-196_0_4_node_49 | 0.4 | n |  | TRUE
7 | bus_LV_6266-196_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_6266-196_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_6266-196_0_4_node_52 | 0.4 | n |  | TRUE
10 | bus_LV_6266-196_0_4_node_145 | 0.4 | n |  | TRUE
11 | bus_LV_6266-196_0_4_node_144 | 0.4 | n |  | TRUE
12 | bus_LV_6266-196_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_6266-196_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_6266-196_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_6266-196_0_4_node_104 | 0.4 | n |  | TRUE
16 | bus_LV_6266-196_0_4_node_102 | 0.4 | n |  | TRUE
17 | bus_LV_6266-196_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_6266-196_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_6266-196_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_6266-196_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_6266-196_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_6266-196_0_4_node_95 | 0.4 | n |  | TRUE
23 | bus_LV_6266-196_0_4_node_96 | 0.4 | n |  | TRUE
24 | bus_LV_6266-196_0_4_node_60 | 0.4 | n |  | TRUE
25 | bus_LV_6266-196_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_6266-196_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_6266-196_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_6266-196_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_6266-196_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_6266-196_0_4_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_6266-196_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_6266-196_0_4_node_137 | 0.4 | n |  | TRUE
33 | bus_LV_6266-196_0_4_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_6266-196_0_4_node_73 | 0.4 | n |  | TRUE
35 | bus_LV_6266-196_0_4_node_71 | 0.4 | n |  | TRUE
36 | bus_LV_6266-196_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_6266-196_0_4_node_63 | 0.4 | n |  | TRUE
38 | bus_LV_6266-196_0_4_node_136 | 0.4 | n |  | TRUE
39 | bus_LV_6266-196_0_4_node_134 | 0.4 | n |  | TRUE
40 | bus_LV_6266-196_0_4_node_69 | 0.4 | n |  | TRUE
41 | bus_LV_6266-196_0_4_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_6266-196_0_4_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_6266-196_0_4_node_64 | 0.4 | n |  | TRUE
44 | bus_LV_6266-196_0_4_node_23 | 0.4 | n |  | TRUE
45 | bus_LV_6266-196_0_4_node_25 | 0.4 | n |  | TRUE
46 | bus_LV_6266-196_0_4_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_6266-196_0_4_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_6266-196_0_4_node_55 | 0.4 | n |  | TRUE
49 | bus_LV_6266-196_0_4_node_30 | 0.4 | n |  | TRUE
50 | bus_LV_6266-196_0_4_node_28 | 0.4 | n |  | TRUE
51 | bus_LV_6266-196_0_4_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_6266-196_0_4_node_56 | 0.4 | n |  | TRUE
53 | bus_LV_6266-196_0_4_node_33 | 0.4 | n |  | TRUE
54 | bus_LV_6266-196_0_4_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_6266-196_0_4_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_6266-196_0_4_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_6266-196_0_4_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_6266-196_0_4_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_6266-196_0_4_node_153 | 0.4 | n |  | TRUE
60 | bus_LV_6266-196_0_4_node_58 | 0.4 | n |  | TRUE
61 | bus_LV_6266-196_0_4_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_6266-196_0_4_node_54 | 0.4 | n |  | TRUE
63 | bus_LV_6266-196_0_4_node_59 | 0.4 | n |  | TRUE
64 | bus_LV_6266-196_0_4_node_57 | 0.4 | n |  | TRUE
65 | bus_LV_6266-196_0_4_node_42 | 0.4 | n |  | TRUE
66 | bus_LV_6266-196_0_4_node_39 | 0.4 | n |  | TRUE
67 | bus_LV_6266-196_0_4_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_6266-196_0_4_node_41 | 0.4 | n |  | TRUE
69 | bus_LV_6266-196_0_4_node_43 | 0.4 | n |  | TRUE
70 | bus_LV_6266-196_0_4_node_44 | 0.4 | n |  | TRUE
71 | bus_LV_6266-196_0_4_node_45 | 0.4 | n |  | TRUE
72 | bus_LV_6266-196_0_4_node_155 | 0.4 | n |  | TRUE
73 | bus_LV_6266-196_0_4_node_147 | 0.4 | n |  | TRUE
74 | bus_LV_6266-196_0_4_node_46 | 0.4 | n |  | TRUE
75 | bus_LV_6266-196_0_4_node_148 | 0.4 | n |  | TRUE
76 | bus_LV_6266-196_0_4_node_146 | 0.4 | n |  | TRUE
77 | bus_LV_6266-196_0_4_node_154 | 0.4 | n |  | TRUE
78 | bus_LV_6266-196_0_4_node_47 | 0.4 | n |  | TRUE
79 | bus_LV_6266-196_0_4_node_48 | 0.4 | n |  | TRUE
80 | bus_LV_6266-196_0_4_node_50 | 0.4 | n |  | TRUE
81 | bus_LV_6266-196_0_4_node_61 | 0.4 | n |  | TRUE
82 | bus_LV_6266-196_0_4_node_62 | 0.4 | n |  | TRUE
83 | bus_LV_6266-196_0_4_node_94 | 0.4 | n |  | TRUE
84 | bus_LV_6266-196_0_4_node_92 | 0.4 | n |  | TRUE
85 | bus_LV_6266-196_0_4_node_90 | 0.4 | n |  | TRUE
86 | bus_LV_6266-196_0_4_node_65 | 0.4 | n |  | TRUE
87 | bus_LV_6266-196_0_4_node_66 | 0.4 | n |  | TRUE
88 | bus_LV_6266-196_0_4_node_67 | 0.4 | n |  | TRUE
89 | bus_LV_6266-196_0_4_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_6266-196_0_4_node_70 | 0.4 | n |  | TRUE
91 | bus_LV_6266-196_0_4_node_72 | 0.4 | n |  | TRUE
92 | bus_LV_6266-196_0_4_node_74 | 0.4 | n |  | TRUE
93 | bus_LV_6266-196_0_4_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_6266-196_0_4_node_132 | 0.4 | n |  | TRUE
95 | bus_LV_6266-196_0_4_node_76 | 0.4 | n |  | TRUE
96 | bus_LV_6266-196_0_4_node_77 | 0.4 | n |  | TRUE
97 | bus_LV_6266-196_0_4_node_78 | 0.4 | n |  | TRUE
98 | bus_LV_6266-196_0_4_node_80 | 0.4 | n |  | TRUE
99 | bus_LV_6266-196_0_4_node_79 | 0.4 | n |  | TRUE
100 | bus_LV_6266-196_0_4_node_81 | 0.4 | n |  | TRUE
101 | bus_LV_6266-196_0_4_node_82 | 0.4 | n |  | TRUE
102 | bus_LV_6266-196_0_4_node_97 | 0.4 | n |  | TRUE
103 | bus_LV_6266-196_0_4_node_83 | 0.4 | n |  | TRUE
104 | bus_LV_6266-196_0_4_node_84 | 0.4 | n |  | TRUE
105 | bus_LV_6266-196_0_4_node_125 | 0.4 | n |  | TRUE
106 | bus_LV_6266-196_0_4_node_98 | 0.4 | n |  | TRUE
107 | bus_LV_6266-196_0_4_node_117 | 0.4 | n |  | TRUE
108 | bus_LV_6266-196_0_4_node_118 | 0.4 | n |  | TRUE
109 | bus_LV_6266-196_0_4_node_119 | 0.4 | n |  | TRUE
110 | bus_LV_6266-196_0_4_node_120 | 0.4 | n |  | TRUE
111 | bus_LV_6266-196_0_4_node_121 | 0.4 | n |  | TRUE
112 | bus_LV_6266-196_0_4_node_123 | 0.4 | n |  | TRUE
113 | bus_LV_6266-196_0_4_node_124 | 0.4 | n |  | TRUE
114 | bus_LV_6266-196_0_4_node_127 | 0.4 | n |  | TRUE
115 | bus_LV_6266-196_0_4_node_149 | 0.4 | n |  | TRUE
116 | bus_LV_6266-196_0_4_node_139 | 0.4 | n |  | TRUE
117 | bus_LV_6266-196_0_4_node_122 | 0.4 | n |  | TRUE
118 | bus_LV_6266-196_0_4_node_150 | 0.4 | n |  | TRUE
119 | bus_LV_6266-196_0_4_node_151 | 0.4 | n |  | TRUE
120 | bus_LV_6266-196_0_4_node_126 | 0.4 | n |  | TRUE
121 | bus_LV_6266-196_0_4_node_128 | 0.4 | n |  | TRUE
122 | bus_LV_6266-196_0_4_node_85 | 0.4 | n |  | TRUE
123 | bus_LV_6266-196_0_4_node_86 | 0.4 | n |  | TRUE
124 | bus_LV_6266-196_0_4_node_87 | 0.4 | n |  | TRUE
125 | bus_LV_6266-196_0_4_node_88 | 0.4 | n |  | TRUE
126 | bus_LV_6266-196_0_4_node_89 | 0.4 | n |  | TRUE
127 | bus_LV_6266-196_0_4_node_107 | 0.4 | n |  | TRUE
128 | bus_LV_6266-196_0_4_node_115 | 0.4 | n |  | TRUE
129 | bus_LV_6266-196_0_4_node_116 | 0.4 | n |  | TRUE
130 | bus_LV_6266-196_0_4_node_108 | 0.4 | n |  | TRUE
131 | bus_LV_6266-196_0_4_node_114 | 0.4 | n |  | TRUE
132 | bus_LV_6266-196_0_4_node_91 | 0.4 | n |  | TRUE
133 | bus_LV_6266-196_0_4_node_93 | 0.4 | n |  | TRUE
134 | bus_LV_6266-196_0_4_node_106 | 0.4 | n |  | TRUE
135 | bus_LV_6266-196_0_4_node_103 | 0.4 | n |  | TRUE
136 | bus_LV_6266-196_0_4_node_99 | 0.4 | n |  | TRUE
137 | bus_LV_6266-196_0_4_node_100 | 0.4 | n |  | TRUE
138 | bus_LV_6266-196_0_4_node_101 | 0.4 | n |  | TRUE
139 | bus_LV_6266-196_0_4_node_105 | 0.4 | n |  | TRUE
140 | bus_LV_6266-196_0_4_node_109 | 0.4 | n |  | TRUE
141 | bus_LV_6266-196_0_4_node_110 | 0.4 | n |  | TRUE
142 | bus_LV_6266-196_0_4_node_111 | 0.4 | n |  | TRUE
143 | bus_LV_6266-196_0_4_node_112 | 0.4 | n |  | TRUE
144 | bus_LV_6266-196_0_4_node_129 | 0.4 | n |  | TRUE
145 | bus_LV_6266-196_0_4_node_130 | 0.4 | n |  | TRUE
146 | bus_LV_6266-196_0_4_node_141 | 0.4 | n |  | TRUE
147 | bus_LV_6266-196_0_4_node_142 | 0.4 | n |  | TRUE
148 | bus_LV_6266-196_0_4_node_143 | 0.4 | n |  | TRUE
149 | bus_LV_6266-196_0_4_node_131 | 0.4 | n |  | TRUE
150 | bus_LV_6266-196_0_4_node_133 | 0.4 | n |  | TRUE
151 | bus_LV_6266-196_0_4_node_135 | 0.4 | n |  | TRUE
152 | bus_LV_6266-196_0_4_node_138 | 0.4 | n |  | TRUE
153 | bus_MV_90_2_node_189 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6266-196_0_4_load_0 | 0 | 0.00075533 | 0.0001893 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6266-196_0_4_load_1 | 1 | 0.0017865 | 0.00044773 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6266-196_0_4_load_2 | 2 | 0.0016104 | 0.0004036 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6266-196_0_4_load_3 | 3 | 0.0011955 | 0.00029962 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6266-196_0_4_load_4 | 4 | 0.0010132 | 0.00025394 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6266-196_0_4_load_51 | 5 | 0.0060649 | 0.00152 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6266-196_0_4_load_49 | 6 | 0.0035245 | 0.00088332 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6266-196_0_4_load_5 | 7 | 0.0022008 | 0.00055158 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6266-196_0_4_load_6 | 8 | 0.0010243 | 0.00025672 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6266-196_0_4_load_52 | 9 | 0.0014544 | 0.00036452 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6266-196_0_4_load_145 | 10 | 0.0028036 | 0.00070264 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6266-196_0_4_load_7 | 12 | 0.0034072 | 0.00085393 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6266-196_0_4_load_9 | 14 | 0.0028382 | 0.00071131 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6266-196_0_4_load_104 | 15 | 0.004728 | 0.0011849 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6266-196_0_4_load_10 | 17 | 0.0040212 | 0.0010078 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6266-196_0_4_load_12 | 19 | 0.0033318 | 0.00083502 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6266-196_0_4_load_13 | 20 | 0.0018145 | 0.00045476 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6266-196_0_4_load_14 | 21 | 0.0031092 | 0.00077924 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6266-196_0_4_load_96 | 23 | 0.0017687 | 0.00044327 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6266-196_0_4_load_60 | 24 | 0.0038056 | 0.00095378 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6266-196_0_4_load_15 | 25 | 0.0020428 | 0.00051196 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6266-196_0_4_load_16 | 26 | 0.0020805 | 0.00052142 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6266-196_0_4_load_17 | 27 | 0.0059878 | 0.0015007 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6266-196_0_4_load_18 | 28 | 0.003852 | 0.0009654 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6266-196_0_4_load_137 | 32 | 0.0039233 | 0.00098326 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6266-196_0_4_load_73 | 34 | 0.0038355 | 0.00096128 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6266-196_0_4_load_71 | 35 | 0.0034062 | 0.00085368 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6266-196_0_4_load_63 | 37 | 0.0031376 | 0.00078637 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6266-196_0_4_load_136 | 38 | 0.0042656 | 0.0010691 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6266-196_0_4_load_134 | 39 | 0.003703 | 0.00092806 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6266-196_0_4_load_31 | 41 | 0.006522 | 0.0016346 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6266-196_0_4_load_24 | 42 | 0.0038975 | 0.0009768 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6266-196_0_4_load_64 | 43 | 0.0035252 | 0.0008835 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6266-196_0_4_load_23 | 44 | 0.0022952 | 0.00057524 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6266-196_0_4_load_27 | 46 | 0.003134 | 0.00078546 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6266-196_0_4_load_55 | 48 | 0.0030459 | 0.00076338 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6266-196_0_4_load_30 | 49 | 0.0031103 | 0.00077952 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6266-196_0_4_load_28 | 50 | 0.0033548 | 0.00084079 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6266-196_0_4_load_32 | 51 | 0.0032708 | 0.00081975 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6266-196_0_4_load_56 | 52 | 0.0054582 | 0.001368 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6266-196_0_4_load_33 | 53 | 0.0022294 | 0.00055874 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6266-196_0_4_load_34 | 54 | 0.0020983 | 0.00052588 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6266-196_0_4_load_35 | 55 | 0.0023316 | 0.00058435 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6266-196_0_4_load_153 | 59 | 0.0034001 | 0.00085214 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6266-196_0_4_load_54 | 62 | 0.0014931 | 0.00037421 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6266-196_0_4_load_59 | 63 | 0.0020065 | 0.00050287 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6266-196_0_4_load_57 | 64 | 0.0041816 | 0.001048 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6266-196_0_4_load_42 | 65 | 0.0035672 | 0.00089401 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6266-196_0_4_load_39 | 66 | 0.0022535 | 0.00056478 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6266-196_0_4_load_53 | 67 | 0.0016906 | 0.00042371 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6266-196_0_4_load_44 | 70 | 0.0031553 | 0.0007908 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6266-196_0_4_load_45 | 71 | 0.0030361 | 0.00076092 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6266-196_0_4_load_155 | 72 | 0.0030542 | 0.00076546 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6266-196_0_4_load_46 | 74 | 0.003275 | 0.00082079 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6266-196_0_4_load_146 | 76 | 0.003097 | 0.00077618 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6266-196_0_4_load_154 | 77 | 0.0059451 | 0.00149 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6266-196_0_4_load_47 | 78 | 0.0016048 | 0.0004022 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6266-196_0_4_load_48 | 79 | 0.0010137 | 0.00025406 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6266-196_0_4_load_50 | 80 | 0.001604 | 0.00040199 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6266-196_0_4_load_61 | 81 | 0.0011798 | 0.00029569 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6266-196_0_4_load_94 | 83 | 0.0028837 | 0.00072273 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6266-196_0_4_load_92 | 84 | 0.0017879 | 0.00044808 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6266-196_0_4_load_90 | 85 | 0.0024444 | 0.00061262 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_6266-196_0_4_load_65 | 86 | 0.0037048 | 0.00092852 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_6266-196_0_4_load_66 | 87 | 0.0038735 | 0.0009708 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_6266-196_0_4_load_67 | 88 | 0.0033078 | 0.00082902 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_6266-196_0_4_load_70 | 90 | 0.0021505 | 0.00053896 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_6266-196_0_4_load_72 | 91 | 0.0023374 | 0.00058582 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_6266-196_0_4_load_74 | 92 | 0.0030481 | 0.00076394 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_6266-196_0_4_load_132 | 94 | 0.0058849 | 0.0014749 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_6266-196_0_4_load_76 | 95 | 0.0025893 | 0.00064894 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_6266-196_0_4_load_77 | 96 | 0.0024639 | 0.0006175 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_6266-196_0_4_load_78 | 97 | 0.0021458 | 0.0005378 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_6266-196_0_4_load_80 | 98 | 0.0033464 | 0.00083869 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_6266-196_0_4_load_79 | 99 | 0.0035874 | 0.00089908 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_6266-196_0_4_load_81 | 100 | 0.006519 | 0.0016338 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_6266-196_0_4_load_82 | 101 | 0.0015586 | 0.00039062 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_6266-196_0_4_load_97 | 102 | 0.0017588 | 0.0004408 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_6266-196_0_4_load_83 | 103 | 0.0033393 | 0.00083691 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_6266-196_0_4_load_84 | 104 | 0.0031338 | 0.00078542 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_6266-196_0_4_load_125 | 105 | 0.0011528 | 0.00028893 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_6266-196_0_4_load_98 | 106 | 0.0024868 | 0.00062325 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_6266-196_0_4_load_117 | 107 | 0.0016332 | 0.00040931 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_6266-196_0_4_load_120 | 110 | 0.0016452 | 0.00041232 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_6266-196_0_4_load_121 | 111 | 0.0017683 | 0.00044319 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_6266-196_0_4_load_123 | 112 | 0.0016514 | 0.00041388 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_6266-196_0_4_load_124 | 113 | 0.0017197 | 0.00043099 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_6266-196_0_4_load_127 | 114 | 0.0011538 | 0.00028918 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_6266-196_0_4_load_149 | 115 | 0.0011522 | 0.00028877 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_6266-196_0_4_load_139 | 116 | 0.0013994 | 0.00035073 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_6266-196_0_4_load_150 | 118 | 0.0011528 | 0.00028891 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_6266-196_0_4_load_151 | 119 | 0.0042156 | 0.0010565 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_6266-196_0_4_load_126 | 120 | 0.0017336 | 0.00043448 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_6266-196_0_4_load_85 | 122 | 0.0019164 | 0.0004803 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_6266-196_0_4_load_86 | 123 | 0.0018585 | 0.00046579 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_6266-196_0_4_load_87 | 124 | 0.0052112 | 0.0013061 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_6266-196_0_4_load_88 | 125 | 0.0027214 | 0.00068204 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_6266-196_0_4_load_89 | 126 | 0.003327 | 0.00083383 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_6266-196_0_4_load_116 | 129 | 0.0034363 | 0.00086123 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_6266-196_0_4_load_114 | 131 | 0.0031477 | 0.00078889 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_6266-196_0_4_load_91 | 132 | 0.006858 | 0.0017188 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_6266-196_0_4_load_93 | 133 | 0.0016684 | 0.00041814 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_6266-196_0_4_load_106 | 134 | 0.001945 | 0.00048747 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_6266-196_0_4_load_103 | 135 | 0.0054599 | 0.0013684 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_6266-196_0_4_load_99 | 136 | 0.002601 | 0.00065187 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_6266-196_0_4_load_100 | 137 | 0.0044399 | 0.0011127 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_6266-196_0_4_load_101 | 138 | 0.0029629 | 0.00074257 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_6266-196_0_4_load_105 | 139 | 0.0037179 | 0.0009318 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_6266-196_0_4_load_109 | 140 | 0.0039032 | 0.00097824 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_6266-196_0_4_load_111 | 142 | 0.005442 | 0.0013639 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_6266-196_0_4_load_112 | 143 | 0.001579 | 0.00039572 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_6266-196_0_4_load_129 | 144 | 0.0018994 | 0.00047605 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_6266-196_0_4_load_141 | 146 | 0.002016 | 0.00050526 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_6266-196_0_4_load_142 | 147 | 0.0048351 | 0.0012118 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_6266-196_0_4_load_143 | 148 | 0.007545 | 0.001891 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_6266-196_0_4_load_131 | 149 | 0.0061088 | 0.001531 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_6266-196_0_4_load_133 | 150 | 0.0024736 | 0.00061993 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_6266-196_0_4_load_135 | 151 | 0.004372 | 0.0010957 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_6266-196_0_4_load_138 | 152 | 0.0071662 | 0.001796 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 89 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6266-196_0_4_line_0 |  | 0 | 1 | 0.051249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6266-196_0_4_line_1 |  | 0 | 2 | 0.066176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6266-196_0_4_line_2 |  | 1 | 3 | 0.076032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6266-196_0_4_line_3 |  | 2 | 4 | 0.042935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6266-196_0_4_line_4 |  | 3 | 7 | 0.0049529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6266-196_0_4_line_5 |  | 4 | 8 | 0.0098888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6266-196_0_4_line_6 |  | 5 | 6 | 0.0019118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6266-196_0_4_line_7 |  | 6 | 80 | 0.0013578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6266-196_0_4_line_8 |  | 7 | 9 | 0.030321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6266-196_0_4_line_9 |  | 9 | 10 | 0.074398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6266-196_0_4_line_10 |  | 10 | 11 | 0.043547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6266-196_0_4_line_11 |  | 11 | 21 | 0.05495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6266-196_0_4_line_12 |  | 12 | 13 | 0.038192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6266-196_0_4_line_13 |  | 13 | 14 | 0.010166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6266-196_0_4_line_14 |  | 14 | 15 | 0.011632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6266-196_0_4_line_15 |  | 15 | 16 | 0.025417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6266-196_0_4_line_16 |  | 16 | 135 | 0.016204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_6266-196_0_4_line_17 |  | 16 | 139 | 0.046123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6266-196_0_4_line_18 |  | 16 | 138 | 0.018023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_6266-196_0_4_line_19 |  | 17 | 18 | 0.040301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6266-196_0_4_line_20 |  | 17 | 19 | 0.057896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6266-196_0_4_line_21 |  | 18 | 20 | 0.012697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6266-196_0_4_line_22 |  | 18 | 21 | 0.025772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6266-196_0_4_line_23 |  | 20 | 22 | 0.012608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6266-196_0_4_line_24 |  | 22 | 23 | 0.0077268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6266-196_0_4_line_25 |  | 22 | 24 | 0.0068891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6266-196_0_4_line_26 |  | 24 | 60 | 0.029598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6266-196_0_4_line_27 |  | 25 | 26 | 0.010972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6266-196_0_4_line_28 |  | 26 | 27 | 0.022605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6266-196_0_4_line_29 |  | 27 | 28 | 0.0042313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6266-196_0_4_line_30 |  | 28 | 29 | 0.06994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6266-196_0_4_line_31 |  | 29 | 30 | 0.077496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6266-196_0_4_line_32 |  | 29 | 31 | 0.047056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6266-196_0_4_line_33 |  | 30 | 32 | 0.014563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6266-196_0_4_line_34 |  | 31 | 36 | 0.049137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6266-196_0_4_line_35 |  | 31 | 37 | 0.020965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6266-196_0_4_line_36 |  | 32 | 38 | 0.02827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6266-196_0_4_line_37 |  | 33 | 34 | 0.068701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6266-196_0_4_line_38 |  | 33 | 35 | 0.02657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6266-196_0_4_line_39 |  | 34 | 39 | 0.019215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6266-196_0_4_line_40 |  | 35 | 40 | 0.0013089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6266-196_0_4_line_41 |  | 36 | 41 | 0.052555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6266-196_0_4_line_42 |  | 36 | 42 | 0.024304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6266-196_0_4_line_43 |  | 37 | 43 | 0.0012745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6266-196_0_4_line_44 |  | 38 | 152 | 0.015692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6266-196_0_4_line_45 |  | 39 | 94 | 0.039235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6266-196_0_4_line_46 |  | 40 | 91 | 0.012973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6266-196_0_4_line_47 |  | 40 | 89 | 0.041943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6266-196_0_4_line_48 |  | 41 | 48 | 0.013508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6266-196_0_4_line_49 |  | 42 | 44 | 0.039638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6266-196_0_4_line_50 |  | 43 | 86 | 0.020897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6266-196_0_4_line_51 |  | 44 | 45 | 0.057344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6266-196_0_4_line_52 |  | 45 | 46 | 0.01996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6266-196_0_4_line_53 |  | 46 | 47 | 0.037978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6266-196_0_4_line_54 |  | 47 | 49 | 0.0052373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6266-196_0_4_line_55 |  | 47 | 50 | 0.024384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6266-196_0_4_line_56 |  | 48 | 52 | 0.0015297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6266-196_0_4_line_57 |  | 49 | 51 | 0.0073766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6266-196_0_4_line_58 |  | 53 | 54 | 0.0034644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6266-196_0_4_line_59 |  | 53 | 55 | 0.031599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6266-196_0_4_line_60 |  | 54 | 56 | 0.058591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6266-196_0_4_line_61 |  | 56 | 57 | 0.023293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6266-196_0_4_line_62 |  | 56 | 58 | 0.022728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6266-196_0_4_line_63 |  | 57 | 59 | 0.024852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6266-196_0_4_line_64 |  | 57 | 60 | 0.053446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_6266-196_0_4_line_65 |  | 58 | 61 | 0.061033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6266-196_0_4_line_66 |  | 58 | 62 | 0.020179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6266-196_0_4_line_67 |  | 60 | 63 | 0.0043765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_6266-196_0_4_line_68 |  | 60 | 64 | 0.085509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6266-196_0_4_line_69 |  | 61 | 65 | 0.023449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6266-196_0_4_line_70 |  | 61 | 66 | 0.0037127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6266-196_0_4_line_71 |  | 62 | 67 | 0.028296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_6266-196_0_4_line_72 |  | 63 | 81 | 0.03916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_6266-196_0_4_line_73 |  | 65 | 71 | 0.0050647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_6266-196_0_4_line_74 |  | 66 | 68 | 0.00018712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_6266-196_0_4_line_75 |  | 68 | 69 | 0.02189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_6266-196_0_4_line_76 |  | 68 | 70 | 0.026285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_6266-196_0_4_line_77 |  | 69 | 72 | 0.030183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_6266-196_0_4_line_78 |  | 69 | 73 | 0.037137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_6266-196_0_4_line_79 |  | 71 | 74 | 0.018082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_6266-196_0_4_line_80 |  | 73 | 75 | 0.020965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_6266-196_0_4_line_81 |  | 73 | 76 | 0.042523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_6266-196_0_4_line_82 |  | 74 | 78 | 0.01623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_6266-196_0_4_line_83 |  | 75 | 77 | 0.068603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_6266-196_0_4_line_84 |  | 78 | 79 | 0.014164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_6266-196_0_4_line_85 |  | 79 | 80 | 0.0030097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_6266-196_0_4_line_86 |  | 81 | 82 | 0.015177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_6266-196_0_4_line_87 |  | 82 | 83 | 0.085521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_6266-196_0_4_line_88 |  | 82 | 84 | 0.015521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_6266-196_0_4_line_89 |  | 84 | 85 | 0.00058836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
90 | LV_6266-196_0_4_line_90 |  | 85 | 132 | 0.042507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
91 | LV_6266-196_0_4_line_91 |  | 86 | 87 | 0.0057399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_6266-196_0_4_line_92 |  | 87 | 88 | 0.0063406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_6266-196_0_4_line_93 |  | 88 | 89 | 0.015013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_6266-196_0_4_line_94 |  | 89 | 90 | 0.033817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
95 | LV_6266-196_0_4_line_95 |  | 90 | 92 | 0.0023142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_6266-196_0_4_line_96 |  | 92 | 93 | 0.0073144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
97 | LV_6266-196_0_4_line_97 |  | 93 | 95 | 0.012553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
98 | LV_6266-196_0_4_line_98 |  | 93 | 96 | 0.021904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_6266-196_0_4_line_99 |  | 94 | 149 | 0.0018731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_6266-196_0_4_line_100 |  | 95 | 97 | 0.020319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_6266-196_0_4_line_101 |  | 96 | 98 | 0.013967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_6266-196_0_4_line_102 |  | 97 | 99 | 0.024797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_6266-196_0_4_line_103 |  | 98 | 100 | 0.0031832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_6266-196_0_4_line_104 |  | 99 | 101 | 0.00029368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
105 | LV_6266-196_0_4_line_105 |  | 100 | 103 | 0.053414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_6266-196_0_4_line_106 |  | 101 | 102 | 0.0074058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
107 | LV_6266-196_0_4_line_107 |  | 102 | 106 | 0.0031852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
108 | LV_6266-196_0_4_line_108 |  | 103 | 104 | 0.0092803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_6266-196_0_4_line_109 |  | 103 | 105 | 0.095711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_6266-196_0_4_line_110 |  | 105 | 114 | 0.022843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_6266-196_0_4_line_111 |  | 105 | 112 | 0.039314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_6266-196_0_4_line_112 |  | 106 | 136 | 0.013747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
113 | LV_6266-196_0_4_line_113 |  | 107 | 108 | 0.0080537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_6266-196_0_4_line_114 |  | 108 | 109 | 0.06075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_6266-196_0_4_line_115 |  | 109 | 117 | 0.086273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_6266-196_0_4_line_116 |  | 109 | 110 | 0.056194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_6266-196_0_4_line_117 |  | 110 | 111 | 0.012366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_6266-196_0_4_line_118 |  | 112 | 113 | 0.015191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_6266-196_0_4_line_119 |  | 113 | 120 | 0.015407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_6266-196_0_4_line_120 |  | 114 | 115 | 0.018453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_6266-196_0_4_line_121 |  | 115 | 118 | 0.0025726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_6266-196_0_4_line_122 |  | 116 | 117 | 0.093583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_6266-196_0_4_line_123 |  | 117 | 146 | 0.024266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_6266-196_0_4_line_124 |  | 118 | 119 | 0.015985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_6266-196_0_4_line_125 |  | 120 | 121 | 0.072117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_6266-196_0_4_line_126 |  | 121 | 144 | 0.082373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_6266-196_0_4_line_127 |  | 121 | 145 | 0.078621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_6266-196_0_4_line_128 |  | 122 | 123 | 0.015646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_6266-196_0_4_line_129 |  | 122 | 124 | 0.010146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_6266-196_0_4_line_130 |  | 123 | 125 | 0.037563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_6266-196_0_4_line_131 |  | 124 | 126 | 0.02355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_6266-196_0_4_line_132 |  | 125 | 127 | 0.020173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_6266-196_0_4_line_133 |  | 126 | 128 | 0.023221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_6266-196_0_4_line_134 |  | 127 | 129 | 0.014809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_6266-196_0_4_line_135 |  | 127 | 130 | 0.0074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_6266-196_0_4_line_136 |  | 128 | 131 | 0.019681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_6266-196_0_4_line_137 |  | 130 | 140 | 0.017119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_6266-196_0_4_line_138 |  | 130 | 139 | 0.0065789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_6266-196_0_4_line_139 |  | 132 | 133 | 0.0023335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
140 | LV_6266-196_0_4_line_140 |  | 133 | 134 | 0.010061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
141 | LV_6266-196_0_4_line_141 |  | 134 | 135 | 0.01677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
142 | LV_6266-196_0_4_line_142 |  | 136 | 137 | 0.0002368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
143 | LV_6266-196_0_4_line_143 |  | 137 | 138 | 0.012125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
144 | LV_6266-196_0_4_line_144 |  | 140 | 141 | 0.010847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_6266-196_0_4_line_145 |  | 141 | 142 | 0.041656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_6266-196_0_4_line_146 |  | 141 | 143 | 0.00962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_6266-196_0_4_line_147 |  | 145 | 146 | 0.048947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_6266-196_0_4_line_148 |  | 145 | 147 | 0.04813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_6266-196_0_4_line_149 |  | 147 | 148 | 0.055902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_6266-196_0_4_line_150 |  | 149 | 150 | 0.027248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_6266-196_0_4_line_151 |  | 150 | 151 | 0.038694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6266-196_0_4_trafo_68 | 0.63 MVA 20/0.4 kV | 153 | 89 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2595344.0549 | 1117140.3069 | 2595344.0549 | 1117140.3069 | 2595356.4623 | 1117190.0317
1 | 2595344.0549 | 1117140.3069 | 2595346.5589 | 1117134.5577 | 2595352.4676 | 1117130.0397 | 2595404.9203 | 1117128.8185
2 | 2595389.5935 | 1117257.9326 | 2595377.4705 | 1117233.9046 | 2595360.3063 | 1117205.4373 | 2595356.4623 | 1117190.0317
3 | 2595404.9203 | 1117128.8185 | 2595412.2293 | 1117128.6483 | 2595447.8498 | 1117129.1286
4 | 2595389.5935 | 1117257.9326 | 2595391.8245 | 1117262.3546
5 | 2595447.8498 | 1117129.1286 | 2595452.0176 | 1117129.1847 | 2595457.7382 | 1117129.1707
6 | 2595263.7644 | 1117250.7354 | 2595262.8659 | 1117252.4229
7 | 2595262.2278 | 1117253.6214 | 2595262.8659 | 1117252.4229
8 | 2595405.4824 | 1117289.4251 | 2595391.8245 | 1117262.3546
9 | 2595412.441 | 1117363.4967 | 2595405.4824 | 1117289.4251
10 | 2595451.8318 | 1117381.1529 | 2595441.851 | 1117379.2596 | 2595426.3172 | 1117372.5682 | 2595412.441 | 1117363.4967
11 | 2595451.8318 | 1117381.1529 | 2595425.6405 | 1117405.8851 | 2595417.0133 | 1117422.7313
12 | 2595467.3241 | 1117576.9371 | 2595469.0636 | 1117580.8377 | 2595474.4532 | 1117584.3354 | 2595483.3541 | 1117587.419 | 2595492.6714 | 1117590.1021 | 2595500.2304 | 1117593.7195
13 | 2595467.3241 | 1117576.9371 | 2595457.1982 | 1117576.0329
14 | 2595445.6127 | 1117574.9984 | 2595457.1982 | 1117576.0329
15 | 2595420.2967 | 1117572.7377 | 2595445.6127 | 1117574.9984
16 | 2595420.2967 | 1117572.7377 | 2595412.8268 | 1117558.3579
17 | 2595420.2967 | 1117572.7377 | 2595423.9364 | 1117578.8045 | 2595428.2855 | 1117583.9593 | 2595430.3571 | 1117588.2932 | 2595431.7172 | 1117615.7599
18 | 2595420.2967 | 1117572.7377 | 2595403.3164 | 1117571.0499 | 2595402.4145 | 1117570.7241
19 | 2595409.8429 | 1117447.3176 | 2595417.2148 | 1117449.0238 | 2595430.4626 | 1117454.1718 | 2595441.6496 | 1117459.1101 | 2595444.4441 | 1117459.8083 | 2595447.8553 | 1117459.7278
20 | 2595448.6638 | 1117426.9111 | 2595436.6509 | 1117421.9734 | 2595434.378 | 1117427.1333 | 2595433.5549 | 1117430.6467 | 2595434.3833 | 1117433.9477 | 2595446.4037 | 1117448.7902 | 2595448.2659 | 1117451.6791 | 2595449.9267 | 1117453.5343 | 2595450.546 | 1117456.0128 | 2595449.4055 | 1117458.3593 | 2595447.8553 | 1117459.7278
21 | 2595409.8429 | 1117447.3176 | 2595397.1471 | 1117447.4719
22 | 2595409.8429 | 1117447.3176 | 2595413.9653 | 1117428.683 | 2595417.0133 | 1117422.7313
23 | 2595385.0196 | 1117444.024 | 2595397.1471 | 1117447.4719
24 | 2595385.0196 | 1117444.024 | 2595388.5127 | 1117437.1318
25 | 2595385.0196 | 1117444.024 | 2595383.5374 | 1117443.6027 | 2595378.4418 | 1117441.9785
26 | 2595350.2418 | 1117432.9901 | 2595378.4418 | 1117441.9785
27 | 2595083.5992 | 1117415.2698 | 2595092.281 | 1117417.7004 | 2595094.1178 | 1117418.3743
28 | 2595094.1178 | 1117418.3743 | 2595107.6675 | 1117423.346 | 2595115.0357 | 1117426.8801
29 | 2595115.0357 | 1117426.8801 | 2595118.8509 | 1117428.71
30 | 2595178.8275 | 1117462.4517 | 2595176.1605 | 1117457.0957 | 2595136.1732 | 1117437.0183 | 2595118.8509 | 1117428.71
31 | 2595178.8275 | 1117462.4517 | 2595159.1476 | 1117463.2681 | 2595128.7579 | 1117467.317 | 2595101.4302 | 1117468.8068
32 | 2595178.8275 | 1117462.4517 | 2595189.7866 | 1117461.9982 | 2595199.7512 | 1117463.0574 | 2595225.6011 | 1117466.4161
33 | 2595101.4302 | 1117468.8068 | 2595114.0321 | 1117476.1046
34 | 2595225.6011 | 1117466.4161 | 2595225.6183 | 1117459.0347 | 2595224.2794 | 1117454.3334 | 2595220.7416 | 1117450.6789 | 2595190.5976 | 1117443.633 | 2595189.7714 | 1117443.2335
35 | 2595225.6011 | 1117466.4161 | 2595235.7221 | 1117470.0431 | 2595244.6868 | 1117474.9369
36 | 2595138.4963 | 1117490.2717 | 2595114.0321 | 1117476.1046
37 | 2595221.6875 | 1117484.9394 | 2595220.2155 | 1117487.5085 | 2595212.3466 | 1117491.7058 | 2595201.888 | 1117509.6563 | 2595193.8217 | 1117527.4159 | 2595183.7694 | 1117532.282 | 2595178.4821 | 1117533.2384
38 | 2595221.6875 | 1117484.9394 | 2595244.258 | 1117498.9593
39 | 2595159.4201 | 1117533.7078 | 2595171.0523 | 1117534.5823 | 2595178.4821 | 1117533.2384
40 | 2595245.3699 | 1117499.6499 | 2595244.258 | 1117498.9593
41 | 2595189.7714 | 1117443.2335 | 2595190.6878 | 1117440.6648 | 2595192.6006 | 1117439.1181 | 2595221.479 | 1117436.6714 | 2595225.6227 | 1117435.5787 | 2595226.9113 | 1117435.2219 | 2595227.898 | 1117433.7204 | 2595226.9087 | 1117432.0204 | 2595220.0487 | 1117426.1952
42 | 2595189.7714 | 1117443.2335 | 2595169.5889 | 1117433.4783 | 2595167.9834 | 1117432.4852
43 | 2595244.6868 | 1117474.9369 | 2595245.8055 | 1117475.5476
44 | 2595152.0755 | 1117498.1354 | 2595138.4963 | 1117490.2717
45 | 2595159.4201 | 1117533.7078 | 2595152.3278 | 1117533.1746 | 2595126.5373 | 1117536.0192 | 2595120.3756 | 1117536.4398
46 | 2595256.4119 | 1117506.5111 | 2595245.3699 | 1117499.6499
47 | 2595286.7998 | 1117500.3729 | 2595283.7373 | 1117502.2763 | 2595265.9314 | 1117501.201 | 2595245.3699 | 1117499.6499
48 | 2595210.086 | 1117417.1801 | 2595210.6514 | 1117418.2155 | 2595220.0487 | 1117426.1952
49 | 2595134.7591 | 1117410.8897 | 2595149.3964 | 1117420.9886 | 2595167.9834 | 1117432.4852
50 | 2595264.1478 | 1117485.5604 | 2595245.8055 | 1117475.5476
51 | 2595086.1764 | 1117380.5872 | 2595107.2481 | 1117391.9088 | 2595134.7591 | 1117410.8897
52 | 2595086.1764 | 1117380.5872 | 2595089.8713 | 1117378.094 | 2595105.3519 | 1117378.9251
53 | 2595142.6624 | 1117378.1508 | 2595138.8361 | 1117380.4329 | 2595131.4808 | 1117380.3277 | 2595105.3519 | 1117378.9251
54 | 2595142.6624 | 1117378.1508 | 2595142.2977 | 1117375.8167 | 2595139.8113 | 1117374.3735
55 | 2595142.6624 | 1117378.1508 | 2595146.0272 | 1117377.9702 | 2595154.7273 | 1117380.3421 | 2595165.5954 | 1117381.7784 | 2595166.622 | 1117381.9045
56 | 2595209.3529 | 1117415.8376 | 2595210.086 | 1117417.1801
57 | 2595132.6707 | 1117372.5229 | 2595139.8113 | 1117374.3735
58 | 2595243.9497 | 1117359.3568 | 2595247.3871 | 1117358.9255
59 | 2595213.4393 | 1117353.0257 | 2595232.2763 | 1117359.4027 | 2595240.3574 | 1117359.8075 | 2595243.9497 | 1117359.3568
60 | 2595303.8863 | 1117372.0965 | 2595289.6268 | 1117366.5828 | 2595278.757 | 1117362.9563 | 2595264.9856 | 1117359.7879 | 2595251.9487 | 1117358.3531 | 2595247.3871 | 1117358.9255
61 | 2595303.8863 | 1117372.0965 | 2595320.0224 | 1117388.9365
62 | 2595303.8863 | 1117372.0965 | 2595285.4144 | 1117358.7824
63 | 2595343.0117 | 1117395.5329 | 2595334.6261 | 1117390.5926 | 2595328.5197 | 1117388.6408 | 2595324.3744 | 1117387.7103 | 2595320.0224 | 1117388.9365
64 | 2595350.2418 | 1117432.9901 | 2595323.1199 | 1117392.169 | 2595320.0224 | 1117388.9365
65 | 2595235.8207 | 1117323.0153 | 2595285.4144 | 1117358.7824
66 | 2595285.4144 | 1117358.7824 | 2595288.5392 | 1117357.6126 | 2595295.2703 | 1117358.8413 | 2595304.4756 | 1117362.748
67 | 2595350.2418 | 1117432.9901 | 2595353.0201 | 1117436.3716
68 | 2595350.2418 | 1117432.9901 | 2595345.1161 | 1117431.749 | 2595332.4706 | 1117417.3185 | 2595323.3565 | 1117408.4546 | 2595308.9596 | 1117394.9482 | 2595296.226 | 1117386.4985 | 2595284.2886 | 1117380.6074
69 | 2595235.8207 | 1117323.0153 | 2595250.4612 | 1117312.5541 | 2595253.7688 | 1117308.216
70 | 2595235.8207 | 1117323.0153 | 2595232.8137 | 1117320.8376
71 | 2595304.4756 | 1117362.748 | 2595324.1607 | 1117371.1023 | 2595330.4264 | 1117374.0186
72 | 2595353.0201 | 1117436.3716 | 2595358.9404 | 1117443.5774 | 2595379.1637 | 1117465.5115
73 | 2595253.7688 | 1117308.216 | 2595254.7991 | 1117303.2572 | 2595254.7991 | 1117303.2572
74 | 2595232.6622 | 1117320.7278 | 2595232.8137 | 1117320.8376
75 | 2595232.6622 | 1117320.7278 | 2595215.7189 | 1117308.4687 | 2595214.9929 | 1117307.7579
76 | 2595232.6622 | 1117320.7278 | 2595234.3709 | 1117314.8125 | 2595235.1932 | 1117310.4763 | 2595234.4729 | 1117307.2865 | 2595232.194 | 1117304.6981 | 2595224.7186 | 1117299.6947
77 | 2595186.4388 | 1117301.6667 | 2595192.7523 | 1117301.8728 | 2595199.3762 | 1117304.0352 | 2595205.2825 | 1117306.5095 | 2595210.664 | 1117308.973 | 2595213.2495 | 1117308.8709 | 2595214.9929 | 1117307.7579
78 | 2595186.7331 | 1117283.8578 | 2595191.7836 | 1117287.3776 | 2595200.147 | 1117293.2182 | 2595214.9929 | 1117307.7579
79 | 2595253.5422 | 1117285.2608 | 2595253.5493 | 1117294.1759 | 2595254.7991 | 1117303.2572
80 | 2595177.1575 | 1117287.0226 | 2595187.9793 | 1117288.2923 | 2595191.7836 | 1117287.3776 | 2595186.7331 | 1117283.8578
81 | 2595186.7331 | 1117283.8578 | 2595182.9877 | 1117271.6659 | 2595177.8939 | 1117262.2988 | 2595170.1665 | 1117244.8246
82 | 2595255.1857 | 1117269.1588 | 2595253.5378 | 1117279.7355 | 2595253.5422 | 1117285.2608
83 | 2595177.1575 | 1117287.0226 | 2595169.2953 | 1117290.1194 | 2595159.9842 | 1117295.9075 | 2595152.1829 | 1117307.4751 | 2595147.3468 | 1117311.2587 | 2595144.5237 | 1117313.462 | 2595140.0833 | 1117319.8688 | 2595137.4919 | 1117322.1387 | 2595123.105 | 1117321.5279
84 | 2595255.1857 | 1117269.1588 | 2595255.5957 | 1117266.5274 | 2595260.8253 | 1117256.2843
85 | 2595262.2278 | 1117253.6214 | 2595261.1827 | 1117255.5843 | 2595260.8253 | 1117256.2843
86 | 2595389.4518 | 1117476.6699 | 2595379.1637 | 1117465.5115
87 | 2595389.4518 | 1117476.6699 | 2595447.2497 | 1117539.7037
88 | 2595389.4518 | 1117476.6699 | 2595391.2489 | 1117492.0866
89 | 2595391.2489 | 1117492.0866 | 2595391.317 | 1117492.671
90 | 2595391.317 | 1117492.671 | 2595393.2976 | 1117509.6609 | 2595396.0581 | 1117516.4288 | 2595397.7164 | 1117525.0317 | 2595396.9332 | 1117534.3307
91 | 2595269.1859 | 1117488.3107 | 2595264.1478 | 1117485.5604
92 | 2595269.1859 | 1117488.3107 | 2595270.1278 | 1117488.8249 | 2595274.458 | 1117491.8243
93 | 2595286.7998 | 1117500.3729 | 2595274.458 | 1117491.8243
94 | 2595286.7998 | 1117500.3729 | 2595298.7853 | 1117509.8237 | 2595311.7269 | 1117523.1185
95 | 2595311.7269 | 1117523.1185 | 2595313.3411 | 1117524.7768
96 | 2595318.443 | 1117530.0181 | 2595313.3411 | 1117524.7768
97 | 2595318.443 | 1117530.0181 | 2595319.6866 | 1117531.2955 | 2595327.4914 | 1117538.7168
98 | 2595318.443 | 1117530.0181 | 2595315.691 | 1117534.1445 | 2595314.7662 | 1117535.8461 | 2595307.3253 | 1117548.8792
99 | 2595118.5068 | 1117536.5673 | 2595120.3756 | 1117536.4398
100 | 2595327.4914 | 1117538.7168 | 2595332.8398 | 1117543.8025 | 2595341.2945 | 1117548.6427 | 2595344.3009 | 1117549.7288
101 | 2595307.3253 | 1117548.8792 | 2595304.2768 | 1117554.2189 | 2595303.345 | 1117556.7987 | 2595302.9322 | 1117561.857
102 | 2595344.3009 | 1117549.7288 | 2595367.6223 | 1117558.1544
103 | 2595299.7753 | 1117561.4482 | 2595302.9322 | 1117561.857
104 | 2595367.8985 | 1117558.2541 | 2595367.6223 | 1117558.1544
105 | 2595299.7753 | 1117561.4482 | 2595277.8113 | 1117610.1373
106 | 2595367.8985 | 1117558.2541 | 2595374.8637 | 1117560.7705
107 | 2595374.8637 | 1117560.7705 | 2595377.8594 | 1117561.8528
108 | 2595277.8113 | 1117610.1373 | 2595279.6317 | 1117609.7989 | 2595286.0613 | 1117613.5201
109 | 2595277.8113 | 1117610.1373 | 2595208.8837 | 1117676.5417
110 | 2595208.8837 | 1117676.5417 | 2595202.1719 | 1117670.6128 | 2595192.6454 | 1117660.5084
111 | 2595208.8837 | 1117676.5417 | 2595223.2945 | 1117689.2716 | 2595231.3555 | 1117694.0342 | 2595240.5824 | 1117699.4968
112 | 2595390.7883 | 1117566.5238 | 2595377.8594 | 1117561.8528
113 | 2595176.2967 | 1117711.2536 | 2595180.1884 | 1117704.2025
114 | 2595231.4439 | 1117737.0775 | 2595192.2009 | 1117718.6777 | 2595176.2967 | 1117711.2536
115 | 2595292.8362 | 1117794.8237 | 2595268.2045 | 1117759.059 | 2595246.6609 | 1117744.2133 | 2595231.4439 | 1117737.0775
116 | 2595231.4439 | 1117737.0775 | 2595228.1845 | 1117733.8229 | 2595221.7659 | 1117727.1248 | 2595215.4933 | 1117719.7484 | 2595205.0364 | 1117710.6301 | 2595198.3027 | 1117705.6775 | 2595197.1674 | 1117704.6001 | 2595197.6834 | 1117703.2546 | 2595200.8848 | 1117701.6068 | 2595204.6632 | 1117701.8809
117 | 2595216.2556 | 1117698.2928 | 2595213.9795 | 1117699.0172 | 2595210.3074 | 1117700.8766 | 2595207.0978 | 1117702.0576 | 2595204.6632 | 1117701.8809
118 | 2595240.5824 | 1117699.4968 | 2595241.2 | 1117699.8625 | 2595253.9614 | 1117706.6894
119 | 2595253.9614 | 1117706.6894 | 2595257.1977 | 1117708.4206 | 2595266.874 | 1117715.0626
120 | 2595192.6454 | 1117660.5084 | 2595188.5154 | 1117656.1278 | 2595181.1481 | 1117646.1135
121 | 2595179.4392 | 1117644.2096 | 2595180.3257 | 1117644.9956 | 2595181.1481 | 1117646.1135
122 | 2595292.8362 | 1117794.8237 | 2595267.4398 | 1117777.5686 | 2595206.6226 | 1117761.5985
123 | 2595292.8362 | 1117794.8237 | 2595309.5071 | 1117806.1383 | 2595313.2359 | 1117807.8857
124 | 2595179.4392 | 1117644.2096 | 2595167.4788 | 1117633.6043
125 | 2595306.1485 | 1117774.8145 | 2595305.545 | 1117772.9474 | 2595295.1276 | 1117754.9356 | 2595280.9885 | 1117734.6591 | 2595275.8554 | 1117723.6244 | 2595269.2977 | 1117716.7262 | 2595266.874 | 1117715.0626
126 | 2595306.1485 | 1117774.8145 | 2595311.0721 | 1117774.655 | 2595316.9719 | 1117779.297 | 2595331.784 | 1117792.0806 | 2595345.3489 | 1117798.8733 | 2595360.7727 | 1117804.4307 | 2595368.1211 | 1117806.1814 | 2595372.0573 | 1117806.5896 | 2595379.3505 | 1117806.8508
127 | 2595357.558 | 1117828.6562 | 2595357.1294 | 1117823.3539 | 2595354.2146 | 1117816.6084 | 2595318.6595 | 1117795.7482 | 2595309.2585 | 1117784.5057 | 2595306.1485 | 1117774.8145
128 | 2595359.5468 | 1117597.8859 | 2595361.4367 | 1117596.5949 | 2595373.3551 | 1117602.626
129 | 2595359.5468 | 1117597.8859 | 2595359.5468 | 1117597.8859 | 2595358.2827 | 1117599.899 | 2595357.2964 | 1117601.9674 | 2595359.9905 | 1117606.7367
130 | 2595373.3551 | 1117602.626 | 2595406.871 | 1117619.5859
131 | 2595371.5728 | 1117627.2413 | 2595359.9905 | 1117606.7367
132 | 2595425.6395 | 1117625.6929 | 2595422.8306 | 1117626.1397 | 2595417.7436 | 1117624.8541 | 2595409.4518 | 1117620.8919 | 2595406.871 | 1117619.5859
133 | 2595383.2938 | 1117647.2028 | 2595382.4907 | 1117646.5697 | 2595371.5728 | 1117627.2413
134 | 2595425.6395 | 1117625.6929 | 2595424.1306 | 1117620.5693 | 2595421.5421 | 1117616.5471 | 2595417.9664 | 1117613.5039
135 | 2595432.0426 | 1117622.3308 | 2595428.0085 | 1117625.3131 | 2595425.6395 | 1117625.6929
136 | 2595383.2938 | 1117647.2028 | 2595386.0044 | 1117649.3239 | 2595400.7846 | 1117656.0505
137 | 2595432.0426 | 1117622.3308 | 2595439.5044 | 1117637.7379
138 | 2595432.0426 | 1117622.3308 | 2595431.7172 | 1117615.7599
139 | 2595397.2979 | 1117536.4955 | 2595396.8063 | 1117535.8377 | 2595396.9332 | 1117534.3307
140 | 2595403.2803 | 1117544.5843 | 2595402.1371 | 1117542.9704 | 2595397.2979 | 1117536.4955
141 | 2595412.8268 | 1117558.3579 | 2595412.5443 | 1117557.8141 | 2595412.2506 | 1117557.2474 | 2595403.2803 | 1117544.5843
142 | 2595391.011 | 1117566.6042 | 2595390.7883 | 1117566.5238
143 | 2595391.011 | 1117566.6042 | 2595402.4145 | 1117570.7241
144 | 2595444.2326 | 1117647.5005 | 2595439.5044 | 1117637.7379
145 | 2595444.2326 | 1117647.5005 | 2595449.1433 | 1117650.4871 | 2595455.2495 | 1117652.4723 | 2595466.2175 | 1117654.1536 | 2595476.9296 | 1117654.1344 | 2595484.6464 | 1117653.0391
146 | 2595444.2326 | 1117647.5005 | 2595441.7952 | 1117649.3366 | 2595440.2454 | 1117651.1942 | 2595439.7315 | 1117655.3188
147 | 2595357.558 | 1117828.6562 | 2595313.2359 | 1117807.8857
148 | 2595357.558 | 1117828.6562 | 2595360.3803 | 1117835.7352 | 2595369.0323 | 1117846.6005 | 2595373.4685 | 1117854.89 | 2595375.7442 | 1117863.6925 | 2595376.9669 | 1117868.0159 | 2595379.5388 | 1117870.5819
149 | 2595397.6971 | 1117909.6759 | 2595401.2073 | 1117898.2231 | 2595405.2351 | 1117887.3925 | 2595403.7267 | 1117882.7914 | 2595400.359 | 1117879.0143 | 2595386.0699 | 1117873.4115 | 2595379.5388 | 1117870.5819
150 | 2595118.5068 | 1117536.5673 | 2595097.6898 | 1117537.9882 | 2595091.5086 | 1117539.5783
151 | 2595053.6784 | 1117547.1814 | 2595066.779 | 1117545.9398 | 2595091.5086 | 1117539.5783

## bus_geodata
| x | y | coords
0 | 2595344.0549 | 1117140.3069
1 | 2595356.4623 | 1117190.0317
2 | 2595404.9203 | 1117128.8185
3 | 2595389.5935 | 1117257.9326
4 | 2595447.8498 | 1117129.1286
5 | 2595263.7644 | 1117250.7354
6 | 2595262.8659 | 1117252.4229
7 | 2595391.8245 | 1117262.3546
8 | 2595457.7382 | 1117129.1707
9 | 2595405.4824 | 1117289.4251
10 | 2595412.441 | 1117363.4967
11 | 2595451.8318 | 1117381.1529
12 | 2595500.2304 | 1117593.7195
13 | 2595467.3241 | 1117576.9371
14 | 2595457.1982 | 1117576.0329
15 | 2595445.6127 | 1117574.9984
16 | 2595420.2967 | 1117572.7377
17 | 2595447.8553 | 1117459.7278
18 | 2595409.8429 | 1117447.3176
19 | 2595448.6638 | 1117426.9111
20 | 2595397.1471 | 1117447.4719
21 | 2595417.0133 | 1117422.7313
22 | 2595385.0196 | 1117444.024
23 | 2595388.5127 | 1117437.1318
24 | 2595378.4418 | 1117441.9785
25 | 2595083.5992 | 1117415.2698
26 | 2595094.1178 | 1117418.3743
27 | 2595115.0357 | 1117426.8801
28 | 2595118.8509 | 1117428.71
29 | 2595178.8275 | 1117462.4517
30 | 2595101.4302 | 1117468.8068
31 | 2595225.6011 | 1117466.4161
32 | 2595114.0321 | 1117476.1046
33 | 2595221.6875 | 1117484.9394
34 | 2595178.4821 | 1117533.2384
35 | 2595244.258 | 1117498.9593
36 | 2595189.7714 | 1117443.2335
37 | 2595244.6868 | 1117474.9369
38 | 2595138.4963 | 1117490.2717
39 | 2595159.4201 | 1117533.7078
40 | 2595245.3699 | 1117499.6499
41 | 2595220.0487 | 1117426.1952
42 | 2595167.9834 | 1117432.4852
43 | 2595245.8055 | 1117475.5475
44 | 2595134.7591 | 1117410.8897
45 | 2595086.1764 | 1117380.5872
46 | 2595105.3519 | 1117378.9251
47 | 2595142.6624 | 1117378.1508
48 | 2595210.086 | 1117417.1801
49 | 2595139.8113 | 1117374.3735
50 | 2595166.622 | 1117381.9045
51 | 2595132.6707 | 1117372.5229
52 | 2595209.3529 | 1117415.8376
53 | 2595243.9497 | 1117359.3568
54 | 2595247.3871 | 1117358.9255
55 | 2595213.4393 | 1117353.0257
56 | 2595303.8863 | 1117372.0965
57 | 2595320.0224 | 1117388.9365
58 | 2595285.4144 | 1117358.7824
59 | 2595343.0117 | 1117395.5329
60 | 2595350.2418 | 1117432.9901
61 | 2595235.8207 | 1117323.0153
62 | 2595304.4756 | 1117362.748
63 | 2595353.0201 | 1117436.3716
64 | 2595284.2886 | 1117380.6074
65 | 2595253.7688 | 1117308.216
66 | 2595232.8137 | 1117320.8376
67 | 2595330.4264 | 1117374.0186
68 | 2595232.6622 | 1117320.7278
69 | 2595214.9929 | 1117307.7579
70 | 2595224.7186 | 1117299.6947
71 | 2595254.7991 | 1117303.2572
72 | 2595186.4388 | 1117301.6667
73 | 2595186.7331 | 1117283.8578
74 | 2595253.5422 | 1117285.2608
75 | 2595177.1575 | 1117287.0226
76 | 2595170.1665 | 1117244.8246
77 | 2595123.105 | 1117321.5279
78 | 2595255.1857 | 1117269.1588
79 | 2595260.8253 | 1117256.2843
80 | 2595262.2278 | 1117253.6214
81 | 2595379.1637 | 1117465.5115
82 | 2595389.4518 | 1117476.6699
83 | 2595447.2497 | 1117539.7037
84 | 2595391.2489 | 1117492.0866
85 | 2595391.317 | 1117492.671
86 | 2595264.1478 | 1117485.5604
87 | 2595269.1859 | 1117488.3107
88 | 2595274.458 | 1117491.8243
89 | 2595286.7998 | 1117500.3729
90 | 2595311.7269 | 1117523.1185
91 | 2595256.4119 | 1117506.5111
92 | 2595313.3411 | 1117524.7768
93 | 2595318.443 | 1117530.0181
94 | 2595120.3756 | 1117536.4398
95 | 2595327.4914 | 1117538.7168
96 | 2595307.3253 | 1117548.8792
97 | 2595344.3009 | 1117549.7288
98 | 2595302.9322 | 1117561.857
99 | 2595367.6223 | 1117558.1544
100 | 2595299.7753 | 1117561.4482
101 | 2595367.8985 | 1117558.2541
102 | 2595374.8637 | 1117560.7705
103 | 2595277.8113 | 1117610.1373
104 | 2595286.0613 | 1117613.5201
105 | 2595208.8837 | 1117676.5417
106 | 2595377.8594 | 1117561.8528
107 | 2595180.1884 | 1117704.2025
108 | 2595176.2967 | 1117711.2536
109 | 2595231.4439 | 1117737.0775
110 | 2595204.6632 | 1117701.8809
111 | 2595216.2556 | 1117698.2928
112 | 2595240.5824 | 1117699.4968
113 | 2595253.9614 | 1117706.6894
114 | 2595192.6454 | 1117660.5084
115 | 2595181.1481 | 1117646.1135
116 | 2595206.6226 | 1117761.5985
117 | 2595292.8362 | 1117794.8237
118 | 2595179.4392 | 1117644.2095
119 | 2595167.4788 | 1117633.6043
120 | 2595266.874 | 1117715.0626
121 | 2595306.1485 | 1117774.8145
122 | 2595359.5468 | 1117597.8859
123 | 2595373.3551 | 1117602.626
124 | 2595359.9905 | 1117606.7368
125 | 2595406.871 | 1117619.5859
126 | 2595371.5728 | 1117627.2413
127 | 2595425.6395 | 1117625.6929
128 | 2595383.2938 | 1117647.2028
129 | 2595417.9664 | 1117613.5039
130 | 2595432.0426 | 1117622.3308
131 | 2595400.7846 | 1117656.0505
132 | 2595396.9332 | 1117534.3307
133 | 2595397.2979 | 1117536.4955
134 | 2595403.2803 | 1117544.5843
135 | 2595412.8268 | 1117558.3579
136 | 2595390.7883 | 1117566.5238
137 | 2595391.011 | 1117566.6042
138 | 2595402.4145 | 1117570.7241
139 | 2595431.7172 | 1117615.7599
140 | 2595439.5044 | 1117637.7379
141 | 2595444.2326 | 1117647.5005
142 | 2595484.6464 | 1117653.0391
143 | 2595439.7315 | 1117655.3188
144 | 2595379.3505 | 1117806.8508
145 | 2595357.558 | 1117828.6562
146 | 2595313.2359 | 1117807.8857
147 | 2595379.5388 | 1117870.5819
148 | 2595397.6971 | 1117909.6759
149 | 2595118.5068 | 1117536.5673
150 | 2595091.5086 | 1117539.5783
151 | 2595053.6784 | 1117547.1814
152 | 2595152.0755 | 1117498.1354
153 | 2595245.3699 | 1117499.6499

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1