## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6300-51_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6300-51_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6300-51_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6300-51_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6300-51_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6300-51_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6300-51_0_6_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_6300-51_0_6_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_6300-51_0_6_node_29 | 0.4 | n |  | TRUE
9 | bus_LV_6300-51_0_6_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_6300-51_0_6_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_6300-51_0_6_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_6300-51_0_6_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_6300-51_0_6_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_6300-51_0_6_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_6300-51_0_6_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_6300-51_0_6_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_6300-51_0_6_node_26 | 0.4 | n |  | TRUE
18 | bus_LV_6300-51_0_6_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_6300-51_0_6_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_6300-51_0_6_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_6300-51_0_6_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_6300-51_0_6_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_6300-51_0_6_node_46 | 0.4 | n |  | TRUE
24 | bus_LV_6300-51_0_6_node_43 | 0.4 | n |  | TRUE
25 | bus_LV_6300-51_0_6_node_36 | 0.4 | n |  | TRUE
26 | bus_LV_6300-51_0_6_node_38 | 0.4 | n |  | TRUE
27 | bus_LV_6300-51_0_6_node_35 | 0.4 | n |  | TRUE
28 | bus_LV_6300-51_0_6_node_37 | 0.4 | n |  | TRUE
29 | bus_LV_6300-51_0_6_node_42 | 0.4 | n |  | TRUE
30 | bus_LV_6300-51_0_6_node_39 | 0.4 | n |  | TRUE
31 | bus_LV_6300-51_0_6_node_40 | 0.4 | n |  | TRUE
32 | bus_LV_6300-51_0_6_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_6300-51_0_6_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_6300-51_0_6_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_6300-51_0_6_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_6300-51_0_6_node_41 | 0.4 | n |  | TRUE
37 | bus_LV_6300-51_0_6_node_44 | 0.4 | n |  | TRUE
38 | bus_LV_6300-51_0_6_node_45 | 0.4 | n |  | TRUE
39 | bus_LV_6300-51_0_6_node_16 | 0.4 | n |  | TRUE
40 | bus_LV_6300-51_0_6_node_17 | 0.4 | n |  | TRUE
41 | bus_LV_6300-51_0_6_node_18 | 0.4 | n |  | TRUE
42 | bus_LV_6300-51_0_6_node_19 | 0.4 | n |  | TRUE
43 | bus_LV_6300-51_0_6_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_6300-51_0_6_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_6300-51_0_6_node_21 | 0.4 | n |  | TRUE
46 | bus_MV_282_0_node_73 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6300-51_0_6_load_0 | 0 | 0.01172 | 0.0029372 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6300-51_0_6_load_1 | 1 | 0.01513 | 0.0037919 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6300-51_0_6_load_3 | 3 | 0.0074327 | 0.0018628 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6300-51_0_6_load_4 | 4 | 0.013386 | 0.0033549 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6300-51_0_6_load_5 | 5 | 0.013076 | 0.0032771 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6300-51_0_6_load_14 | 6 | 0.0094275 | 0.0023628 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6300-51_0_6_load_12 | 7 | 0.020099 | 0.0050372 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6300-51_0_6_load_29 | 8 | 0.020074 | 0.005031 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6300-51_0_6_load_15 | 9 | 0.013658 | 0.003423 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6300-51_0_6_load_11 | 10 | 0.016392 | 0.0041082 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6300-51_0_6_load_9 | 11 | 0.017603 | 0.0044117 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6300-51_0_6_load_6 | 12 | 0.037138 | 0.0093076 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6300-51_0_6_load_7 | 13 | 0.016431 | 0.0041179 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6300-51_0_6_load_8 | 14 | 0.025971 | 0.0065089 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6300-51_0_6_load_28 | 16 | 0.0096996 | 0.002431 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6300-51_0_6_load_26 | 17 | 0.022557 | 0.0056534 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6300-51_0_6_load_24 | 18 | 0.022043 | 0.0055245 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6300-51_0_6_load_20 | 20 | 0.025778 | 0.0064605 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6300-51_0_6_load_27 | 21 | 0.015314 | 0.0038382 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6300-51_0_6_load_13 | 22 | 0.014385 | 0.0036053 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6300-51_0_6_load_46 | 23 | 0.019731 | 0.0049451 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6300-51_0_6_load_43 | 24 | 0.037334 | 0.0093569 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6300-51_0_6_load_38 | 26 | 0.0068948 | 0.001728 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6300-51_0_6_load_37 | 28 | 0.0095607 | 0.0023961 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6300-51_0_6_load_42 | 29 | 0.0058637 | 0.0014696 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6300-51_0_6_load_30 | 32 | 0.014645 | 0.0036703 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6300-51_0_6_load_31 | 33 | 0.010168 | 0.0025484 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6300-51_0_6_load_32 | 34 | 0.013368 | 0.0033503 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6300-51_0_6_load_45 | 38 | 0.014195 | 0.0035577 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6300-51_0_6_load_17 | 40 | 0.0093577 | 0.0023453 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6300-51_0_6_load_18 | 41 | 0.020245 | 0.0050739 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6300-51_0_6_load_19 | 42 | 0.012861 | 0.0032233 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6300-51_0_6_load_25 | 43 | 0.026761 | 0.0067069 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6300-51_0_6_load_34 | 44 | 0.027586 | 0.0069137 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6300-51_0_6_line_0 |  | 0 | 1 | 0.0127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_6300-51_0_6_line_1 |  | 0 | 2 | 0.0073714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_6300-51_0_6_line_2 |  | 1 | 3 | 0.0048685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6300-51_0_6_line_3 |  | 2 | 4 | 0.031516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_6300-51_0_6_line_4 |  | 2 | 5 | 0.016107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_6300-51_0_6_line_5 |  | 3 | 6 | 0.0012214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6300-51_0_6_line_6 |  | 4 | 7 | 0.0014188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_6300-51_0_6_line_7 |  | 5 | 8 | 0.010606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_6300-51_0_6_line_8 |  | 6 | 9 | 0.012659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6300-51_0_6_line_9 |  | 7 | 10 | 0.03505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_6300-51_0_6_line_10 |  | 8 | 11 | 0.01931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_6300-51_0_6_line_11 |  | 9 | 39 | 0.012806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6300-51_0_6_line_12 |  | 10 | 22 | 0.036352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_6300-51_0_6_line_13 |  | 11 | 13 | 0.0035555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_6300-51_0_6_line_14 |  | 12 | 13 | 0.0061566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_6300-51_0_6_line_15 |  | 12 | 14 | 0.014025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6300-51_0_6_line_16 |  | 14 | 15 | 0.0035935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6300-51_0_6_line_17 |  | 15 | 16 | 0.0095365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6300-51_0_6_line_18 |  | 15 | 17 | 0.0171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6300-51_0_6_line_19 |  | 16 | 20 | 0.061071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6300-51_0_6_line_20 |  | 17 | 21 | 0.00074687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6300-51_0_6_line_21 |  | 18 | 19 | 0.068991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6300-51_0_6_line_22 |  | 19 | 45 | 0.02333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6300-51_0_6_line_23 |  | 20 | 45 | 0.03992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6300-51_0_6_line_24 |  | 22 | 23 | 0.10857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6300-51_0_6_line_25 |  | 22 | 24 | 0.083739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6300-51_0_6_line_26 |  | 23 | 31 | 0.021372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6300-51_0_6_line_27 |  | 24 | 36 | 0.051078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6300-51_0_6_line_28 |  | 25 | 26 | 0.0084266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6300-51_0_6_line_29 |  | 25 | 27 | 0.035259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6300-51_0_6_line_30 |  | 26 | 30 | 0.011544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6300-51_0_6_line_31 |  | 27 | 28 | 0.025351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6300-51_0_6_line_32 |  | 28 | 29 | 0.0083344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6300-51_0_6_line_33 |  | 30 | 31 | 0.023499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6300-51_0_6_line_34 |  | 32 | 33 | 0.011653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6300-51_0_6_line_35 |  | 32 | 34 | 0.021397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6300-51_0_6_line_36 |  | 33 | 35 | 0.027582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6300-51_0_6_line_37 |  | 35 | 36 | 0.03891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6300-51_0_6_line_38 |  | 36 | 37 | 0.005082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6300-51_0_6_line_39 |  | 37 | 38 | 0.027914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6300-51_0_6_line_40 |  | 39 | 40 | 0.06205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6300-51_0_6_line_41 |  | 39 | 41 | 0.070744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6300-51_0_6_line_42 |  | 39 | 42 | 0.069358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6300-51_0_6_line_43 |  | 39 | 43 | 0.10534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6300-51_0_6_line_44 |  | 41 | 44 | 0.0085509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6300-51_0_6_trafo_12 | 0.63 MVA 20/0.4 kV | 46 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2623949.9029 | 1095642.1374 | 2623953.2018 | 1095638.7356 | 2623959.4725 | 1095633.8309
1 | 2623944.7712 | 1095647.4292 | 2623949.9029 | 1095642.1374
2 | 2623959.4725 | 1095633.8309 | 2623963.3073 | 1095630.8314
3 | 2623944.7712 | 1095647.4292 | 2623951.9035 | 1095663.5877 | 2623956.9871 | 1095676.4751
4 | 2623944.7712 | 1095647.4292 | 2623931.6996 | 1095656.841
5 | 2623964.2693 | 1095630.079 | 2623963.3073 | 1095630.8314
6 | 2623956.9871 | 1095676.4751 | 2623957.5077 | 1095677.7949
7 | 2623923.0924 | 1095663.0384 | 2623931.6996 | 1095656.841
8 | 2623964.2693 | 1095630.079 | 2623974.2404 | 1095622.2799
9 | 2623957.5077 | 1095677.7949 | 2623957.9469 | 1095678.9082 | 2623960.275 | 1095705.3643 | 2623964.4283 | 1095711.3615
10 | 2623906.5676 | 1095673.0003 | 2623920.2327 | 1095665.0974 | 2623923.0924 | 1095663.0384
11 | 2623984.3275 | 1095614.39 | 2623974.2404 | 1095622.2799
12 | 2623979.1136 | 1095740.5454 | 2623966.9326 | 1095722.0657 | 2623970.226 | 1095719.7331 | 2623964.4283 | 1095711.3615
13 | 2623906.5676 | 1095673.0003 | 2623903.4897 | 1095674.7803
14 | 2623898.1602 | 1095677.8625 | 2623903.4897 | 1095674.7803
15 | 2623898.1602 | 1095677.8625 | 2623894.171 | 1095680.1696 | 2623886.7366 | 1095685.9499
16 | 2623883.8997 | 1095688.1556 | 2623886.7366 | 1095685.9499
17 | 2623883.8997 | 1095688.1556 | 2623875.8481 | 1095693.2662
18 | 2623883.8997 | 1095688.1556 | 2623891.5285 | 1095703.46
19 | 2623875.8481 | 1095693.2662 | 2623823.9995 | 1095660.9961
20 | 2623891.8617 | 1095704.1284 | 2623891.5285 | 1095703.46
21 | 2623780.7729 | 1095652.3561 | 2623791.5876 | 1095646.0173 | 2623837.0128 | 1095612.494
22 | 2623780.7729 | 1095652.3561 | 2623787.0141 | 1095656.8272 | 2623792.3321 | 1095671.5667
23 | 2623792.3321 | 1095671.5667 | 2623802.3465 | 1095667.8372 | 2623810.9121 | 1095664.191 | 2623822.7475 | 1095656.311 | 2623824.3556 | 1095657.0955 | 2623823.9995 | 1095660.9961
24 | 2623979.1136 | 1095740.5454 | 2624066.1823 | 1095805.4108
25 | 2623979.1136 | 1095740.5454 | 2623930.775 | 1095808.9238
26 | 2624080.5925 | 1095804.5673 | 2624074.9942 | 1095804.1005 | 2624071.6945 | 1095802.1532 | 2624071.301 | 1095807.6433 | 2624066.9337 | 1095807.3481 | 2624066.1823 | 1095805.4108
27 | 2623935.9787 | 1095858.5475 | 2623937.1509 | 1095822.4002 | 2623930.775 | 1095808.9238
28 | 2624102.205 | 1095768.7566 | 2624099.0403 | 1095775.7811 | 2624098.9253 | 1095776.494
29 | 2624103.5218 | 1095733.5326 | 2624102.96 | 1095752.1733 | 2624102.205 | 1095768.7566
30 | 2624097.0869 | 1095787.8907 | 2624098.9253 | 1095776.494
31 | 2624103.5218 | 1095733.5326 | 2624096.4172 | 1095749.6462 | 2624092.1767 | 1095756.1226
32 | 2624088.5774 | 1095763.6334 | 2624091.8506 | 1095756.6206 | 2624092.1767 | 1095756.1226
33 | 2624097.0869 | 1095787.8907 | 2624081.2482 | 1095803.2693 | 2624080.5925 | 1095804.5673
34 | 2623906.767 | 1095806.8636 | 2623911.6944 | 1095815.6523 | 2623910.7533 | 1095816.918
35 | 2623896.3032 | 1095788.2001 | 2623906.767 | 1095806.8636
36 | 2623901.051 | 1095841.5572 | 2623901.961 | 1095828.7431 | 2623910.7533 | 1095816.918
37 | 2623901.051 | 1095841.5572 | 2623929.3829 | 1095853.7413 | 2623935.9787 | 1095858.5475
38 | 2623939.9008 | 1095861.7534 | 2623939.1453 | 1095860.8611 | 2623935.9787 | 1095858.5475
39 | 2623939.9008 | 1095861.7534 | 2623961.1795 | 1095843.6166
40 | 2623984.3275 | 1095614.39 | 2623999.4895 | 1095597.8079 | 2624010.121 | 1095584.9765 | 2624025.6442 | 1095580.9356 | 2624031.681 | 1095577.6414
41 | 2623984.3275 | 1095614.39 | 2623980.8883 | 1095618.3452 | 2623980.2278 | 1095630.6711 | 2623991.8218 | 1095636.9533 | 2624004.1343 | 1095657.4568 | 2624003.6089 | 1095661.0566 | 2623994.0729 | 1095669.0115
42 | 2623984.3275 | 1095614.39 | 2623994.0267 | 1095606.1907 | 2623998.2703 | 1095606.4631 | 2624000.4606 | 1095610.8406 | 2624018.0011 | 1095651.1082 | 2624020.3149 | 1095653.8512
43 | 2623984.3275 | 1095614.39 | 2623920.659 | 1095530.4674
44 | 2623987.5067 | 1095674.4889 | 2623994.0729 | 1095669.0115

## bus_geodata
| x | y | coords
0 | 2623949.9029 | 1095642.1374
1 | 2623959.4725 | 1095633.8309
2 | 2623944.7712 | 1095647.4292
3 | 2623963.3073 | 1095630.8314
4 | 2623956.9871 | 1095676.4751
5 | 2623931.6996 | 1095656.841
6 | 2623964.2693 | 1095630.079
7 | 2623957.5077 | 1095677.7949
8 | 2623923.0924 | 1095663.0384
9 | 2623974.2404 | 1095622.2799
10 | 2623964.4283 | 1095711.3615
11 | 2623906.5676 | 1095673.0003
12 | 2623898.1602 | 1095677.8625
13 | 2623903.4897 | 1095674.7803
14 | 2623886.7366 | 1095685.9499
15 | 2623883.8997 | 1095688.1556
16 | 2623875.8481 | 1095693.2662
17 | 2623891.5285 | 1095703.46
18 | 2623837.0128 | 1095612.494
19 | 2623780.7729 | 1095652.3561
20 | 2623823.9995 | 1095660.9961
21 | 2623891.8617 | 1095704.1284
22 | 2623979.1136 | 1095740.5454
23 | 2624066.1823 | 1095805.4108
24 | 2623930.775 | 1095808.9238
25 | 2624102.205 | 1095768.7566
26 | 2624098.9253 | 1095776.494
27 | 2624103.5218 | 1095733.5326
28 | 2624092.1767 | 1095756.1226
29 | 2624088.5774 | 1095763.6334
30 | 2624097.0869 | 1095787.8907
31 | 2624080.5925 | 1095804.5673
32 | 2623906.767 | 1095806.8636
33 | 2623910.7533 | 1095816.918
34 | 2623896.3032 | 1095788.2001
35 | 2623901.051 | 1095841.5572
36 | 2623935.9787 | 1095858.5475
37 | 2623939.9008 | 1095861.7534
38 | 2623961.1795 | 1095843.6166
39 | 2623984.3275 | 1095614.39
40 | 2624031.681 | 1095577.6414
41 | 2623994.0729 | 1095669.0115
42 | 2624020.3149 | 1095653.8512
43 | 2623920.659 | 1095530.4674
44 | 2623987.5067 | 1095674.4889
45 | 2623792.3321 | 1095671.5667
46 | 2623944.7712 | 1095647.4292

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1