## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6300-80_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6300-80_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6300-80_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6300-80_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6300-80_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6300-80_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6300-80_0_3_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_6300-80_0_3_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_6300-80_0_3_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_6300-80_0_3_node_25 | 0.4 | n |  | TRUE
10 | bus_LV_6300-80_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_6300-80_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_6300-80_0_3_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_6300-80_0_3_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_6300-80_0_3_node_23 | 0.4 | n |  | TRUE
15 | bus_LV_6300-80_0_3_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_6300-80_0_3_node_24 | 0.4 | n |  | TRUE
17 | bus_LV_6300-80_0_3_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_6300-80_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_6300-80_0_3_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_6300-80_0_3_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_6300-80_0_3_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_6300-80_0_3_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_6300-80_0_3_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_6300-80_0_3_node_20 | 0.4 | n |  | TRUE
25 | bus_MV_0_node_11 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6300-80_0_3_load_0 | 0 | 0.0010307 | 0.00025833 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6300-80_0_3_load_1 | 1 | 0.00066665 | 0.00016708 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6300-80_0_3_load_9 | 6 | 0.00099349 | 0.00024899 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6300-80_0_3_load_10 | 7 | 0.001284 | 0.00032181 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6300-80_0_3_load_11 | 8 | 0.015126 | 0.0037909 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6300-80_0_3_load_25 | 9 | 0.0028655 | 0.00071816 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6300-80_0_3_load_12 | 12 | 0.0020242 | 0.0005073 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6300-80_0_3_load_23 | 14 | 0.024465 | 0.0061315 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6300-80_0_3_load_24 | 16 | 0.0024961 | 0.00062558 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6300-80_0_3_load_17 | 17 | 0.00087113 | 0.00021833 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6300-80_0_3_load_15 | 18 | 0.0010793 | 0.0002705 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6300-80_0_3_load_18 | 19 | 0.0056592 | 0.0014183 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6300-80_0_3_load_21 | 21 | 0.00067379 | 0.00016887 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6300-80_0_3_load_16 | 22 | 0.0069239 | 0.0017353 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6300-80_0_3_load_19 | 23 | 0.0026353 | 0.00066048 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6300-80_0_3_load_20 | 24 | 0.0033811 | 0.00084739 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6300-80_0_3_line_0 |  | 0 | 1 | 0.013288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6300-80_0_3_line_1 |  | 0 | 2 | 0.38543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_6300-80_0_3_line_2 |  | 1 | 3 | 0.0047225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6300-80_0_3_line_3 |  | 2 | 4 | 0.040611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_6300-80_0_3_line_4 |  | 2 | 5 | 0.86565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6300-80_0_3_line_5 |  | 3 | 6 | 0.0063858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6300-80_0_3_line_6 |  | 3 | 7 | 0.0085412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6300-80_0_3_line_7 |  | 4 | 8 | 0.11849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_6300-80_0_3_line_8 |  | 5 | 9 | 0.56264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6300-80_0_3_line_9 |  | 6 | 17 | 0.00059385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6300-80_0_3_line_10 |  | 7 | 18 | 0.0018434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6300-80_0_3_line_11 |  | 8 | 19 | 0.03884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6300-80_0_3_line_12 |  | 10 | 11 | 0.52622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6300-80_0_3_line_13 |  | 10 | 12 | 0.077694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6300-80_0_3_line_14 |  | 11 | 13 | 0.44064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6300-80_0_3_line_15 |  | 11 | 14 | 0.0098708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6300-80_0_3_line_16 |  | 12 | 20 | 0.0064692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6300-80_0_3_line_17 |  | 13 | 21 | 0.12905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6300-80_0_3_line_18 |  | 14 | 15 | 0.10101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6300-80_0_3_line_19 |  | 15 | 16 | 0.18026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6300-80_0_3_line_20 |  | 17 | 22 | 0.0024822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6300-80_0_3_line_21 |  | 18 | 20 | 0.016599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6300-80_0_3_line_22 |  | 19 | 23 | 0.016719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6300-80_0_3_line_23 |  | 23 | 24 | 0.0047226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6300-80_0_3_trafo_11 | 0.63 MVA 20/0.4 kV | 25 | 8 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27
0 | 2621551.4553 | 1095025.3049 | 2621560.2539 | 1095028.2651 | 2621563.9273 | 1095029.8594
1 | 2621326.0166 | 1094929.7351 | 2621326.0107 | 1094938.0616 | 2621324.6535 | 1094947.3393 | 2621292.2129 | 1095013.1375 | 2621292.8683 | 1095020.6436 | 2621300.4356 | 1095025.4058 | 2621315.7696 | 1095015.5655 | 2621328.4134 | 1095012.9639 | 2621333.5318 | 1095013.5599 | 2621338.3996 | 1095019.3688 | 2621349.0211 | 1095034.5582 | 2621352.959 | 1095038.2517 | 2621357.5254 | 1095039.4016 | 2621361.3711 | 1095038.4368 | 2621402.2027 | 1095023.15 | 2621411.0832 | 1095022.3474 | 2621420.7439 | 1095024.349 | 2621425.3201 | 1095022.7087 | 2621435.2039 | 1095014.1502 | 2621446.3548 | 1095008.7533 | 2621451.2931 | 1095007.6812 | 2621456.2244 | 1095008.6324 | 2621460.0677 | 1095008.3347 | 2621466.36 | 1095005.5665 | 2621472.7916 | 1095005.0334 | 2621487.3409 | 1095006.8967 | 2621516.909 | 1095013.6822 | 2621551.4553 | 1095025.3049
2 | 2621568.2593 | 1095031.7396 | 2621563.9273 | 1095029.8594
3 | 2621326.0166 | 1094929.7351 | 2621292.3239 | 1094952.5512
4 | 2620610.8791 | 1094993.8972 | 2620635.9021 | 1094988.9237 | 2620707.1109 | 1094972.4345 | 2620804.3808 | 1094957.9694 | 2620846.4923 | 1094957.7798 | 2620861.5816 | 1094958.1427 | 2620926.2913 | 1094953.1063 | 2620949.5359 | 1094945.0265 | 2621007.9423 | 1094939.3579 | 2621026.3296 | 1094944.8129 | 2621046.3578 | 1094943.926 | 2621080.3705 | 1094933.6272 | 2621108.878 | 1094933.7259 | 2621125.7965 | 1094929.3489 | 2621137.4908 | 1094914.6374 | 2621162.1872 | 1094892.3784 | 2621204.0361 | 1094883.2191 | 2621237.3807 | 1094871.3735 | 2621254.5224 | 1094865.2857 | 2621314.3252 | 1094852.688 | 2621338.0215 | 1094846.3899 | 2621322.5024 | 1094864.745 | 2621318.2953 | 1094878.1928 | 2621323.0482 | 1094885.8689 | 2621332.0154 | 1094891.2919 | 2621337.9541 | 1094901.0399 | 2621344.4777 | 1094916.2595 | 2621326.0166 | 1094929.7351
5 | 2621568.2593 | 1095031.7396 | 2621574.111 | 1095034.2963
6 | 2621568.2593 | 1095031.7396 | 2621564.382 | 1095039.35
7 | 2621292.3239 | 1094952.5512 | 2621289.4189 | 1094965.8479 | 2621282.2119 | 1094977.6844 | 2621267.7127 | 1094994.7203 | 2621257.4369 | 1095006.9018 | 2621249.5922 | 1095021.682 | 2621237.1652 | 1095055.4449 | 2621237.1652 | 1095055.4449
8 | 2620248.6911 | 1094910.7299 | 2620236.9602 | 1094923.0862 | 2620224.5531 | 1094936.1517 | 2620199.327 | 1094962.7261 | 2620190.1507 | 1094980.3826 | 2620192.3067 | 1094996.0088 | 2620210.1628 | 1095012.3319 | 2620234.8386 | 1095030.1006 | 2620265.7992 | 1095035.4951 | 2620305.3999 | 1095035.4379 | 2620338.3363 | 1095040.6726 | 2620366.1333 | 1095044.6007 | 2620387.5095 | 1095038.947 | 2620403.0111 | 1095022.5461 | 2620423.2765 | 1094992.3985 | 2620444.6782 | 1094988.4348 | 2620485.4001 | 1094993.6853 | 2620557.2776 | 1094996.9956 | 2620610.8791 | 1094993.8972
9 | 2621574.6552 | 1095034.534 | 2621574.111 | 1095034.2963
10 | 2621563.5452 | 1095040.9925 | 2621564.382 | 1095039.35
11 | 2621237.1652 | 1095055.4449 | 2621253.8805 | 1095044.8422 | 2621266.622 | 1095030.6867
12 | 2621099.662 | 1095277.47 | 2621095.5594 | 1095276.6221 | 2621088.8023 | 1095275.0757 | 2621087.3149 | 1095272.8805 | 2621088.3483 | 1095269.738 | 2621091.3149 | 1095265.3238 | 2621133.2827 | 1095250.1392 | 2621174.3803 | 1095240.1989 | 2621190.7287 | 1095239.1441 | 2621231.8375 | 1095223.8459 | 2621263.4853 | 1095218.2645 | 2621288.2811 | 1095205.022 | 2621300.1186 | 1095204.7188 | 2621313.6607 | 1095210.9471 | 2621329.6503 | 1095215.0496 | 2621380.5558 | 1095196.1738 | 2621385.6316 | 1095195.6246 | 2621396.1128 | 1095199.9414 | 2621421.11 | 1095200.0292 | 2621439.8955 | 1095188.8673 | 2621456.3227 | 1095187.48 | 2621467.7591 | 1095173.5131 | 2621487.13 | 1095172.1362 | 2621494.3701 | 1095161.9343 | 2621507.5624 | 1095155.3107 | 2621534.7725 | 1095149.6261 | 2621557.8337 | 1095136.4675
13 | 2621557.8337 | 1095136.4675 | 2621548.7213 | 1095121.8612 | 2621550.255 | 1095106.5588 | 2621552.3531 | 1095080.6084 | 2621558.4207 | 1095062.5353
14 | 2621099.662 | 1095277.47 | 2621103.1841 | 1095278.1937 | 2621117.9972 | 1095277.5447 | 2621131.1489 | 1095280.2027 | 2621153.5795 | 1095289.8521 | 2621164.4263 | 1095287.0439 | 2621181.0754 | 1095290.8148 | 2621198.6999 | 1095292.5325 | 2621240.7208 | 1095308.7759 | 2621256.8827 | 1095305.6418 | 2621287.6697 | 1095306.861 | 2621292.6486 | 1095305.1886 | 2621301.3319 | 1095311.889 | 2621309.6163 | 1095306.4152 | 2621325.6113 | 1095304.4924 | 2621367.5113 | 1095313.1435 | 2621385.339 | 1095312.1055 | 2621409.5977 | 1095321.6066 | 2621427.1624 | 1095318.2666 | 2621445.871 | 1095320.0333 | 2621454.4428 | 1095318.774 | 2621472.2994 | 1095322.7277 | 2621492.9125 | 1095318.2092 | 2621515.1718 | 1095319.1437 | 2621525.2714 | 1095319.5685
15 | 2621099.662 | 1095277.47 | 2621090.0794 | 1095279.8381
16 | 2621560.4797 | 1095056.4025 | 2621558.4207 | 1095062.5353
17 | 2621525.2714 | 1095319.5685 | 2621539.8665 | 1095327.9688 | 2621568.1361 | 1095329.136 | 2621585.8455 | 1095324.3185 | 2621611.9408 | 1095329.1468 | 2621638.6142 | 1095323.8942 | 2621650.2525 | 1095326.0594
18 | 2620991.2817 | 1095291.6476 | 2621000.1835 | 1095293.4903 | 2621020.94 | 1095287.7589 | 2621046.77 | 1095282.1118 | 2621050.4677 | 1095283.5698 | 2621060.1439 | 1095281.0019 | 2621069.711 | 1095280.8571 | 2621090.0794 | 1095279.8381
19 | 2620991.2817 | 1095291.6476 | 2620978.1615 | 1095293.3144 | 2620952.9953 | 1095301.9545 | 2620939.2979 | 1095302.5299 | 2620900.8555 | 1095308.6789 | 2620890.1353 | 1095313.0333 | 2620880.9822 | 1095318.9717 | 2620875.1472 | 1095319.5742 | 2620849.5914 | 1095333.4605 | 2620832.533 | 1095338.3936 | 2620828.1154 | 1095339.0455 | 2620820.2766 | 1095341.2088
20 | 2621576.9298 | 1095035.5278 | 2621574.6552 | 1095034.534
21 | 2621560.4797 | 1095056.4025 | 2621559.1402 | 1095049.6388 | 2621563.5452 | 1095040.9925
22 | 2621277.3074 | 1095017.833 | 2621269.3718 | 1095027.6318 | 2621266.622 | 1095030.6867
23 | 2621280.2795 | 1095014.163 | 2621277.3074 | 1095017.833

## bus_geodata
| x | y | coords
0 | 2621551.4553 | 1095025.3049
1 | 2621563.9273 | 1095029.8594
2 | 2621326.0166 | 1094929.7351
3 | 2621568.2593 | 1095031.7396
4 | 2621292.3239 | 1094952.5512
5 | 2620610.8791 | 1094993.8972
6 | 2621574.111 | 1095034.2963
7 | 2621564.382 | 1095039.35
8 | 2621237.1652 | 1095055.4449
9 | 2620248.6911 | 1094910.7299
10 | 2621557.8337 | 1095136.4675
11 | 2621099.662 | 1095277.47
12 | 2621558.4207 | 1095062.5353
13 | 2621525.2714 | 1095319.5685
14 | 2621090.0794 | 1095279.8381
15 | 2620991.2817 | 1095291.6476
16 | 2620820.2766 | 1095341.2088
17 | 2621574.6552 | 1095034.534
18 | 2621563.5452 | 1095040.9925
19 | 2621266.622 | 1095030.6867
20 | 2621560.4797 | 1095056.4025
21 | 2621650.2525 | 1095326.0594
22 | 2621576.9298 | 1095035.5278
23 | 2621277.3074 | 1095017.833
24 | 2621280.2795 | 1095014.163
25 | 2621237.1652 | 1095055.4449

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1