## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_768-3_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_768-3_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_768-3_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_768-3_0_7_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_768-3_0_7_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_768-3_0_7_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_768-3_0_7_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_768-3_0_7_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_768-3_0_7_node_66 | 0.4 | n |  | TRUE
9 | bus_LV_768-3_0_7_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_768-3_0_7_node_85 | 0.4 | n |  | TRUE
11 | bus_LV_768-3_0_7_node_45 | 0.4 | n |  | TRUE
12 | bus_LV_768-3_0_7_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_768-3_0_7_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_768-3_0_7_node_43 | 0.4 | n |  | TRUE
15 | bus_LV_768-3_0_7_node_84 | 0.4 | n |  | TRUE
16 | bus_LV_768-3_0_7_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_768-3_0_7_node_93 | 0.4 | n |  | TRUE
18 | bus_LV_768-3_0_7_node_86 | 0.4 | n |  | TRUE
19 | bus_LV_768-3_0_7_node_31 | 0.4 | n |  | TRUE
20 | bus_LV_768-3_0_7_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_768-3_0_7_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_768-3_0_7_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_768-3_0_7_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_768-3_0_7_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_768-3_0_7_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_768-3_0_7_node_37 | 0.4 | n |  | TRUE
27 | bus_LV_768-3_0_7_node_50 | 0.4 | n |  | TRUE
28 | bus_LV_768-3_0_7_node_82 | 0.4 | n |  | TRUE
29 | bus_LV_768-3_0_7_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_768-3_0_7_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_768-3_0_7_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_768-3_0_7_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_768-3_0_7_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_768-3_0_7_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_768-3_0_7_node_40 | 0.4 | n |  | TRUE
36 | bus_LV_768-3_0_7_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_768-3_0_7_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_768-3_0_7_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_768-3_0_7_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_768-3_0_7_node_87 | 0.4 | n |  | TRUE
41 | bus_LV_768-3_0_7_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_768-3_0_7_node_83 | 0.4 | n |  | TRUE
43 | bus_LV_768-3_0_7_node_91 | 0.4 | n |  | TRUE
44 | bus_LV_768-3_0_7_node_28 | 0.4 | n |  | TRUE
45 | bus_LV_768-3_0_7_node_90 | 0.4 | n |  | TRUE
46 | bus_LV_768-3_0_7_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_768-3_0_7_node_39 | 0.4 | n |  | TRUE
48 | bus_LV_768-3_0_7_node_51 | 0.4 | n |  | TRUE
49 | bus_LV_768-3_0_7_node_49 | 0.4 | n |  | TRUE
50 | bus_LV_768-3_0_7_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_768-3_0_7_node_33 | 0.4 | n |  | TRUE
52 | bus_LV_768-3_0_7_node_34 | 0.4 | n |  | TRUE
53 | bus_LV_768-3_0_7_node_35 | 0.4 | n |  | TRUE
54 | bus_LV_768-3_0_7_node_36 | 0.4 | n |  | TRUE
55 | bus_LV_768-3_0_7_node_53 | 0.4 | n |  | TRUE
56 | bus_LV_768-3_0_7_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_768-3_0_7_node_54 | 0.4 | n |  | TRUE
58 | bus_LV_768-3_0_7_node_46 | 0.4 | n |  | TRUE
59 | bus_LV_768-3_0_7_node_64 | 0.4 | n |  | TRUE
60 | bus_LV_768-3_0_7_node_58 | 0.4 | n |  | TRUE
61 | bus_LV_768-3_0_7_node_89 | 0.4 | n |  | TRUE
62 | bus_LV_768-3_0_7_node_65 | 0.4 | n |  | TRUE
63 | bus_LV_768-3_0_7_node_81 | 0.4 | n |  | TRUE
64 | bus_LV_768-3_0_7_node_57 | 0.4 | n |  | TRUE
65 | bus_LV_768-3_0_7_node_69 | 0.4 | n |  | TRUE
66 | bus_LV_768-3_0_7_node_78 | 0.4 | n |  | TRUE
67 | bus_LV_768-3_0_7_node_79 | 0.4 | n |  | TRUE
68 | bus_LV_768-3_0_7_node_48 | 0.4 | n |  | TRUE
69 | bus_LV_768-3_0_7_node_72 | 0.4 | n |  | TRUE
70 | bus_LV_768-3_0_7_node_67 | 0.4 | n |  | TRUE
71 | bus_LV_768-3_0_7_node_68 | 0.4 | n |  | TRUE
72 | bus_LV_768-3_0_7_node_52 | 0.4 | n |  | TRUE
73 | bus_LV_768-3_0_7_node_88 | 0.4 | n |  | TRUE
74 | bus_LV_768-3_0_7_node_55 | 0.4 | n |  | TRUE
75 | bus_LV_768-3_0_7_node_59 | 0.4 | n |  | TRUE
76 | bus_LV_768-3_0_7_node_60 | 0.4 | n |  | TRUE
77 | bus_LV_768-3_0_7_node_61 | 0.4 | n |  | TRUE
78 | bus_LV_768-3_0_7_node_62 | 0.4 | n |  | TRUE
79 | bus_LV_768-3_0_7_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_768-3_0_7_node_71 | 0.4 | n |  | TRUE
81 | bus_LV_768-3_0_7_node_76 | 0.4 | n |  | TRUE
82 | bus_LV_768-3_0_7_node_80 | 0.4 | n |  | TRUE
83 | bus_LV_768-3_0_7_node_74 | 0.4 | n |  | TRUE
84 | bus_LV_768-3_0_7_node_73 | 0.4 | n |  | TRUE
85 | bus_MV_118_0_node_163 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_768-3_0_7_load_0 | 0 | 0.0060712 | 0.0015216 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_768-3_0_7_load_1 | 1 | 0.010937 | 0.002741 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_768-3_0_7_load_3 | 3 | 0.0023521 | 0.00058949 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_768-3_0_7_load_6 | 5 | 0.0029187 | 0.0007315 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_768-3_0_7_load_66 | 8 | 0.0046495 | 0.0011653 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_768-3_0_7_load_7 | 9 | 0.022283 | 0.0055847 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_768-3_0_7_load_85 | 10 | 0.052332 | 0.013116 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_768-3_0_7_load_45 | 11 | 0.0027242 | 0.00068275 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_768-3_0_7_load_43 | 14 | 0.0083083 | 0.0020823 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_768-3_0_7_load_93 | 17 | 0.046408 | 0.011631 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_768-3_0_7_load_86 | 18 | 0.027391 | 0.0068648 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_768-3_0_7_load_13 | 20 | 0.0015633 | 0.00039179 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_768-3_0_7_load_14 | 21 | 0.00072349 | 0.00018132 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_768-3_0_7_load_15 | 22 | 0.011964 | 0.0029984 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_768-3_0_7_load_29 | 24 | 0.0057818 | 0.0014491 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_768-3_0_7_load_50 | 27 | 0.00095493 | 0.00023933 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_768-3_0_7_load_82 | 28 | 0.0093296 | 0.0023382 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_768-3_0_7_load_18 | 29 | 0.0036412 | 0.00091256 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_768-3_0_7_load_20 | 31 | 0.0037391 | 0.00093711 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_768-3_0_7_load_22 | 33 | 0.0025382 | 0.00063614 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_768-3_0_7_load_26 | 34 | 0.0026565 | 0.00066577 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_768-3_0_7_load_41 | 37 | 0.0018081 | 0.00045315 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_768-3_0_7_load_23 | 38 | 0.0020861 | 0.00052283 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_768-3_0_7_load_87 | 40 | 0.0032988 | 0.00082675 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_768-3_0_7_load_91 | 43 | 0.00048943 | 0.00012266 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_768-3_0_7_load_90 | 45 | 0.0018261 | 0.00045766 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_768-3_0_7_load_38 | 46 | 0.010082 | 0.0025267 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_768-3_0_7_load_51 | 48 | 0.0003614 | 9.0576e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_768-3_0_7_load_32 | 50 | 0.0050443 | 0.0012642 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_768-3_0_7_load_34 | 52 | 0.0040085 | 0.0010046 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_768-3_0_7_load_35 | 53 | 0.0024317 | 0.00060943 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_768-3_0_7_load_36 | 54 | 0.00075468 | 0.00018914 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_768-3_0_7_load_53 | 55 | 0.0020923 | 0.00052438 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_768-3_0_7_load_54 | 57 | 0.0016801 | 0.00042107 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_768-3_0_7_load_46 | 58 | 0.002969 | 0.00074411 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_768-3_0_7_load_64 | 59 | 0.0092048 | 0.0023069 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_768-3_0_7_load_89 | 61 | 0.018041 | 0.0045216 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_768-3_0_7_load_65 | 62 | 0.013518 | 0.003388 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_768-3_0_7_load_81 | 63 | 0.048746 | 0.012217 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_768-3_0_7_load_78 | 66 | 0.0020624 | 0.00051689 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_768-3_0_7_load_79 | 67 | 0.00072732 | 0.00018228 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_768-3_0_7_load_72 | 69 | 0.035507 | 0.008899 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_768-3_0_7_load_67 | 70 | 0.02309 | 0.0057868 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_768-3_0_7_load_52 | 72 | 0.013741 | 0.0034438 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_768-3_0_7_load_88 | 73 | 0.0020386 | 0.00051091 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_768-3_0_7_load_55 | 74 | 0.038971 | 0.0097671 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_768-3_0_7_load_59 | 75 | 0.018855 | 0.0047256 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_768-3_0_7_load_60 | 76 | 0.018626 | 0.0046681 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_768-3_0_7_load_62 | 78 | 0.011402 | 0.0028577 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_768-3_0_7_load_63 | 79 | 0.030542 | 0.0076547 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_768-3_0_7_load_80 | 82 | 0.019529 | 0.0048945 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_768-3_0_7_load_73 | 84 | 0.012272 | 0.0030756 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 25 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_768-3_0_7_line_0 |  | 0 | 1 | 0.023481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_768-3_0_7_line_1 |  | 0 | 2 | 0.011264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_768-3_0_7_line_2 |  | 1 | 3 | 0.034587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_768-3_0_7_line_3 |  | 2 | 4 | 0.051749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_768-3_0_7_line_4 |  | 3 | 5 | 0.0022885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_768-3_0_7_line_5 |  | 4 | 7 | 0.036824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_768-3_0_7_line_6 |  | 4 | 9 | 0.024759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_768-3_0_7_line_7 |  | 5 | 10 | 0.0021131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_768-3_0_7_line_8 |  | 6 | 7 | 0.032212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_768-3_0_7_line_9 |  | 6 | 8 | 0.01922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_768-3_0_7_line_10 |  | 7 | 11 | 0.023495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_768-3_0_7_line_11 |  | 10 | 12 | 0.03885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_768-3_0_7_line_12 |  | 11 | 13 | 0.0050476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_768-3_0_7_line_13 |  | 12 | 15 | 0.073137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_768-3_0_7_line_14 |  | 12 | 16 | 0.0084124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_768-3_0_7_line_15 |  | 13 | 14 | 0.02048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_768-3_0_7_line_16 |  | 15 | 18 | 0.027697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_768-3_0_7_line_17 |  | 15 | 19 | 0.010705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_768-3_0_7_line_18 |  | 16 | 17 | 0.009608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_768-3_0_7_line_19 |  | 18 | 42 | 0.038919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_768-3_0_7_line_20 |  | 19 | 28 | 0.0063793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_768-3_0_7_line_21 |  | 19 | 25 | 0.083964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_768-3_0_7_line_22 |  | 20 | 21 | 0.013021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_768-3_0_7_line_23 |  | 20 | 22 | 0.016512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_768-3_0_7_line_24 |  | 21 | 23 | 0.019474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_768-3_0_7_line_25 |  | 23 | 24 | 0.023005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_768-3_0_7_line_26 |  | 23 | 25 | 0.048271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_768-3_0_7_line_27 |  | 24 | 26 | 0.059603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_768-3_0_7_line_28 |  | 25 | 27 | 0.024025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_768-3_0_7_line_29 |  | 26 | 46 | 0.015703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_768-3_0_7_line_30 |  | 26 | 47 | 0.017084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_768-3_0_7_line_31 |  | 27 | 48 | 0.030514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_768-3_0_7_line_32 |  | 28 | 49 | 0.013903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_768-3_0_7_line_33 |  | 29 | 30 | 0.01841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_768-3_0_7_line_34 |  | 29 | 31 | 0.015344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_768-3_0_7_line_35 |  | 30 | 32 | 0.015867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_768-3_0_7_line_36 |  | 30 | 33 | 0.015804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_768-3_0_7_line_37 |  | 32 | 34 | 0.025276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_768-3_0_7_line_38 |  | 33 | 35 | 0.005354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_768-3_0_7_line_39 |  | 34 | 36 | 0.061111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_768-3_0_7_line_40 |  | 35 | 37 | 0.0089874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_768-3_0_7_line_41 |  | 36 | 44 | 0.12477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_768-3_0_7_line_42 |  | 37 | 66 | 0.0094404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_768-3_0_7_line_43 |  | 38 | 39 | 0.0041941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_768-3_0_7_line_44 |  | 38 | 40 | 0.065869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_768-3_0_7_line_45 |  | 39 | 41 | 0.031195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_768-3_0_7_line_46 |  | 40 | 42 | 0.006883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_768-3_0_7_line_47 |  | 41 | 43 | 0.015196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_768-3_0_7_line_48 |  | 44 | 45 | 0.017912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_768-3_0_7_line_49 |  | 46 | 59 | 0.0062103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_768-3_0_7_line_50 |  | 47 | 60 | 0.025475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_768-3_0_7_line_51 |  | 47 | 61 | 0.025312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_768-3_0_7_line_52 |  | 48 | 72 | 0.0022798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_768-3_0_7_line_53 |  | 49 | 56 | 0.050881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_768-3_0_7_line_54 |  | 50 | 51 | 0.02223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_768-3_0_7_line_55 |  | 50 | 52 | 0.020215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_768-3_0_7_line_56 |  | 51 | 53 | 0.019409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_768-3_0_7_line_57 |  | 51 | 54 | 0.014696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_768-3_0_7_line_58 |  | 53 | 55 | 0.0058351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_768-3_0_7_line_59 |  | 54 | 56 | 0.023831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_768-3_0_7_line_60 |  | 55 | 57 | 0.0050339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_768-3_0_7_line_61 |  | 56 | 58 | 0.011648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_768-3_0_7_line_62 |  | 57 | 73 | 0.004845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_768-3_0_7_line_63 |  | 59 | 62 | 0.016446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_768-3_0_7_line_64 |  | 60 | 63 | 0.0068511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_768-3_0_7_line_65 |  | 60 | 64 | 0.04274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_768-3_0_7_line_66 |  | 61 | 65 | 0.0098274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_768-3_0_7_line_67 |  | 62 | 78 | 0.017093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_768-3_0_7_line_68 |  | 64 | 74 | 0.026969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_768-3_0_7_line_69 |  | 65 | 80 | 0.003852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_768-3_0_7_line_70 |  | 65 | 71 | 0.012809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_768-3_0_7_line_71 |  | 66 | 67 | 0.0036278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_768-3_0_7_line_72 |  | 67 | 73 | 0.0019024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_768-3_0_7_line_73 |  | 68 | 69 | 0.002837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_768-3_0_7_line_74 |  | 68 | 70 | 0.018105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_768-3_0_7_line_75 |  | 70 | 71 | 0.024706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_768-3_0_7_line_76 |  | 75 | 76 | 0.038847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_768-3_0_7_line_77 |  | 75 | 77 | 0.0052773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_768-3_0_7_line_78 |  | 76 | 78 | 0.020654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_768-3_0_7_line_79 |  | 77 | 79 | 0.023809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_768-3_0_7_line_80 |  | 80 | 81 | 0.020121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_768-3_0_7_line_81 |  | 81 | 83 | 0.06125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_768-3_0_7_line_82 |  | 81 | 82 | 0.032675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_768-3_0_7_line_83 |  | 83 | 84 | 0.046568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_768-3_0_7_trafo_30 | 0.63 MVA 20/0.4 kV | 85 | 25 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27
0 | 2618278.8863 | 1171195.891 | 2618273.501 | 1171196.9017 | 2618257.8978 | 1171198.8999 | 2618255.6306 | 1171199.027
1 | 2618289.9415 | 1171193.7389 | 2618287.8977 | 1171194.1996 | 2618278.8863 | 1171195.891
2 | 2618255.6306 | 1171199.027 | 2618243.5986 | 1171199.7014 | 2618238.0684 | 1171199.5957 | 2618232.9971 | 1171199.5026 | 2618221.0751 | 1171198.992
3 | 2618292.154 | 1171230.8978 | 2618307.5974 | 1171221.0508 | 2618306.4501 | 1171218.5016 | 2618304.2476 | 1171210.8021 | 2618300.3991 | 1171206.0547 | 2618294.4489 | 1171200.6561 | 2618291.6495 | 1171198.0463 | 2618290.7369 | 1171196.3093 | 2618290.2059 | 1171194.8403 | 2618289.9415 | 1171193.7389
4 | 2618218.7887 | 1171198.8941 | 2618221.0751 | 1171198.992
5 | 2618292.154 | 1171230.8978 | 2618290.5035 | 1171235.3506 | 2618289.5473 | 1171240.4058 | 2618289.8003 | 1171245.2534 | 2618290.754 | 1171248.6025 | 2618291.8039 | 1171250.4511 | 2618293.1991 | 1171252.0005 | 2618294.9539 | 1171253.4955 | 2618298.4519 | 1171255.2514 | 2618300.5535 | 1171255.9026 | 2618304.5526 | 1171256.4039 | 2618306.5189 | 1171256.2654
6 | 2618292.154 | 1171230.8978 | 2618288.3486 | 1171232.0979 | 2618282.2146 | 1171231.8681 | 2618279.2012 | 1171231.7033 | 2618267.8074 | 1171233.9468
7 | 2618216.6775 | 1171198.8037 | 2618218.7887 | 1171198.8941
8 | 2618322.6979 | 1171233.4363 | 2618322.7982 | 1171240.6959 | 2618321.9484 | 1171245.9515 | 2618319.1493 | 1171250.801 | 2618315.9514 | 1171253.4482 | 2618311.8995 | 1171255.2479 | 2618306.5189 | 1171256.2654
9 | 2618322.6979 | 1171233.4363 | 2618324.852 | 1171234.3989 | 2618341.6957 | 1171235.152
10 | 2618306.5189 | 1171256.2654 | 2618305.1975 | 1171258.1512 | 2618302.301 | 1171259.7988 | 2618284.7807 | 1171263.2644
11 | 2618178.1982 | 1171193.9897 | 2618182.702 | 1171194.548 | 2618190.4535 | 1171196.2056 | 2618193.1978 | 1171196.8031 | 2618196.799 | 1171197.3476 | 2618212.0481 | 1171198.6054 | 2618216.6775 | 1171198.8037
12 | 2618279.8291 | 1171264.2439 | 2618284.7807 | 1171263.2644
13 | 2618163.6039 | 1171122.7208 | 2618163.6995 | 1171123.9995 | 2618167.2987 | 1171153.1028 | 2618168.8872 | 1171164.1132 | 2618170.0605 | 1171170.7534 | 2618170.3994 | 1171172.4998 | 2618171.5042 | 1171176.5051 | 2618175.4967 | 1171186.8001 | 2618178.1982 | 1171193.9897
14 | 2618171.8273 | 1171196.1605 | 2618178.6988 | 1171195.4031 | 2618178.1982 | 1171193.9897
15 | 2618279.8291 | 1171264.2439 | 2618280.4325 | 1171264.557 | 2618291.4686 | 1171270.1934 | 2618298.3706 | 1171272.8856
16 | 2618163.6039 | 1171122.7208 | 2618168.9015 | 1171123.8706 | 2618182.7763 | 1171126.8696 | 2618190.8536 | 1171126.6257
17 | 2618162.8023 | 1171112.0463 | 2618162.9862 | 1171114.4703 | 2618163.6039 | 1171122.7208
18 | 2618176.016 | 1171204.8108 | 2618171.8273 | 1171196.1605
19 | 2618213.7388 | 1171110.0657 | 2618213.8973 | 1171125.9298 | 2618190.8536 | 1171126.6257
20 | 2618162.8023 | 1171112.0463 | 2618159.3978 | 1171112.2028 | 2618156.7014 | 1171113.4508
21 | 2618162.8023 | 1171112.0463 | 2618163.2297 | 1171104.7661 | 2618163.5039 | 1171100.0979 | 2618164.8043 | 1171092.498 | 2618166.8645 | 1171084.0444 | 2618172.5137 | 1171065.0407 | 2618173.302 | 1171062.3973 | 2618167.1586 | 1171062.6344 | 2618153.8085 | 1171063.1611 | 2618152.1025 | 1171063.2227 | 2618152.1627 | 1171053.4068 | 2618152.1715 | 1171053.0066 | 2618152.2069 | 1171051.4392
22 | 2618191.7907 | 1171019.2332 | 2618203.6755 | 1171013.914
23 | 2618218.7403 | 1171007.1547 | 2618218.2337 | 1171007.3829 | 2618214.1969 | 1171009.205 | 2618203.6755 | 1171013.914
24 | 2618174.0582 | 1171027.2818 | 2618182.247 | 1171023.5046 | 2618191.7907 | 1171019.2332
25 | 2618174.0582 | 1171027.2818 | 2618173.3515 | 1171025.7011 | 2618170.399 | 1171020.5563 | 2618168.2041 | 1171017.8483 | 2618165.7024 | 1171015.4062 | 2618159.6039 | 1171010.8966 | 2618158.9062 | 1171010.5586
26 | 2618174.0582 | 1171027.2818 | 2618176.1817 | 1171033.3579 | 2618176.3025 | 1171033.903 | 2618176.6299 | 1171036.9278 | 2618176.8011 | 1171038.4957 | 2618176.7006 | 1171041.3969 | 2618175.5985 | 1171051.6988 | 2618169.5021 | 1171051.6026 | 2618167.1001 | 1171051.6064 | 2618152.2069 | 1171051.4392
27 | 2618106.7144 | 1170985.4245 | 2618108.3024 | 1170988.9978 | 2618109.7042 | 1170990.9029 | 2618112.9105 | 1170993.1026 | 2618116.0023 | 1170995.2018 | 2618120.7993 | 1170997.5063 | 2618121.3189 | 1170997.6969 | 2618127.5005 | 1171000.0055 | 2618146.8994 | 1171005.2999 | 2618152.4008 | 1171007.4065 | 2618158.9062 | 1171010.5586
28 | 2618152.2069 | 1171051.4392 | 2618152.3572 | 1171044.703 | 2618152.4975 | 1171038.7559 | 2618152.6209 | 1171033.3425 | 2618152.7006 | 1171029.7631 | 2618152.2401 | 1171027.7162 | 2618152.0606 | 1171027.5489
29 | 2618106.7144 | 1170985.4245 | 2618109.0038 | 1170984.6977 | 2618113.5996 | 1170982.6994 | 2618119.699 | 1170979.3049 | 2618120.8209 | 1170978.63
30 | 2618089.9442 | 1170988.6536 | 2618092.4997 | 1170988.5056 | 2618095.8973 | 1170988.1045 | 2618104.3024 | 1170986.1954 | 2618106.7144 | 1170985.4245
31 | 2618152.0606 | 1171027.5489 | 2618148.3879 | 1171024.125 | 2618141.1751 | 1171021.3241 | 2618138.0794 | 1171020.5255 | 2618137.0009 | 1171020.4778 | 2618133.0002 | 1171020.4769 | 2618123.5223 | 1171020.4706 | 2618123.5223 | 1171020.4706
32 | 2618146.5372 | 1171122.9361 | 2618147.7569 | 1171121.7948 | 2618156.7014 | 1171113.4508
33 | 2618045.7435 | 1171216.136 | 2618045.2014 | 1171220.9035 | 2618045.697 | 1171223.9954 | 2618046.7025 | 1171225.3991 | 2618048.1985 | 1171226.5042 | 2618054.7771 | 1171228.5668
34 | 2618068.2043 | 1171235.8022 | 2618058.4008 | 1171229.703 | 2618054.7771 | 1171228.5668
35 | 2618045.7435 | 1171216.136 | 2618032.9974 | 1171216.8982 | 2618029.8535 | 1171216.8999
36 | 2618045.7435 | 1171216.136 | 2618047.1025 | 1171201.6995 | 2618046.9401 | 1171200.4059
37 | 2618029.8535 | 1171216.8999 | 2618029.7525 | 1171219.9456 | 2618028.9561 | 1171242.1596
38 | 2618046.2732 | 1171195.0936 | 2618046.9401 | 1171200.4059
39 | 2618028.4871 | 1171302.7949 | 2618027.4504 | 1171301.6023 | 2618026.9526 | 1171299.2551 | 2618026.9488 | 1171297.9545 | 2618028.317 | 1171259.9838 | 2618028.9561 | 1171242.1596
40 | 2618046.2732 | 1171195.0936 | 2618055.2606 | 1171195.0652
41 | 2618122.5505 | 1171330.6356 | 2618116.2359 | 1171329.416 | 2618109.0717 | 1171328.3717 | 2618104.4634 | 1171327.0016 | 2618099.6837 | 1171326.6426 | 2618095.2364 | 1171327.652 | 2618091.1329 | 1171328.8292 | 2618085.6632 | 1171331.5363 | 2618080.8763 | 1171333.5674 | 2618076.4281 | 1171334.9214 | 2618072.502 | 1171335.5878 | 2618069.0849 | 1171334.8994 | 2618065.5015 | 1171333.5213 | 2618061.2394 | 1171331.463 | 2618054.0737 | 1171328.3844 | 2618048.1053 | 1171326.4878 | 2618043.8386 | 1171325.9636 | 2618037.6876 | 1171326.2898 | 2618032.3939 | 1171326.4407 | 2618027.559 | 1171326.6264 | 2618028.9808 | 1171324.3961 | 2618031.221 | 1171319.6338 | 2618032.2572 | 1171315.8905 | 2618032.604 | 1171312.4899 | 2618032.2746 | 1171310.0988 | 2618030.6995 | 1171307.3038 | 2618030.1489 | 1171304.7008 | 2618028.4871 | 1171302.7949
42 | 2618055.2606 | 1171195.0652 | 2618058.9025 | 1171195.0537 | 2618063.9973 | 1171194.9467 | 2618064.6987 | 1171194.9087
43 | 2618278.8661 | 1171072.4773 | 2618274.6744 | 1171072.6195
44 | 2618220.638 | 1171110.2867 | 2618274.6744 | 1171072.6195
45 | 2618278.8661 | 1171072.4773 | 2618282.7985 | 1171072.3003 | 2618290.649 | 1171071.646 | 2618294.5539 | 1171070.4461 | 2618297.7503 | 1171068.2992 | 2618298.9242 | 1171067.1355 | 2618299.2624 | 1171066.6029 | 2618301.0474 | 1171068.2536 | 2618301.252 | 1171068.899 | 2618301.6007 | 1171072.4463 | 2618301.815 | 1171074.926
46 | 2618220.638 | 1171110.2867 | 2618213.7388 | 1171110.0657
47 | 2618301.815 | 1171074.926 | 2618302.8025 | 1171084.7562 | 2618304.2327 | 1171089.8742
48 | 2618122.5505 | 1171330.6356 | 2618127.0039 | 1171327.5808 | 2618131.2845 | 1171323.5027 | 2618135.9113 | 1171318.7587
49 | 2618120.8209 | 1170978.63 | 2618126.1426 | 1170975.4288
50 | 2618089.9442 | 1170988.6536 | 2618090.1018 | 1170979.505 | 2618091.299 | 1170973.1053 | 2618093.7044 | 1170966.8983 | 2618095.5022 | 1170964.3024
51 | 2618089.9442 | 1170988.6536 | 2618064.6391 | 1170989.2503
52 | 2618123.4543 | 1171022.7493 | 2618123.505 | 1171021.1486 | 2618123.5223 | 1171020.4706
53 | 2618146.5372 | 1171122.9361 | 2618145.302 | 1171124.1552 | 2618127.3471 | 1171139.898 | 2618109.4538 | 1171153.0064 | 2618106.604 | 1171154.3985
54 | 2618105.3026 | 1171192.903 | 2618104.2022 | 1171215.1061
55 | 2618103.2016 | 1171235.2959 | 2618104.2022 | 1171215.1061
56 | 2618105.3026 | 1171192.903 | 2618085.9155 | 1171193.8326
57 | 2618105.3026 | 1171192.903 | 2618105.799 | 1171178.2155
58 | 2618085.9155 | 1171193.8326 | 2618080.0871 | 1171194.112
59 | 2618106.604 | 1171154.3985 | 2618105.799 | 1171178.2155
60 | 2618080.0871 | 1171194.112 | 2618075.0591 | 1171194.3531
61 | 2618106.604 | 1171154.3985 | 2618105.2486 | 1171154.9058 | 2618101.8496 | 1171155.7516 | 2618095.1667 | 1171156.2039
62 | 2618075.0591 | 1171194.3531 | 2618074.1038 | 1171194.3989 | 2618070.2208 | 1171194.6094
63 | 2618140.0415 | 1170966.6433 | 2618132.4971 | 1170971.6062 | 2618126.1426 | 1170975.4288
64 | 2618095.5022 | 1170964.3024 | 2618090.5417 | 1170969.028
65 | 2618095.5022 | 1170964.3024 | 2618103.4224 | 1170955.7441 | 2618121.1038 | 1170936.9989 | 2618124.8179 | 1170933.1303
66 | 2618054.8145 | 1170989.4819 | 2618064.6391 | 1170989.2503
67 | 2618140.0415 | 1170966.6433 | 2618150.9005 | 1170959.4999 | 2618154.3098 | 1170957.2314
68 | 2618124.8179 | 1170933.1303 | 2618130.5017 | 1170938.2055 | 2618131.187 | 1170939.2414 | 2618131.6591 | 1170939.9655 | 2618131.9104 | 1170940.3442 | 2618137.4999 | 1170948.7986 | 2618143.1363 | 1170945.2629
69 | 2618054.8145 | 1170989.4819 | 2618054.2828 | 1170985.6673
70 | 2618041.97 | 1170989.6991 | 2618049.2987 | 1170989.5988 | 2618054.8145 | 1170989.4819
71 | 2618064.6987 | 1171194.9087 | 2618068.3212 | 1171194.7123
72 | 2618070.2208 | 1171194.6094 | 2618068.3212 | 1171194.7123
73 | 2618044.6109 | 1171032.5176 | 2618041.7653 | 1171032.509
74 | 2618041.7653 | 1171032.509 | 2618041.8519 | 1171014.4045
75 | 2618041.97 | 1170989.6991 | 2618041.8519 | 1171014.4045
76 | 2618203.8462 | 1170924.2698 | 2618171.5047 | 1170945.7899
77 | 2618208.2738 | 1170921.3982 | 2618204.1042 | 1170924.0981 | 2618203.8462 | 1170924.2698
78 | 2618171.5047 | 1170945.7899 | 2618154.3098 | 1170957.2314
79 | 2618208.2738 | 1170921.3982 | 2618218.7013 | 1170938.8052 | 2618220.6968 | 1170941.7016
80 | 2618047.5544 | 1170966.7042 | 2618047.797 | 1170967.4053 | 2618053.2975 | 1170982.5961 | 2618054.2828 | 1170985.6673
81 | 2618047.5544 | 1170966.7042 | 2618041.4035 | 1170948.9991 | 2618040.9029 | 1170947.5857 | 2618032.074 | 1170922.391 | 2618031.4975 | 1170920.7551 | 2618030.9985 | 1170918.7971 | 2618031.0378 | 1170915.8957 | 2618031.1008 | 1170915.2956 | 2618031.7023 | 1170913.6966 | 2618033.0002 | 1170911.9996 | 2618034.7026 | 1170910.604 | 2618035.0014 | 1170910.4604 | 2618035.599 | 1170910.1509
82 | 2618047.5544 | 1170966.7042 | 2618044.0708 | 1170967.6832 | 2618018.4994 | 1170974.8325 | 2618017.7032 | 1170975.0524 | 2618016.0868 | 1170975.5042
83 | 2618035.599 | 1170910.1509 | 2618037.1006 | 1170909.3995 | 2618045.8994 | 1170906.3021 | 2618056.0986 | 1170903.0977 | 2618067.2015 | 1170899.4958 | 2618079.5143 | 1170894.746

## bus_geodata
| x | y | coords
0 | 2618278.8863 | 1171195.891
1 | 2618255.6306 | 1171199.027
2 | 2618289.9415 | 1171193.7389
3 | 2618221.0751 | 1171198.992
4 | 2618292.154 | 1171230.8978
5 | 2618218.7887 | 1171198.8941
6 | 2618322.6979 | 1171233.4363
7 | 2618306.5189 | 1171256.2654
8 | 2618341.6957 | 1171235.152
9 | 2618267.8074 | 1171233.9468
10 | 2618216.6775 | 1171198.8037
11 | 2618284.7807 | 1171263.2644
12 | 2618178.1982 | 1171193.9897
13 | 2618279.8291 | 1171264.2439
14 | 2618298.3706 | 1171272.8856
15 | 2618163.6039 | 1171122.7208
16 | 2618171.8273 | 1171196.1605
17 | 2618176.016 | 1171204.8108
18 | 2618190.8536 | 1171126.6257
19 | 2618162.8023 | 1171112.0463
20 | 2618203.6755 | 1171013.914
21 | 2618191.7907 | 1171019.2332
22 | 2618218.7403 | 1171007.1547
23 | 2618174.0582 | 1171027.2818
24 | 2618158.9062 | 1171010.5586
25 | 2618152.2069 | 1171051.4392
26 | 2618106.7144 | 1170985.4245
27 | 2618152.0606 | 1171027.5489
28 | 2618156.7014 | 1171113.4508
29 | 2618054.7771 | 1171228.5668
30 | 2618045.7435 | 1171216.136
31 | 2618068.2043 | 1171235.8022
32 | 2618029.8535 | 1171216.8999
33 | 2618046.9401 | 1171200.4059
34 | 2618028.9561 | 1171242.1596
35 | 2618046.2732 | 1171195.0936
36 | 2618028.4871 | 1171302.7949
37 | 2618055.2606 | 1171195.0652
38 | 2618274.6744 | 1171072.6195
39 | 2618278.8661 | 1171072.4773
40 | 2618220.638 | 1171110.2867
41 | 2618301.815 | 1171074.926
42 | 2618213.7388 | 1171110.0657
43 | 2618304.2327 | 1171089.8742
44 | 2618122.5505 | 1171330.6356
45 | 2618135.9113 | 1171318.7587
46 | 2618120.8209 | 1170978.63
47 | 2618089.9442 | 1170988.6536
48 | 2618123.5223 | 1171020.4706
49 | 2618146.5372 | 1171122.9361
50 | 2618104.2022 | 1171215.1061
51 | 2618105.3026 | 1171192.903
52 | 2618103.2016 | 1171235.2959
53 | 2618085.9155 | 1171193.8326
54 | 2618105.799 | 1171178.2155
55 | 2618080.0871 | 1171194.112
56 | 2618106.604 | 1171154.3985
57 | 2618075.0591 | 1171194.3531
58 | 2618095.1667 | 1171156.2039
59 | 2618126.1426 | 1170975.4288
60 | 2618095.5022 | 1170964.3024
61 | 2618064.6391 | 1170989.2503
62 | 2618140.0415 | 1170966.6433
63 | 2618090.5417 | 1170969.028
64 | 2618124.8179 | 1170933.1303
65 | 2618054.8145 | 1170989.4819
66 | 2618064.6987 | 1171194.9087
67 | 2618068.3212 | 1171194.7123
68 | 2618041.7653 | 1171032.509
69 | 2618044.6109 | 1171032.5176
70 | 2618041.8519 | 1171014.4045
71 | 2618041.97 | 1170989.6991
72 | 2618123.4543 | 1171022.7493
73 | 2618070.2208 | 1171194.6094
74 | 2618143.1363 | 1170945.2629
75 | 2618203.8462 | 1170924.2698
76 | 2618171.5047 | 1170945.7899
77 | 2618208.2738 | 1170921.3982
78 | 2618154.3098 | 1170957.2314
79 | 2618220.6968 | 1170941.7016
80 | 2618054.2828 | 1170985.6673
81 | 2618047.5544 | 1170966.7042
82 | 2618016.0868 | 1170975.5042
83 | 2618035.599 | 1170910.1509
84 | 2618079.5143 | 1170894.746
85 | 2618152.1025 | 1171063.2227

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1