## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_939-46_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_939-46_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_939-46_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_939-46_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_939-46_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_939-46_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_939-46_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_939-46_0_3_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_939-46_0_3_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_939-46_0_3_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_939-46_0_3_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_939-46_0_3_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_939-46_0_3_node_54 | 0.4 | n |  | TRUE
13 | bus_LV_939-46_0_3_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_939-46_0_3_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_939-46_0_3_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_939-46_0_3_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_939-46_0_3_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_939-46_0_3_node_60 | 0.4 | n |  | TRUE
19 | bus_LV_939-46_0_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_939-46_0_3_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_939-46_0_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_939-46_0_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_939-46_0_3_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_939-46_0_3_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_939-46_0_3_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_939-46_0_3_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_939-46_0_3_node_56 | 0.4 | n |  | TRUE
28 | bus_LV_939-46_0_3_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_939-46_0_3_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_939-46_0_3_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_939-46_0_3_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_939-46_0_3_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_939-46_0_3_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_939-46_0_3_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_939-46_0_3_node_36 | 0.4 | n |  | TRUE
36 | bus_LV_939-46_0_3_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_939-46_0_3_node_39 | 0.4 | n |  | TRUE
38 | bus_LV_939-46_0_3_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_939-46_0_3_node_40 | 0.4 | n |  | TRUE
40 | bus_LV_939-46_0_3_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_939-46_0_3_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_939-46_0_3_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_939-46_0_3_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_939-46_0_3_node_53 | 0.4 | n |  | TRUE
45 | bus_LV_939-46_0_3_node_51 | 0.4 | n |  | TRUE
46 | bus_LV_939-46_0_3_node_44 | 0.4 | n |  | TRUE
47 | bus_LV_939-46_0_3_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_939-46_0_3_node_46 | 0.4 | n |  | TRUE
49 | bus_LV_939-46_0_3_node_47 | 0.4 | n |  | TRUE
50 | bus_LV_939-46_0_3_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_939-46_0_3_node_55 | 0.4 | n |  | TRUE
52 | bus_LV_939-46_0_3_node_58 | 0.4 | n |  | TRUE
53 | bus_LV_939-46_0_3_node_57 | 0.4 | n |  | TRUE
54 | bus_LV_939-46_0_3_node_49 | 0.4 | n |  | TRUE
55 | bus_LV_939-46_0_3_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_939-46_0_3_node_52 | 0.4 | n |  | TRUE
57 | bus_LV_939-46_0_3_node_59 | 0.4 | n |  | TRUE
58 | bus_MV_93_0_node_121 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_939-46_0_3_load_0 | 0 | 0.012714 | 0.0031866 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_939-46_0_3_load_3 | 3 | 0.0015205 | 0.00038108 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_939-46_0_3_load_4 | 4 | 0.017284 | 0.0043319 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_939-46_0_3_load_6 | 6 | 0.0029418 | 0.00073727 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_939-46_0_3_load_11 | 7 | 0.0051795 | 0.0012981 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_939-46_0_3_load_20 | 9 | 0.006529 | 0.0016363 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_939-46_0_3_load_54 | 12 | 0.002289 | 0.00057367 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_939-46_0_3_load_21 | 13 | 0.0070703 | 0.001772 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_939-46_0_3_load_7 | 14 | 0.01165 | 0.0029198 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_939-46_0_3_load_14 | 15 | 0.01477 | 0.0037018 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_939-46_0_3_load_60 | 18 | 0.011555 | 0.002896 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_939-46_0_3_load_17 | 20 | 0.0087855 | 0.0022019 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_939-46_0_3_load_18 | 21 | 0.013186 | 0.0033048 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_939-46_0_3_load_19 | 22 | 0.0076243 | 0.0019108 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_939-46_0_3_load_25 | 24 | 0.0063962 | 0.001603 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_939-46_0_3_load_26 | 25 | 0.0060549 | 0.0015175 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_939-46_0_3_load_22 | 26 | 0.0076951 | 0.0019286 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_939-46_0_3_load_56 | 27 | 0.0018474 | 0.00046301 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_939-46_0_3_load_27 | 28 | 0.0050183 | 0.0012577 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_939-46_0_3_load_28 | 29 | 0.010438 | 0.002616 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_939-46_0_3_load_29 | 30 | 0.0064695 | 0.0016214 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_939-46_0_3_load_30 | 31 | 0.01168 | 0.0029272 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_939-46_0_3_load_33 | 34 | 0.0067901 | 0.0017018 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_939-46_0_3_load_34 | 36 | 0.007569 | 0.001897 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_939-46_0_3_load_37 | 38 | 0.0073486 | 0.0018417 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_939-46_0_3_load_40 | 39 | 0.0050312 | 0.0012609 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_939-46_0_3_load_38 | 40 | 0.0018373 | 0.00046047 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_939-46_0_3_load_41 | 41 | 0.010251 | 0.0025691 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_939-46_0_3_load_42 | 42 | 0.0020794 | 0.00052114 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_939-46_0_3_load_43 | 43 | 0.001833 | 0.00045941 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_939-46_0_3_load_53 | 44 | 0.0017547 | 0.00043976 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_939-46_0_3_load_51 | 45 | 0.0016873 | 0.00042288 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_939-46_0_3_load_44 | 46 | 0.0016431 | 0.00041179 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_939-46_0_3_load_45 | 47 | 0.0020293 | 0.00050858 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_939-46_0_3_load_46 | 48 | 0.0021996 | 0.00055128 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_939-46_0_3_load_47 | 49 | 0.0018036 | 0.00045203 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_939-46_0_3_load_48 | 50 | 0.0021099 | 0.0005288 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_939-46_0_3_load_55 | 51 | 0.0038151 | 0.00095616 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_939-46_0_3_load_58 | 52 | 0.0020931 | 0.00052459 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_939-46_0_3_load_57 | 53 | 0.0017968 | 0.00045032 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_939-46_0_3_load_49 | 54 | 0.0058583 | 0.0014682 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_939-46_0_3_load_50 | 55 | 0.0019413 | 0.00048654 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_939-46_0_3_load_52 | 56 | 0.0020548 | 0.00051499 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_939-46_0_3_load_59 | 57 | 0.0066879 | 0.0016761 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_939-46_0_3_line_0 |  | 0 | 1 | 0.00068139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_939-46_0_3_line_1 |  | 0 | 2 | 0.020866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_939-46_0_3_line_2 |  | 1 | 3 | 0.027289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_939-46_0_3_line_3 |  | 1 | 4 | 0.021067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_939-46_0_3_line_4 |  | 2 | 5 | 0.004853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_939-46_0_3_line_5 |  | 2 | 6 | 0.045628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_939-46_0_3_line_6 |  | 3 | 7 | 0.00086719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_939-46_0_3_line_7 |  | 4 | 8 | 0.0067613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_939-46_0_3_line_8 |  | 5 | 9 | 0.014269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_939-46_0_3_line_9 |  | 6 | 10 | 0.0097721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_939-46_0_3_line_10 |  | 7 | 11 | 0.045586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_939-46_0_3_line_11 |  | 8 | 12 | 0.039892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_939-46_0_3_line_12 |  | 9 | 13 | 0.013055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_939-46_0_3_line_13 |  | 10 | 14 | 0.018713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_939-46_0_3_line_14 |  | 11 | 17 | 0.054917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_939-46_0_3_line_15 |  | 12 | 27 | 0.00064149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_939-46_0_3_line_16 |  | 13 | 26 | 0.022533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_939-46_0_3_line_17 |  | 15 | 16 | 0.011576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_939-46_0_3_line_18 |  | 16 | 19 | 0.013801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_939-46_0_3_line_19 |  | 17 | 18 | 0.013771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_939-46_0_3_line_20 |  | 19 | 20 | 0.032471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_939-46_0_3_line_21 |  | 20 | 21 | 0.023104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_939-46_0_3_line_22 |  | 21 | 22 | 0.018196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_939-46_0_3_line_23 |  | 22 | 23 | 0.032979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_939-46_0_3_line_24 |  | 23 | 24 | 0.020209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_939-46_0_3_line_25 |  | 23 | 25 | 0.0035042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_939-46_0_3_line_26 |  | 24 | 28 | 0.0283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_939-46_0_3_line_27 |  | 25 | 26 | 0.012811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_939-46_0_3_line_28 |  | 27 | 53 | 0.0016112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_939-46_0_3_line_29 |  | 28 | 29 | 0.00074103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_939-46_0_3_line_30 |  | 29 | 30 | 0.00026224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_939-46_0_3_line_31 |  | 30 | 31 | 0.017208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_939-46_0_3_line_32 |  | 31 | 32 | 0.0067725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_939-46_0_3_line_33 |  | 32 | 33 | 0.006571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_939-46_0_3_line_34 |  | 32 | 34 | 0.014065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_939-46_0_3_line_35 |  | 33 | 35 | 0.022817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_939-46_0_3_line_36 |  | 33 | 36 | 0.025111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_939-46_0_3_line_37 |  | 34 | 37 | 0.017048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_939-46_0_3_line_38 |  | 35 | 38 | 0.020024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_939-46_0_3_line_39 |  | 37 | 39 | 0.026709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_939-46_0_3_line_40 |  | 38 | 40 | 0.022531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_939-46_0_3_line_41 |  | 39 | 41 | 0.0011063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_939-46_0_3_line_42 |  | 41 | 42 | 0.02072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_939-46_0_3_line_43 |  | 42 | 43 | 0.0056494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_939-46_0_3_line_44 |  | 43 | 44 | 0.0041478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_939-46_0_3_line_45 |  | 44 | 45 | 0.004981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_939-46_0_3_line_46 |  | 45 | 54 | 0.0024393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_939-46_0_3_line_47 |  | 46 | 47 | 0.0080324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_939-46_0_3_line_48 |  | 46 | 48 | 0.010614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_939-46_0_3_line_49 |  | 47 | 49 | 0.0057512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_939-46_0_3_line_50 |  | 48 | 50 | 0.00067435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_939-46_0_3_line_51 |  | 49 | 51 | 0.0018205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_939-46_0_3_line_52 |  | 50 | 52 | 0.0017838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_939-46_0_3_line_53 |  | 52 | 53 | 0.000599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_939-46_0_3_line_54 |  | 54 | 55 | 0.0032239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_939-46_0_3_line_55 |  | 55 | 56 | 0.0057144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_939-46_0_3_line_56 |  | 56 | 57 | 0.2257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_939-46_0_3_trafo_22 | 0.63 MVA 20/0.4 kV | 58 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2613550.4829 | 1180624.5036 | 2613550.8058 | 1180623.9035
1 | 2613540.5978 | 1180642.8792 | 2613550.4829 | 1180624.5036
2 | 2613550.8058 | 1180623.9035 | 2613562.9754 | 1180599.4783
3 | 2613550.8058 | 1180623.9035 | 2613553.9396 | 1180626.1562 | 2613555.6915 | 1180628.2723 | 2613556.9156 | 1180630.6985 | 2613557.932 | 1180633.8024 | 2613559.9144 | 1180642.0444
4 | 2613538.4037 | 1180647.2098 | 2613540.5978 | 1180642.8792
5 | 2613540.5978 | 1180642.8792 | 2613501.0109 | 1180620.1898
6 | 2613562.9754 | 1180599.4783 | 2613563.3621 | 1180598.7021
7 | 2613560.0749 | 1180648.8038 | 2613559.9144 | 1180642.0444
8 | 2613538.4037 | 1180647.2098 | 2613531.7779 | 1180659.8474
9 | 2613497.2339 | 1180611.8437 | 2613497.4679 | 1180616.4799 | 2613501.0109 | 1180620.1898
10 | 2613583.757 | 1180557.9328 | 2613574.6736 | 1180575.9993 | 2613563.3621 | 1180598.7021
11 | 2613560.0749 | 1180648.8038 | 2613560.0855 | 1180654.2511 | 2613560.8245 | 1180658.4438 | 2613562.4926 | 1180663.817 | 2613562.5853 | 1180666.7409 | 2613560.9321 | 1180675.097 | 2613558.7577 | 1180688.0334
12 | 2613525.7159 | 1180671.4097 | 2613531.7779 | 1180659.8474
13 | 2613497.2339 | 1180611.8437 | 2613506.3829 | 1180595.5198
14 | 2613583.757 | 1180557.9328 | 2613585.3298 | 1180554.8125 | 2613603.5325 | 1180563.7359 | 2613601.1977 | 1180569.5225 | 2613622.9599 | 1180578.2095 | 2613624.3334 | 1180578.7573
15 | 2613558.7577 | 1180688.0334 | 2613558.6514 | 1180688.666
16 | 2613525.7159 | 1180671.4097 | 2613515.2528 | 1180691.3661
17 | 2613432.8248 | 1180626.963 | 2613438.6803 | 1180616.9776
18 | 2613432.8248 | 1180626.963 | 2613425.6347 | 1180638.753
19 | 2613619.1798 | 1180591.53 | 2613624.3334 | 1180578.7573
20 | 2613425.6347 | 1180638.753 | 2613445.1748 | 1180657.5618 | 2613448.8707 | 1180661.4286
21 | 2613464.8344 | 1180678.1301 | 2613448.8707 | 1180661.4286
22 | 2613464.8344 | 1180678.1301 | 2613465.9074 | 1180679.2526 | 2613470.6107 | 1180683.2096 | 2613479.2259 | 1180689.2055
23 | 2613507.6771 | 1180705.8153 | 2613500.7885 | 1180702.3425 | 2613484.344 | 1180692.7675 | 2613479.2259 | 1180689.2055
24 | 2613507.6771 | 1180705.8153 | 2613498.5078 | 1180723.8243
25 | 2613507.6771 | 1180705.8153 | 2613509.3043 | 1180702.7118
26 | 2613485.6674 | 1180749.0432 | 2613498.5078 | 1180723.8243
27 | 2613509.3043 | 1180702.7118 | 2613515.2528 | 1180691.3661
28 | 2613558.6514 | 1180688.666 | 2613558.3843 | 1180690.2549
29 | 2613485.3312 | 1180749.7036 | 2613485.6674 | 1180749.0432
30 | 2613485.2122 | 1180749.9373 | 2613485.3312 | 1180749.7036
31 | 2613477.4043 | 1180765.2724 | 2613485.2122 | 1180749.9373
32 | 2613474.3314 | 1180771.3076 | 2613477.4043 | 1180765.2724
33 | 2613474.3314 | 1180771.3076 | 2613471.2941 | 1180777.1371
34 | 2613474.3314 | 1180771.3076 | 2613480.8201 | 1180772.6339 | 2613488.1919 | 1180773.6534
35 | 2613461.8005 | 1180797.8932 | 2613471.2941 | 1180777.1371
36 | 2613471.2941 | 1180777.1371 | 2613462.0305 | 1180773.6146 | 2613456.5576 | 1180772.2906 | 2613451.2352 | 1180771.9785 | 2613447.0302 | 1180772.5076
37 | 2613505.1693 | 1180775.1453 | 2613491.524 | 1180774.1142 | 2613488.1919 | 1180773.6534
38 | 2613461.8005 | 1180797.8932 | 2613479.5725 | 1180807.1201
39 | 2613505.1693 | 1180775.1453 | 2613531.8385 | 1180773.6932
40 | 2613479.5725 | 1180807.1201 | 2613485.4557 | 1180810.1746 | 2613494.8569 | 1180817.0326 | 2613497.9141 | 1180820.0065
41 | 2613531.8385 | 1180773.6932 | 2613532.9431 | 1180773.6331
42 | 2613532.9431 | 1180773.6331 | 2613539.8768 | 1180773.2556 | 2613547.706 | 1180772.7618 | 2613553.637 | 1180772.6955
43 | 2613559.286 | 1180772.6324 | 2613553.637 | 1180772.6955
44 | 2613563.4335 | 1180772.586 | 2613559.286 | 1180772.6324
45 | 2613568.4142 | 1180772.532 | 2613565.0886 | 1180772.5675 | 2613563.4335 | 1180772.586
46 | 2613570.8534 | 1180772.5059 | 2613568.4142 | 1180772.532
47 | 2613556.1183 | 1180703.7369 | 2613554.7868 | 1180711.6582
48 | 2613556.1183 | 1180703.7369 | 2613557.8776 | 1180693.2697
49 | 2613554.7868 | 1180711.6582 | 2613553.8335 | 1180717.3298
50 | 2613557.9894 | 1180692.6047 | 2613557.8776 | 1180693.2697
51 | 2613553.5317 | 1180719.1252 | 2613553.8335 | 1180717.3298
52 | 2613558.2851 | 1180690.8456 | 2613557.9894 | 1180692.6047
53 | 2613558.3843 | 1180690.2549 | 2613558.2851 | 1180690.8456
54 | 2613570.8534 | 1180772.5059 | 2613574.0771 | 1180772.4715
55 | 2613579.7911 | 1180772.4105 | 2613574.0771 | 1180772.4715
56 | 2613579.7911 | 1180772.4105 | 2613805.4939 | 1180771.5387

## bus_geodata
| x | y | coords
0 | 2613550.4829 | 1180624.5036
1 | 2613550.8058 | 1180623.9035
2 | 2613540.5978 | 1180642.8792
3 | 2613562.9754 | 1180599.4783
4 | 2613559.9144 | 1180642.0444
5 | 2613538.4037 | 1180647.2098
6 | 2613501.0109 | 1180620.1898
7 | 2613563.3621 | 1180598.7021
8 | 2613560.0749 | 1180648.8038
9 | 2613531.7779 | 1180659.8474
10 | 2613497.2339 | 1180611.8437
11 | 2613583.757 | 1180557.9328
12 | 2613558.7577 | 1180688.0334
13 | 2613525.7159 | 1180671.4097
14 | 2613506.3829 | 1180595.5198
15 | 2613438.6803 | 1180616.9776
16 | 2613432.8248 | 1180626.963
17 | 2613624.3334 | 1180578.7573
18 | 2613619.1798 | 1180591.53
19 | 2613425.6347 | 1180638.753
20 | 2613448.8707 | 1180661.4286
21 | 2613464.8344 | 1180678.1301
22 | 2613479.2259 | 1180689.2055
23 | 2613507.6771 | 1180705.8153
24 | 2613498.5078 | 1180723.8243
25 | 2613509.3043 | 1180702.7118
26 | 2613515.2528 | 1180691.3661
27 | 2613558.6514 | 1180688.666
28 | 2613485.6674 | 1180749.0432
29 | 2613485.3312 | 1180749.7036
30 | 2613485.2122 | 1180749.9373
31 | 2613477.4043 | 1180765.2724
32 | 2613474.3314 | 1180771.3076
33 | 2613471.2941 | 1180777.1371
34 | 2613488.1919 | 1180773.6534
35 | 2613461.8005 | 1180797.8932
36 | 2613447.0302 | 1180772.5076
37 | 2613505.1693 | 1180775.1453
38 | 2613479.5725 | 1180807.1201
39 | 2613531.8385 | 1180773.6932
40 | 2613497.9141 | 1180820.0065
41 | 2613532.9431 | 1180773.6331
42 | 2613553.637 | 1180772.6955
43 | 2613559.286 | 1180772.6324
44 | 2613563.4335 | 1180772.586
45 | 2613568.4142 | 1180772.532
46 | 2613556.1183 | 1180703.7369
47 | 2613554.7868 | 1180711.6582
48 | 2613557.8776 | 1180693.2697
49 | 2613553.8335 | 1180717.3298
50 | 2613557.9894 | 1180692.6047
51 | 2613553.5317 | 1180719.1252
52 | 2613558.2851 | 1180690.8456
53 | 2613558.3843 | 1180690.2549
54 | 2613570.8534 | 1180772.5059
55 | 2613574.0771 | 1180772.4715
56 | 2613579.7911 | 1180772.4105
57 | 2613805.4939 | 1180771.5387
58 | 2613507.6771 | 1180705.8153

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1