## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_941-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_941-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_941-5_0_4_node_148 | 0.4 | n |  | TRUE
3 | bus_LV_941-5_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_941-5_0_4_node_140 | 0.4 | n |  | TRUE
5 | bus_LV_941-5_0_4_node_146 | 0.4 | n |  | TRUE
6 | bus_LV_941-5_0_4_node_147 | 0.4 | n |  | TRUE
7 | bus_LV_941-5_0_4_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_941-5_0_4_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_941-5_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_941-5_0_4_node_166 | 0.4 | n |  | TRUE
11 | bus_LV_941-5_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_941-5_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_941-5_0_4_node_167 | 0.4 | n |  | TRUE
14 | bus_LV_941-5_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_941-5_0_4_node_43 | 0.4 | n |  | TRUE
16 | bus_LV_941-5_0_4_node_42 | 0.4 | n |  | TRUE
17 | bus_LV_941-5_0_4_node_60 | 0.4 | n |  | TRUE
18 | bus_LV_941-5_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_941-5_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_941-5_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_941-5_0_4_node_38 | 0.4 | n |  | TRUE
22 | bus_LV_941-5_0_4_node_40 | 0.4 | n |  | TRUE
23 | bus_LV_941-5_0_4_node_39 | 0.4 | n |  | TRUE
24 | bus_LV_941-5_0_4_node_49 | 0.4 | n |  | TRUE
25 | bus_LV_941-5_0_4_node_37 | 0.4 | n |  | TRUE
26 | bus_LV_941-5_0_4_node_41 | 0.4 | n |  | TRUE
27 | bus_LV_941-5_0_4_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_941-5_0_4_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_941-5_0_4_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_941-5_0_4_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_941-5_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_941-5_0_4_node_154 | 0.4 | n |  | TRUE
33 | bus_LV_941-5_0_4_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_941-5_0_4_node_153 | 0.4 | n |  | TRUE
35 | bus_LV_941-5_0_4_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_941-5_0_4_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_941-5_0_4_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_941-5_0_4_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_941-5_0_4_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_941-5_0_4_node_156 | 0.4 | n |  | TRUE
41 | bus_LV_941-5_0_4_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_941-5_0_4_node_155 | 0.4 | n |  | TRUE
43 | bus_LV_941-5_0_4_node_158 | 0.4 | n |  | TRUE
44 | bus_LV_941-5_0_4_node_46 | 0.4 | n |  | TRUE
45 | bus_LV_941-5_0_4_node_48 | 0.4 | n |  | TRUE
46 | bus_LV_941-5_0_4_node_44 | 0.4 | n |  | TRUE
47 | bus_LV_941-5_0_4_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_941-5_0_4_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_941-5_0_4_node_30 | 0.4 | n |  | TRUE
50 | bus_LV_941-5_0_4_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_941-5_0_4_node_152 | 0.4 | n |  | TRUE
52 | bus_LV_941-5_0_4_node_32 | 0.4 | n |  | TRUE
53 | bus_LV_941-5_0_4_node_33 | 0.4 | n |  | TRUE
54 | bus_LV_941-5_0_4_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_941-5_0_4_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_941-5_0_4_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_941-5_0_4_node_50 | 0.4 | n |  | TRUE
58 | bus_LV_941-5_0_4_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_941-5_0_4_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_941-5_0_4_node_77 | 0.4 | n |  | TRUE
61 | bus_LV_941-5_0_4_node_69 | 0.4 | n |  | TRUE
62 | bus_LV_941-5_0_4_node_51 | 0.4 | n |  | TRUE
63 | bus_LV_941-5_0_4_node_59 | 0.4 | n |  | TRUE
64 | bus_LV_941-5_0_4_node_61 | 0.4 | n |  | TRUE
65 | bus_LV_941-5_0_4_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_941-5_0_4_node_52 | 0.4 | n |  | TRUE
67 | bus_LV_941-5_0_4_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_941-5_0_4_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_941-5_0_4_node_56 | 0.4 | n |  | TRUE
70 | bus_LV_941-5_0_4_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_941-5_0_4_node_57 | 0.4 | n |  | TRUE
72 | bus_LV_941-5_0_4_node_63 | 0.4 | n |  | TRUE
73 | bus_LV_941-5_0_4_node_62 | 0.4 | n |  | TRUE
74 | bus_LV_941-5_0_4_node_168 | 0.4 | n |  | TRUE
75 | bus_LV_941-5_0_4_node_64 | 0.4 | n |  | TRUE
76 | bus_LV_941-5_0_4_node_65 | 0.4 | n |  | TRUE
77 | bus_LV_941-5_0_4_node_88 | 0.4 | n |  | TRUE
78 | bus_LV_941-5_0_4_node_89 | 0.4 | n |  | TRUE
79 | bus_LV_941-5_0_4_node_96 | 0.4 | n |  | TRUE
80 | bus_LV_941-5_0_4_node_99 | 0.4 | n |  | TRUE
81 | bus_LV_941-5_0_4_node_104 | 0.4 | n |  | TRUE
82 | bus_LV_941-5_0_4_node_66 | 0.4 | n |  | TRUE
83 | bus_LV_941-5_0_4_node_67 | 0.4 | n |  | TRUE
84 | bus_LV_941-5_0_4_node_68 | 0.4 | n |  | TRUE
85 | bus_LV_941-5_0_4_node_70 | 0.4 | n |  | TRUE
86 | bus_LV_941-5_0_4_node_76 | 0.4 | n |  | TRUE
87 | bus_LV_941-5_0_4_node_136 | 0.4 | n |  | TRUE
88 | bus_LV_941-5_0_4_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_941-5_0_4_node_71 | 0.4 | n |  | TRUE
90 | bus_LV_941-5_0_4_node_72 | 0.4 | n |  | TRUE
91 | bus_LV_941-5_0_4_node_74 | 0.4 | n |  | TRUE
92 | bus_LV_941-5_0_4_node_81 | 0.4 | n |  | TRUE
93 | bus_LV_941-5_0_4_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_941-5_0_4_node_86 | 0.4 | n |  | TRUE
95 | bus_LV_941-5_0_4_node_82 | 0.4 | n |  | TRUE
96 | bus_LV_941-5_0_4_node_79 | 0.4 | n |  | TRUE
97 | bus_LV_941-5_0_4_node_94 | 0.4 | n |  | TRUE
98 | bus_LV_941-5_0_4_node_83 | 0.4 | n |  | TRUE
99 | bus_LV_941-5_0_4_node_78 | 0.4 | n |  | TRUE
100 | bus_LV_941-5_0_4_node_80 | 0.4 | n |  | TRUE
101 | bus_LV_941-5_0_4_node_84 | 0.4 | n |  | TRUE
102 | bus_LV_941-5_0_4_node_85 | 0.4 | n |  | TRUE
103 | bus_LV_941-5_0_4_node_92 | 0.4 | n |  | TRUE
104 | bus_LV_941-5_0_4_node_133 | 0.4 | n |  | TRUE
105 | bus_LV_941-5_0_4_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_941-5_0_4_node_134 | 0.4 | n |  | TRUE
107 | bus_LV_941-5_0_4_node_95 | 0.4 | n |  | TRUE
108 | bus_LV_941-5_0_4_node_97 | 0.4 | n |  | TRUE
109 | bus_LV_941-5_0_4_node_100 | 0.4 | n |  | TRUE
110 | bus_LV_941-5_0_4_node_103 | 0.4 | n |  | TRUE
111 | bus_LV_941-5_0_4_node_91 | 0.4 | n |  | TRUE
112 | bus_LV_941-5_0_4_node_93 | 0.4 | n |  | TRUE
113 | bus_LV_941-5_0_4_node_98 | 0.4 | n |  | TRUE
114 | bus_LV_941-5_0_4_node_130 | 0.4 | n |  | TRUE
115 | bus_LV_941-5_0_4_node_128 | 0.4 | n |  | TRUE
116 | bus_LV_941-5_0_4_node_161 | 0.4 | n |  | TRUE
117 | bus_LV_941-5_0_4_node_163 | 0.4 | n |  | TRUE
118 | bus_LV_941-5_0_4_node_159 | 0.4 | n |  | TRUE
119 | bus_LV_941-5_0_4_node_164 | 0.4 | n |  | TRUE
120 | bus_LV_941-5_0_4_node_165 | 0.4 | n |  | TRUE
121 | bus_LV_941-5_0_4_node_101 | 0.4 | n |  | TRUE
122 | bus_LV_941-5_0_4_node_102 | 0.4 | n |  | TRUE
123 | bus_LV_941-5_0_4_node_122 | 0.4 | n |  | TRUE
124 | bus_LV_941-5_0_4_node_116 | 0.4 | n |  | TRUE
125 | bus_LV_941-5_0_4_node_132 | 0.4 | n |  | TRUE
126 | bus_LV_941-5_0_4_node_123 | 0.4 | n |  | TRUE
127 | bus_LV_941-5_0_4_node_114 | 0.4 | n |  | TRUE
128 | bus_LV_941-5_0_4_node_131 | 0.4 | n |  | TRUE
129 | bus_LV_941-5_0_4_node_105 | 0.4 | n |  | TRUE
130 | bus_LV_941-5_0_4_node_106 | 0.4 | n |  | TRUE
131 | bus_LV_941-5_0_4_node_107 | 0.4 | n |  | TRUE
132 | bus_LV_941-5_0_4_node_142 | 0.4 | n |  | TRUE
133 | bus_LV_941-5_0_4_node_108 | 0.4 | n |  | TRUE
134 | bus_LV_941-5_0_4_node_141 | 0.4 | n |  | TRUE
135 | bus_LV_941-5_0_4_node_109 | 0.4 | n |  | TRUE
136 | bus_LV_941-5_0_4_node_110 | 0.4 | n |  | TRUE
137 | bus_LV_941-5_0_4_node_111 | 0.4 | n |  | TRUE
138 | bus_LV_941-5_0_4_node_112 | 0.4 | n |  | TRUE
139 | bus_LV_941-5_0_4_node_113 | 0.4 | n |  | TRUE
140 | bus_LV_941-5_0_4_node_115 | 0.4 | n |  | TRUE
141 | bus_LV_941-5_0_4_node_117 | 0.4 | n |  | TRUE
142 | bus_LV_941-5_0_4_node_118 | 0.4 | n |  | TRUE
143 | bus_LV_941-5_0_4_node_119 | 0.4 | n |  | TRUE
144 | bus_LV_941-5_0_4_node_120 | 0.4 | n |  | TRUE
145 | bus_LV_941-5_0_4_node_121 | 0.4 | n |  | TRUE
146 | bus_LV_941-5_0_4_node_124 | 0.4 | n |  | TRUE
147 | bus_LV_941-5_0_4_node_125 | 0.4 | n |  | TRUE
148 | bus_LV_941-5_0_4_node_127 | 0.4 | n |  | TRUE
149 | bus_LV_941-5_0_4_node_129 | 0.4 | n |  | TRUE
150 | bus_LV_941-5_0_4_node_135 | 0.4 | n |  | TRUE
151 | bus_LV_941-5_0_4_node_169 | 0.4 | n |  | TRUE
152 | bus_LV_941-5_0_4_node_137 | 0.4 | n |  | TRUE
153 | bus_LV_941-5_0_4_node_138 | 0.4 | n |  | TRUE
154 | bus_LV_941-5_0_4_node_139 | 0.4 | n |  | TRUE
155 | bus_LV_941-5_0_4_node_151 | 0.4 | n |  | TRUE
156 | bus_LV_941-5_0_4_node_149 | 0.4 | n |  | TRUE
157 | bus_LV_941-5_0_4_node_143 | 0.4 | n |  | TRUE
158 | bus_LV_941-5_0_4_node_144 | 0.4 | n |  | TRUE
159 | bus_LV_941-5_0_4_node_145 | 0.4 | n |  | TRUE
160 | bus_LV_941-5_0_4_node_150 | 0.4 | n |  | TRUE
161 | bus_LV_941-5_0_4_node_157 | 0.4 | n |  | TRUE
162 | bus_LV_941-5_0_4_node_160 | 0.4 | n |  | TRUE
163 | bus_LV_941-5_0_4_node_162 | 0.4 | n |  | TRUE
164 | bus_LV_941-5_0_4_node_170 | 0.4 | n |  | TRUE
165 | bus_MV_93_2_node_131 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_941-5_0_4_load_0 | 0 | 0.0031748 | 0.00079567 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_941-5_0_4_load_1 | 1 | 0.00093774 | 0.00023502 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_941-5_0_4_load_2 | 3 | 0.00049839 | 0.00012491 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_941-5_0_4_load_140 | 4 | 0.0046378 | 0.0011623 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_941-5_0_4_load_146 | 5 | 0.0037707 | 0.00094502 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_941-5_0_4_load_147 | 6 | 0.0029087 | 0.00072899 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_941-5_0_4_load_3 | 7 | 0.0017982 | 0.00045067 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_941-5_0_4_load_4 | 8 | 0.0049139 | 0.0012315 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_941-5_0_4_load_166 | 10 | 0.0010948 | 0.00027437 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_941-5_0_4_load_10 | 12 | 0.0016968 | 0.00042526 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_941-5_0_4_load_167 | 13 | 0.0011049 | 0.00027692 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_941-5_0_4_load_7 | 14 | 0.0012763 | 0.00031988 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_941-5_0_4_load_43 | 15 | 0.00063313 | 0.00015868 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_941-5_0_4_load_42 | 16 | 0.00020361 | 5.103e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_941-5_0_4_load_13 | 20 | 0.00050908 | 0.00012759 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_941-5_0_4_load_38 | 21 | 0.00037557 | 9.4127e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_941-5_0_4_load_40 | 22 | 0.00049517 | 0.0001241 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_941-5_0_4_load_49 | 24 | 0.0034376 | 0.00086154 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_941-5_0_4_load_41 | 26 | 0.00064385 | 0.00016136 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_941-5_0_4_load_14 | 27 | 0.0011842 | 0.00029679 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_941-5_0_4_load_15 | 28 | 0.00083847 | 0.00021014 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_941-5_0_4_load_16 | 29 | 0.00081331 | 0.00020383 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_941-5_0_4_load_17 | 30 | 0.00092683 | 0.00023229 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_941-5_0_4_load_18 | 31 | 0.0036569 | 0.0009165 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_941-5_0_4_load_154 | 32 | 0.00036693 | 9.1962e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_941-5_0_4_load_19 | 33 | 0.00058416 | 0.0001464 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_941-5_0_4_load_153 | 34 | 0.00042367 | 0.00010618 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_941-5_0_4_load_21 | 35 | 0.0021775 | 0.00054573 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_941-5_0_4_load_23 | 36 | 0.0037529 | 0.00094057 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_941-5_0_4_load_24 | 37 | 0.00088264 | 0.00022121 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_941-5_0_4_load_25 | 38 | 0.00081465 | 0.00020417 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_941-5_0_4_load_156 | 40 | 0.001438 | 0.00036039 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_941-5_0_4_load_27 | 41 | 0.0011312 | 0.0002835 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_941-5_0_4_load_158 | 43 | 0.0014656 | 0.00036731 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_941-5_0_4_load_48 | 45 | 0.0013586 | 0.00034049 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_941-5_0_4_load_44 | 46 | 0.0012435 | 0.00031165 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_941-5_0_4_load_28 | 47 | 0.00050553 | 0.0001267 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_941-5_0_4_load_29 | 48 | 0.0027314 | 0.00068454 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_941-5_0_4_load_30 | 49 | 0.00023209 | 5.8167e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_941-5_0_4_load_31 | 50 | 0.00097314 | 0.00024389 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_941-5_0_4_load_152 | 51 | 0.00077714 | 0.00019477 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_941-5_0_4_load_32 | 52 | 0.00038719 | 9.7038e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_941-5_0_4_load_33 | 53 | 0.00022156 | 5.5527e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_941-5_0_4_load_34 | 54 | 0.0012699 | 0.00031825 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_941-5_0_4_load_35 | 55 | 0.0034313 | 0.00085997 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_941-5_0_4_load_36 | 56 | 0.0014815 | 0.00037129 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_941-5_0_4_load_50 | 57 | 0.0019192 | 0.00048099 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_941-5_0_4_load_45 | 58 | 0.0019412 | 0.00048652 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_941-5_0_4_load_47 | 59 | 0.00048149 | 0.00012067 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_941-5_0_4_load_77 | 60 | 0.0033489 | 0.0008393 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_941-5_0_4_load_51 | 62 | 0.0021931 | 0.00054964 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_941-5_0_4_load_55 | 65 | 0.001234 | 0.00030927 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_941-5_0_4_load_52 | 66 | 0.0023935 | 0.00059987 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_941-5_0_4_load_56 | 69 | 0.015687 | 0.0039316 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_941-5_0_4_load_57 | 71 | 0.00065896 | 0.00016515 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_941-5_0_4_load_63 | 72 | 0.001107 | 0.00027744 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_941-5_0_4_load_62 | 73 | 0.0049997 | 0.001253 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_941-5_0_4_load_168 | 74 | 0.00093753 | 0.00023497 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_941-5_0_4_load_64 | 75 | 0.003992 | 0.0010005 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_941-5_0_4_load_89 | 78 | 0.009092 | 0.0022787 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_941-5_0_4_load_99 | 80 | 0.0090013 | 0.0022559 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_941-5_0_4_load_104 | 81 | 0.0031289 | 0.00078417 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_941-5_0_4_load_66 | 82 | 0.0054018 | 0.0013538 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_941-5_0_4_load_67 | 83 | 0.0018062 | 0.00045267 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_941-5_0_4_load_68 | 84 | 0.0016727 | 0.00041923 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_941-5_0_4_load_70 | 85 | 0.0013646 | 0.00034201 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_941-5_0_4_load_76 | 86 | 0.00048163 | 0.00012071 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_941-5_0_4_load_136 | 87 | 0.0064858 | 0.0016255 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_941-5_0_4_load_71 | 89 | 0.00060945 | 0.00015274 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_941-5_0_4_load_72 | 90 | 0.00037551 | 9.4111e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_941-5_0_4_load_74 | 91 | 0.00015912 | 3.988e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_941-5_0_4_load_81 | 92 | 0.00020086 | 5.0341e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_941-5_0_4_load_86 | 94 | 0.0060814 | 0.0015241 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_941-5_0_4_load_82 | 95 | 0.004573 | 0.0011461 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_941-5_0_4_load_79 | 96 | 0.0012814 | 0.00032115 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_941-5_0_4_load_94 | 97 | 0.0028705 | 0.00071942 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_941-5_0_4_load_78 | 99 | 0.0015901 | 0.00039851 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_941-5_0_4_load_80 | 100 | 0.00016525 | 4.1415e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_941-5_0_4_load_84 | 101 | 0.0036307 | 0.00090995 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_941-5_0_4_load_85 | 102 | 0.0032358 | 0.00081097 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_941-5_0_4_load_92 | 103 | 0.0049899 | 0.0012506 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_941-5_0_4_load_133 | 104 | 0.0035097 | 0.00087961 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_941-5_0_4_load_90 | 105 | 0.0066724 | 0.0016723 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_941-5_0_4_load_134 | 106 | 0.0034199 | 0.00085711 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_941-5_0_4_load_95 | 107 | 0.0029541 | 0.00074037 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_941-5_0_4_load_97 | 108 | 0.0025968 | 0.00065081 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_941-5_0_4_load_103 | 110 | 0.0022895 | 0.00057381 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_941-5_0_4_load_91 | 111 | 0.0045202 | 0.0011329 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_941-5_0_4_load_93 | 112 | 0.0055189 | 0.0013832 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_941-5_0_4_load_98 | 113 | 0.0030189 | 0.0007566 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_941-5_0_4_load_130 | 114 | 0.0026931 | 0.00067495 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_941-5_0_4_load_128 | 115 | 0.0038745 | 0.00097104 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_941-5_0_4_load_161 | 116 | 0.001506 | 0.00037743 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_941-5_0_4_load_163 | 117 | 0.00039758 | 9.9643e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_941-5_0_4_load_165 | 120 | 0.0014299 | 0.00035838 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_941-5_0_4_load_102 | 122 | 0.0076965 | 0.0019289 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_941-5_0_4_load_122 | 123 | 0.0040331 | 0.0010108 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_941-5_0_4_load_116 | 124 | 0.0043802 | 0.0010978 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_941-5_0_4_load_123 | 126 | 0.0028486 | 0.00071394 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_941-5_0_4_load_114 | 127 | 0.0027329 | 0.00068493 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_941-5_0_4_load_131 | 128 | 0.0080015 | 0.0020054 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_941-5_0_4_load_107 | 131 | 0.002935 | 0.00073559 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_941-5_0_4_load_142 | 132 | 0.0016117 | 0.00040393 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_941-5_0_4_load_108 | 133 | 0.00314 | 0.00078695 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_941-5_0_4_load_141 | 134 | 0.0013854 | 0.00034722 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_941-5_0_4_load_110 | 136 | 0.0036947 | 0.00092598 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_941-5_0_4_load_111 | 137 | 0.003 | 0.00075187 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_941-5_0_4_load_112 | 138 | 0.0024056 | 0.0006029 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_941-5_0_4_load_113 | 139 | 0.0022397 | 0.00056133 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_941-5_0_4_load_115 | 140 | 0.0020599 | 0.00051627 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_941-5_0_4_load_118 | 142 | 0.0043994 | 0.0011026 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_941-5_0_4_load_119 | 143 | 0.0021252 | 0.00053263 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_941-5_0_4_load_120 | 144 | 0.0022475 | 0.00056329 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_941-5_0_4_load_121 | 145 | 0.0031346 | 0.0007856 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_941-5_0_4_load_124 | 146 | 0.0034563 | 0.00086623 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_941-5_0_4_load_125 | 147 | 0.0020907 | 0.00052397 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_941-5_0_4_load_127 | 148 | 0.0042145 | 0.0010563 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_941-5_0_4_load_129 | 149 | 0.012472 | 0.0031258 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_941-5_0_4_load_135 | 150 | 0.0023741 | 0.000595 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_941-5_0_4_load_169 | 151 | 0.011211 | 0.0028096 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_941-5_0_4_load_137 | 152 | 0.0048759 | 0.001222 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_941-5_0_4_load_138 | 153 | 0.0052713 | 0.0013211 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_941-5_0_4_load_139 | 154 | 0.0053112 | 0.0013311 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_941-5_0_4_load_151 | 155 | 0.0068013 | 0.0017046 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_941-5_0_4_load_149 | 156 | 0.0022532 | 0.00056471 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_941-5_0_4_load_144 | 158 | 0.0014926 | 0.00037408 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_941-5_0_4_load_145 | 159 | 0.0023672 | 0.00059327 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_941-5_0_4_load_150 | 160 | 0.0013815 | 0.00034625 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_941-5_0_4_load_157 | 161 | 0.003824 | 0.00095839 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_941-5_0_4_load_162 | 163 | 0.0016649 | 0.00041726 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_941-5_0_4_load_170 | 164 | 0.001118 | 0.00028021 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 94 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_941-5_0_4_line_0 |  | 0 | 1 | 0.12802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_941-5_0_4_line_1 |  | 0 | 2 | 0.15005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_941-5_0_4_line_2 |  | 1 | 3 | 0.025199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_941-5_0_4_line_3 |  | 2 | 4 | 0.016878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_941-5_0_4_line_4 |  | 4 | 153 | 0.014409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_941-5_0_4_line_5 |  | 5 | 6 | 0.017722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_941-5_0_4_line_6 |  | 6 | 130 | 0.024632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_941-5_0_4_line_7 |  | 7 | 8 | 0.023166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_941-5_0_4_line_8 |  | 7 | 9 | 0.039966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_941-5_0_4_line_9 |  | 8 | 10 | 0.038803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_941-5_0_4_line_10 |  | 9 | 11 | 0.008074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_941-5_0_4_line_11 |  | 10 | 12 | 0.16727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_941-5_0_4_line_12 |  | 11 | 14 | 0.011797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_941-5_0_4_line_13 |  | 12 | 13 | 0.16224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_941-5_0_4_line_14 |  | 13 | 17 | 0.073139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_941-5_0_4_line_15 |  | 15 | 16 | 0.016396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_941-5_0_4_line_16 |  | 16 | 26 | 0.0032725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_941-5_0_4_line_17 |  | 17 | 63 | 0.025078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_941-5_0_4_line_18 |  | 18 | 19 | 0.024629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_941-5_0_4_line_19 |  | 18 | 20 | 0.0010033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_941-5_0_4_line_20 |  | 19 | 21 | 0.010959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_941-5_0_4_line_21 |  | 20 | 22 | 0.025404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_941-5_0_4_line_22 |  | 21 | 25 | 0.010983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_941-5_0_4_line_23 |  | 22 | 26 | 0.013262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_941-5_0_4_line_24 |  | 23 | 24 | 0.034564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_941-5_0_4_line_25 |  | 23 | 25 | 0.016304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_941-5_0_4_line_26 |  | 24 | 57 | 0.015394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_941-5_0_4_line_27 |  | 25 | 55 | 0.016519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_941-5_0_4_line_28 |  | 27 | 28 | 0.0064151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_941-5_0_4_line_29 |  | 27 | 29 | 0.0092043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_941-5_0_4_line_30 |  | 28 | 30 | 0.042115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_941-5_0_4_line_31 |  | 29 | 31 | 0.017815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_941-5_0_4_line_32 |  | 30 | 33 | 0.085009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_941-5_0_4_line_33 |  | 32 | 33 | 0.46082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_941-5_0_4_line_34 |  | 32 | 34 | 0.028137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_941-5_0_4_line_35 |  | 34 | 42 | 0.021465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_941-5_0_4_line_36 |  | 35 | 36 | 0.10866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_941-5_0_4_line_37 |  | 36 | 37 | 0.031624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_941-5_0_4_line_38 |  | 37 | 38 | 0.046732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_941-5_0_4_line_39 |  | 38 | 39 | 0.073824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_941-5_0_4_line_40 |  | 38 | 40 | 0.12366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_941-5_0_4_line_41 |  | 39 | 41 | 0.014874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_941-5_0_4_line_42 |  | 40 | 42 | 0.025046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_941-5_0_4_line_43 |  | 41 | 44 | 0.020662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_941-5_0_4_line_44 |  | 42 | 43 | 0.32473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_941-5_0_4_line_45 |  | 43 | 161 | 0.0071472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_941-5_0_4_line_46 |  | 44 | 45 | 0.030156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_941-5_0_4_line_47 |  | 44 | 46 | 0.028426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_941-5_0_4_line_48 |  | 45 | 51 | 0.033493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_941-5_0_4_line_49 |  | 45 | 56 | 0.010275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_941-5_0_4_line_50 |  | 46 | 58 | 0.0038975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_941-5_0_4_line_51 |  | 47 | 48 | 0.026864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_941-5_0_4_line_52 |  | 47 | 49 | 0.042032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_941-5_0_4_line_53 |  | 48 | 50 | 0.02162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_941-5_0_4_line_54 |  | 50 | 51 | 0.047245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_941-5_0_4_line_55 |  | 52 | 53 | 0.0032954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_941-5_0_4_line_56 |  | 52 | 54 | 0.043543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_941-5_0_4_line_57 |  | 53 | 55 | 0.0085215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_941-5_0_4_line_58 |  | 54 | 56 | 0.006727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_941-5_0_4_line_59 |  | 57 | 62 | 0.021844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_941-5_0_4_line_60 |  | 58 | 59 | 0.014182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_941-5_0_4_line_61 |  | 59 | 60 | 0.020912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_941-5_0_4_line_62 |  | 60 | 61 | 0.012191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_941-5_0_4_line_63 |  | 61 | 86 | 0.019752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_941-5_0_4_line_64 |  | 61 | 83 | 0.029357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_941-5_0_4_line_65 |  | 62 | 63 | 0.022332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_941-5_0_4_line_66 |  | 63 | 64 | 0.063325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_941-5_0_4_line_67 |  | 63 | 65 | 0.035409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_941-5_0_4_line_68 |  | 64 | 74 | 0.0068651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_941-5_0_4_line_69 |  | 65 | 67 | 0.019492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_941-5_0_4_line_70 |  | 66 | 67 | 0.016094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_941-5_0_4_line_71 |  | 66 | 68 | 0.012418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_941-5_0_4_line_72 |  | 67 | 69 | 0.011897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_941-5_0_4_line_73 |  | 68 | 70 | 0.004635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_941-5_0_4_line_74 |  | 69 | 71 | 0.009958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_941-5_0_4_line_75 |  | 70 | 72 | 0.015945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_941-5_0_4_line_76 |  | 72 | 73 | 0.010004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_941-5_0_4_line_77 |  | 73 | 75 | 0.023178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_941-5_0_4_line_78 |  | 75 | 76 | 0.017119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_941-5_0_4_line_79 |  | 76 | 77 | 0.033799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_941-5_0_4_line_80 |  | 76 | 78 | 0.019174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_941-5_0_4_line_81 |  | 77 | 79 | 0.010074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_941-5_0_4_line_82 |  | 77 | 80 | 0.0016382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_941-5_0_4_line_83 |  | 78 | 81 | 0.0093508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_941-5_0_4_line_84 |  | 79 | 108 | 0.019155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_941-5_0_4_line_85 |  | 79 | 107 | 0.036643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_941-5_0_4_line_86 |  | 80 | 109 | 0.054943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_941-5_0_4_line_87 |  | 81 | 110 | 0.014663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_941-5_0_4_line_88 |  | 82 | 83 | 0.00082388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_941-5_0_4_line_89 |  | 82 | 84 | 0.0090212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_941-5_0_4_line_90 |  | 84 | 85 | 0.0084867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_941-5_0_4_line_91 |  | 85 | 87 | 0.015126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_941-5_0_4_line_92 |  | 86 | 88 | 0.04377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_941-5_0_4_line_93 |  | 88 | 89 | 0.03259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_941-5_0_4_line_94 |  | 89 | 90 | 0.040404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_941-5_0_4_line_95 |  | 90 | 91 | 0.018891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_941-5_0_4_line_96 |  | 91 | 92 | 0.0018933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_941-5_0_4_line_97 |  | 92 | 96 | 0.0056206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_941-5_0_4_line_98 |  | 93 | 94 | 0.037581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_941-5_0_4_line_99 |  | 93 | 95 | 0.031896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_941-5_0_4_line_100 |  | 94 | 97 | 0.014299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_941-5_0_4_line_101 |  | 95 | 98 | 0.012952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_941-5_0_4_line_102 |  | 96 | 99 | 0.025971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_941-5_0_4_line_103 |  | 97 | 107 | 0.013288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_941-5_0_4_line_104 |  | 98 | 101 | 0.015922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_941-5_0_4_line_105 |  | 98 | 102 | 0.023661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_941-5_0_4_line_106 |  | 99 | 100 | 0.0050934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_941-5_0_4_line_107 |  | 101 | 103 | 0.026771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_941-5_0_4_line_108 |  | 102 | 104 | 0.014207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_941-5_0_4_line_109 |  | 103 | 105 | 0.0054272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_941-5_0_4_line_110 |  | 104 | 106 | 0.004247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_941-5_0_4_line_111 |  | 105 | 111 | 0.044217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_941-5_0_4_line_112 |  | 106 | 150 | 0.0069596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_941-5_0_4_line_113 |  | 108 | 114 | 0.019761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_941-5_0_4_line_114 |  | 109 | 121 | 0.028516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_941-5_0_4_line_115 |  | 109 | 122 | 0.0033998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_941-5_0_4_line_116 |  | 110 | 129 | 0.036565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_941-5_0_4_line_117 |  | 111 | 112 | 0.040276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_941-5_0_4_line_118 |  | 112 | 113 | 0.012528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_941-5_0_4_line_119 |  | 114 | 115 | 0.017815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_941-5_0_4_line_120 |  | 115 | 148 | 0.022728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_941-5_0_4_line_121 |  | 116 | 117 | 0.014304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_941-5_0_4_line_122 |  | 116 | 118 | 0.013185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_941-5_0_4_line_123 |  | 117 | 119 | 0.070361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_941-5_0_4_line_124 |  | 118 | 162 | 0.034448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_941-5_0_4_line_125 |  | 118 | 163 | 0.019372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_941-5_0_4_line_126 |  | 118 | 161 | 0.024671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_941-5_0_4_line_127 |  | 119 | 120 | 0.021169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_941-5_0_4_line_128 |  | 121 | 123 | 0.010716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_941-5_0_4_line_129 |  | 121 | 124 | 0.036411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_941-5_0_4_line_130 |  | 122 | 125 | 0.043943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_941-5_0_4_line_131 |  | 123 | 126 | 0.0063473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_941-5_0_4_line_132 |  | 124 | 127 | 0.015141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_941-5_0_4_line_133 |  | 125 | 128 | 0.009948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_941-5_0_4_line_134 |  | 127 | 139 | 0.03652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_941-5_0_4_line_135 |  | 129 | 130 | 0.047078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_941-5_0_4_line_136 |  | 129 | 131 | 0.016637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_941-5_0_4_line_137 |  | 130 | 132 | 0.013494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_941-5_0_4_line_138 |  | 131 | 133 | 0.0025386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_941-5_0_4_line_139 |  | 132 | 134 | 0.00014264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_941-5_0_4_line_140 |  | 133 | 135 | 0.025772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_941-5_0_4_line_141 |  | 134 | 157 | 0.016624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_941-5_0_4_line_142 |  | 135 | 136 | 0.016208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_941-5_0_4_line_143 |  | 135 | 137 | 0.0062346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_941-5_0_4_line_144 |  | 137 | 138 | 0.0063864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_941-5_0_4_line_145 |  | 139 | 140 | 0.023845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_941-5_0_4_line_146 |  | 140 | 141 | 0.016863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_941-5_0_4_line_147 |  | 141 | 142 | 0.01948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_941-5_0_4_line_148 |  | 142 | 143 | 0.014143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_941-5_0_4_line_149 |  | 143 | 144 | 0.01841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_941-5_0_4_line_150 |  | 144 | 145 | 0.028758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_941-5_0_4_line_151 |  | 145 | 146 | 0.024302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_941-5_0_4_line_152 |  | 146 | 147 | 0.017353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_941-5_0_4_line_153 |  | 148 | 149 | 0.033428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_941-5_0_4_line_154 |  | 150 | 151 | 0.0078644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_941-5_0_4_line_155 |  | 152 | 153 | 0.014877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_941-5_0_4_line_156 |  | 152 | 154 | 0.0087646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_941-5_0_4_line_157 |  | 154 | 155 | 0.069539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_941-5_0_4_line_158 |  | 155 | 156 | 0.0070879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_941-5_0_4_line_159 |  | 156 | 160 | 0.00016703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_941-5_0_4_line_160 |  | 157 | 158 | 0.0085049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_941-5_0_4_line_161 |  | 157 | 159 | 0.01067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_941-5_0_4_line_162 |  | 159 | 160 | 1.4983e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_941-5_0_4_line_163 |  | 162 | 164 | 0.00698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_941-5_0_4_trafo_86 | 0.63 MVA 20/0.4 kV | 165 | 94 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2609844.0367 | 1178370.3765 | 2609783.5616 | 1178257.5418
1 | 2609795.768 | 1178107.9921 | 2609783.5616 | 1178257.5418
2 | 2609844.0367 | 1178370.3765 | 2609847.69 | 1178372.0221 | 2609861.7158 | 1178377.7368 | 2609866.433 | 1178380.4348 | 2609866.9295 | 1178380.7929
3 | 2609795.768 | 1178107.9921 | 2609809.1222 | 1178097.6705
4 | 2609820.523 | 1178088.8588 | 2609809.1222 | 1178097.6705
5 | 2609777.7707 | 1178024.918 | 2609782.9298 | 1178007.9633
6 | 2609790.1005 | 1177984.3977 | 2609782.9298 | 1178007.9633
7 | 2609327.3494 | 1178028.2623 | 2609333.8452 | 1178028.0753 | 2609337.4422 | 1178029.1926 | 2609340.0982 | 1178031.0976 | 2609342.047 | 1178035.7363 | 2609343.228 | 1178040.1834
8 | 2609295.4764 | 1178011.5522 | 2609298.3841 | 1178018.7047 | 2609301.0304 | 1178021.9772 | 2609304.2509 | 1178024.4945 | 2609307.8617 | 1178026.5678 | 2609312.1839 | 1178028.1197 | 2609316.6148 | 1178028.5712 | 2609327.3494 | 1178028.2623
9 | 2609343.228 | 1178040.1834 | 2609381.4483 | 1178046.8799
10 | 2609294.442 | 1178003.5465 | 2609295.4764 | 1178011.5522
11 | 2609536.1192 | 1177983.1809 | 2609381.4483 | 1178046.8799
12 | 2609294.442 | 1178003.5465 | 2609294.1883 | 1177991.7519
13 | 2609659.8903 | 1177878.2932 | 2609536.1192 | 1177983.1809
14 | 2609673.383 | 1177825.9734 | 2609670.3711 | 1177822.0888 | 2609667.1419 | 1177820.2494 | 2609664.224 | 1177819.6778 | 2609661.5562 | 1177820.3405 | 2609660.0717 | 1177821.7166 | 2609659.1432 | 1177824.2164 | 2609658.9329 | 1177826.6729 | 2609659.8903 | 1177878.2932
15 | 2609519.7953 | 1177816.9161 | 2609518.6147 | 1177817.4565 | 2609504.8754 | 1177823.7146
16 | 2609519.7953 | 1177816.9161 | 2609522.7708 | 1177815.554
17 | 2609691.5855 | 1177820.0663 | 2609687.3674 | 1177829.7756 | 2609673.383 | 1177825.9734
18 | 2609558.9417 | 1177799.2665 | 2609567.3825 | 1177795.9671 | 2609575.372 | 1177792.9671 | 2609582.2137 | 1177791.0881
19 | 2609558.9417 | 1177799.2665 | 2609558.0239 | 1177799.6718
20 | 2609582.2137 | 1177791.0881 | 2609581.8527 | 1177787.4635 | 2609582.7446 | 1177783.9186 | 2609584.7972 | 1177780.887
21 | 2609558.0239 | 1177799.6718 | 2609542.2116 | 1177806.6549 | 2609534.8297 | 1177810.034
22 | 2609594.9186 | 1177777.9127 | 2609591.2589 | 1177777.6956 | 2609587.7501 | 1177778.7239 | 2609584.7972 | 1177780.887
23 | 2609534.8297 | 1177810.034 | 2609522.7708 | 1177815.554
24 | 2609602.9064 | 1177790.4095 | 2609611.6999 | 1177791.2017 | 2609619.3163 | 1177792.2254 | 2609625.6332 | 1177793.5473 | 2609636.7602 | 1177796.812
25 | 2609594.9186 | 1177777.9127 | 2609598.6447 | 1177779.5861 | 2609601.4595 | 1177782.5365 | 2609602.9511 | 1177786.3297 | 2609602.9064 | 1177790.4095
26 | 2609636.7602 | 1177796.812 | 2609638.4716 | 1177797.3141 | 2609649.7883 | 1177801.8345 | 2609651.0982 | 1177802.3938
27 | 2609594.9186 | 1177777.9127 | 2609596.3137 | 1177770.311 | 2609598.075 | 1177763.0546 | 2609598.4349 | 1177761.7809
28 | 2609363.5051 | 1176996.4272 | 2609359.5075 | 1177001.4444
29 | 2609353.7718 | 1177008.643 | 2609359.5075 | 1177001.4444
30 | 2609363.5051 | 1176996.4272 | 2609370.8367 | 1176987.2256 | 2609385.8468 | 1176960.8472
31 | 2609353.7718 | 1177008.643 | 2609349.6579 | 1177013.8063 | 2609341.498 | 1177021.4977
32 | 2609385.8468 | 1176960.8472 | 2609458.1854 | 1177005.4981
33 | 2609573.0325 | 1177451.7787 | 2609458.1854 | 1177005.4981
34 | 2609573.0325 | 1177451.7787 | 2609583.295 | 1177446.8925 | 2609588.4096 | 1177445.2776 | 2609594.352 | 1177446.9212 | 2609598.5762 | 1177450.0244
35 | 2609616.8828 | 1177458.7964 | 2609611.1358 | 1177459.2097 | 2609605.6081 | 1177456.3328 | 2609601.3128 | 1177452.0349 | 2609598.5762 | 1177450.0244
36 | 2609503.1047 | 1177583.2984 | 2609398.8322 | 1177552.7317
37 | 2609534.3654 | 1177587.872 | 2609533.9919 | 1177587.775 | 2609524.4889 | 1177586.0703 | 2609506.3671 | 1177584.0629 | 2609503.1047 | 1177583.2984
38 | 2609579.5543 | 1177599.6251 | 2609563.9701 | 1177596.2601 | 2609558.0887 | 1177594.8278 | 2609552.7116 | 1177593.3964 | 2609542.7374 | 1177590.0455 | 2609534.3654 | 1177587.872
39 | 2609643.947 | 1177631.9276 | 2609637.3726 | 1177629.0045 | 2609633.7925 | 1177626.7421 | 2609630.7475 | 1177624.3694 | 2609623.9432 | 1177617.077 | 2609618.7776 | 1177612.422 | 2609612.1592 | 1177608.3205 | 2609606.18 | 1177605.8875 | 2609599.2909 | 1177603.8867 | 2609579.5543 | 1177599.6251
40 | 2609579.5543 | 1177599.6251 | 2609613.9822 | 1177480.8586
41 | 2609643.947 | 1177631.9276 | 2609638.9393 | 1177645.9338
42 | 2609616.8828 | 1177458.7964 | 2609619.9496 | 1177466.772 | 2609619.9414 | 1177471.8746 | 2609618.9097 | 1177476.7754 | 2609613.9822 | 1177480.8586
43 | 2609632.9892 | 1177665.7162 | 2609638.0599 | 1177648.3933 | 2609638.9393 | 1177645.9338
44 | 2609616.8828 | 1177458.7964 | 2609910.703 | 1177320.52
45 | 2609917.5415 | 1177318.4447 | 2609912.8166 | 1177319.9266 | 2609910.703 | 1177320.52
46 | 2609626.4855 | 1177695.1541 | 2609629.0849 | 1177684.6307 | 2609632.9892 | 1177665.7162
47 | 2609632.9892 | 1177665.7162 | 2609647.8003 | 1177668.8303 | 2609659.0033 | 1177672.9059 | 2609660.2378 | 1177673.5004
48 | 2609626.4855 | 1177695.1541 | 2609596.0766 | 1177681.1165
49 | 2609626.4855 | 1177695.1541 | 2609623.001 | 1177704.8202
50 | 2609660.2378 | 1177673.5004 | 2609663.7492 | 1177675.1915
51 | 2609534.6319 | 1177650.1871 | 2609511.4651 | 1177636.5866
52 | 2609527.5087 | 1177599.6264 | 2609525.6421 | 1177610.6624 | 2609521.555 | 1177619.7606 | 2609514.5469 | 1177625.3635 | 2609511.4722 | 1177632.0843 | 2609511.4651 | 1177636.5866
53 | 2609534.6319 | 1177650.1871 | 2609553.2764 | 1177661.1328
54 | 2609553.2764 | 1177661.1328 | 2609555.0784 | 1177662.1906 | 2609596.0766 | 1177681.1165
55 | 2609602.2591 | 1177750.6105 | 2609602.2591 | 1177750.6105 | 2609601.0952 | 1177753.6935
56 | 2609602.2591 | 1177750.6105 | 2609606.9907 | 1177739.9014 | 2609620.2081 | 1177710.94
57 | 2609601.0952 | 1177753.6935 | 2609599.6042 | 1177757.6431 | 2609598.4349 | 1177761.7809
58 | 2609623.001 | 1177704.8202 | 2609620.2081 | 1177710.94
59 | 2609671.1396 | 1177811.0828 | 2609660.4783 | 1177806.3984 | 2609651.0982 | 1177802.3938
60 | 2609663.7492 | 1177675.1915 | 2609668.7076 | 1177677.5793 | 2609676.0509 | 1177682.2045
61 | 2609690.9557 | 1177696.869 | 2609682.0706 | 1177687.8949 | 2609676.0509 | 1177682.2045 | 2609676.0509 | 1177682.2045
62 | 2609699.5327 | 1177705.5319 | 2609690.9557 | 1177696.869
63 | 2609699.5327 | 1177705.5319 | 2609704.7971 | 1177710.4428 | 2609710.3607 | 1177714.6539 | 2609715.1531 | 1177717.5015
64 | 2609699.5327 | 1177705.5319 | 2609694.1319 | 1177718.9078 | 2609687.9422 | 1177732.4959
65 | 2609691.5855 | 1177820.0663 | 2609671.1396 | 1177811.0828
66 | 2609691.5855 | 1177820.0663 | 2609687.3674 | 1177829.7756 | 2609685.1638 | 1177836.4087 | 2609684.2738 | 1177843.4109 | 2609683.9952 | 1177855.1942 | 2609684.5429 | 1177870.992 | 2609685.909 | 1177876.7193 | 2609688.362 | 1177881.3145
67 | 2609691.5855 | 1177820.0663 | 2609724.0484 | 1177834.2073
68 | 2609688.362 | 1177881.3145 | 2609691.434 | 1177885.8106 | 2609692.5422 | 1177886.698
69 | 2609741.9189 | 1177841.9918 | 2609724.0484 | 1177834.2073
70 | 2609741.9189 | 1177841.9918 | 2609756.672 | 1177848.4224
71 | 2609768.0552 | 1177853.3842 | 2609756.672 | 1177848.4224
72 | 2609741.9189 | 1177841.9918 | 2609741.4911 | 1177851.4181 | 2609742.3584 | 1177853.7207
73 | 2609772.3158 | 1177855.2365 | 2609768.0552 | 1177853.3842
74 | 2609742.3584 | 1177853.7207 | 2609744.0222 | 1177854.9462 | 2609751.4521 | 1177857.606
75 | 2609772.3158 | 1177855.2365 | 2609780.3332 | 1177858.629 | 2609787.1442 | 1177861.0837
76 | 2609796.6398 | 1177864.2271 | 2609789.5045 | 1177861.9344 | 2609787.1442 | 1177861.0837
77 | 2609796.6398 | 1177864.2271 | 2609798.3022 | 1177864.7612 | 2609805.8716 | 1177866.4411 | 2609813.4569 | 1177867.654 | 2609819.4336 | 1177868.1384
78 | 2609836.5247 | 1177867.6026 | 2609827.7978 | 1177868.2554 | 2609820.455 | 1177868.2212 | 2609819.4336 | 1177868.1384
79 | 2609836.5247 | 1177867.6026 | 2609843.2733 | 1177866.5464 | 2609849.9309 | 1177865.1121 | 2609855.0985 | 1177863.642 | 2609862.1014 | 1177861.2744 | 2609868.9906 | 1177858.3509
80 | 2609836.5247 | 1177867.6026 | 2609836.0406 | 1177873.994 | 2609835.2164 | 1177878.0391 | 2609834.1408 | 1177881.6948 | 2609832.1317 | 1177886.0826
81 | 2609863.0057 | 1177850.237 | 2609868.9906 | 1177858.3509
82 | 2609868.9906 | 1177858.3509 | 2609870.4764 | 1177857.661
83 | 2609832.1317 | 1177886.0826 | 2609832.1317 | 1177886.0826 | 2609826.9444 | 1177893.8627
84 | 2609863.0057 | 1177850.237 | 2609873.6394 | 1177834.3051
85 | 2609863.0057 | 1177850.237 | 2609841.1453 | 1177820.8294
86 | 2609920.2542 | 1177834.4449 | 2609914.8486 | 1177836.5705 | 2609909.5573 | 1177838.8741 | 2609897.5136 | 1177844.5572 | 2609883.8638 | 1177851.1604 | 2609875.5514 | 1177855.3045 | 2609870.4764 | 1177857.661
87 | 2609818.8518 | 1177906.0903 | 2609824.1428 | 1177898.0646 | 2609826.9444 | 1177893.8627
88 | 2609687.9422 | 1177732.4959 | 2609687.6007 | 1177733.2457
89 | 2609687.6007 | 1177733.2457 | 2609683.8611 | 1177741.4553
90 | 2609679.4137 | 1177748.5907 | 2609680.2783 | 1177747.7447 | 2609682.1544 | 1177745.2019 | 2609683.8611 | 1177741.4553
91 | 2609668.5769 | 1177759.1428 | 2609678.0666 | 1177749.9089 | 2609679.4137 | 1177748.5907
92 | 2609753.9538 | 1177737.6692 | 2609737.3624 | 1177729.9051 | 2609731.4911 | 1177727.0387 | 2609718.315 | 1177719.3802 | 2609715.1531 | 1177717.5015
93 | 2609753.9538 | 1177737.6692 | 2609762.0738 | 1177720.2512 | 2609762.7584 | 1177717.4732 | 2609762.8465 | 1177714.9609 | 2609762.4383 | 1177712.2033 | 2609760.8611 | 1177709.4438 | 2609759.5726 | 1177707.8735
94 | 2609759.5726 | 1177707.8735 | 2609756.0567 | 1177703.5886 | 2609752.9538 | 1177699.2369 | 2609749.9437 | 1177694.2295 | 2609744.818 | 1177683.8271 | 2609739.3358 | 1177673.0655
95 | 2609739.3358 | 1177673.0655 | 2609732.8137 | 1177660.2624 | 2609731.2214 | 1177656.0298
96 | 2609730.6069 | 1177654.2447 | 2609730.6377 | 1177654.4782 | 2609731.2214 | 1177656.0298
97 | 2609730.6069 | 1177654.2447 | 2609730.1394 | 1177650.6977 | 2609730.3704 | 1177648.6679
98 | 2609805.5527 | 1177766.3896 | 2609824.7492 | 1177798.6981
99 | 2609805.5527 | 1177766.3896 | 2609832.8378 | 1177749.8706
100 | 2609824.7492 | 1177798.6981 | 2609828.032 | 1177804.2232 | 2609832.9306 | 1177810.3859
101 | 2609843.9178 | 1177743.1624 | 2609832.8378 | 1177749.8706
102 | 2609741.877 | 1177625.4864 | 2609733.6095 | 1177640.6203 | 2609731.3251 | 1177645.1634 | 2609730.4417 | 1177648.0412 | 2609730.3704 | 1177648.6679
103 | 2609841.1453 | 1177820.8294 | 2609839.897 | 1177819.1501 | 2609832.9306 | 1177810.3859
104 | 2609843.9178 | 1177743.1624 | 2609857.5663 | 1177734.9639
105 | 2609843.9178 | 1177743.1624 | 2609862.4861 | 1177757.827
106 | 2609741.877 | 1177625.4864 | 2609744.3189 | 1177621.0165
107 | 2609857.5663 | 1177734.9639 | 2609880.5153 | 1177721.1788
108 | 2609862.4861 | 1177757.827 | 2609864.3845 | 1177759.3263 | 2609873.14 | 1177767.2188
109 | 2609885.1678 | 1177718.3841 | 2609880.5153 | 1177721.1788
110 | 2609876.2945 | 1177770.0623 | 2609876.2945 | 1177770.0623 | 2609873.14 | 1177767.2188
111 | 2609885.1678 | 1177718.3841 | 2609904.6396 | 1177706.6876 | 2609923.0991 | 1177698.1358 | 2609924.177 | 1177697.713
112 | 2609871.4185 | 1177775.0282 | 2609876.2945 | 1177770.0623
113 | 2609884.6095 | 1177817.8693 | 2609873.6394 | 1177834.3051
114 | 2609915.6927 | 1177862.2516 | 2609916.3811 | 1177857.1613 | 2609919.5774 | 1177846.4055 | 2609920.5992 | 1177843.0054 | 2609920.8569 | 1177839.6152 | 2609920.2542 | 1177834.4449
115 | 2609920.2542 | 1177834.4449 | 2609923.4479 | 1177833.2791
116 | 2609804.5607 | 1177939.5984 | 2609809.7511 | 1177924.0656 | 2609812.2134 | 1177918.1666 | 2609815.0576 | 1177912.3349 | 2609818.5129 | 1177906.6043 | 2609818.8518 | 1177906.0903
117 | 2609959.6328 | 1177679.3976 | 2609956.5324 | 1177682.0493 | 2609950.3733 | 1177686.9417 | 2609940.7385 | 1177691.2169 | 2609924.177 | 1177697.713
118 | 2609959.6328 | 1177679.3976 | 2609969.1537 | 1177671.2545
119 | 2609895.3136 | 1177803.6698 | 2609889.7993 | 1177810.0937 | 2609884.6095 | 1177817.8693
120 | 2609895.3136 | 1177803.6698 | 2609910.117 | 1177786.4244
121 | 2609958.8468 | 1177320.7387 | 2609946.718 | 1177313.1566
122 | 2609937.3035 | 1177303.9253 | 2609946.718 | 1177313.1566 | 2609946.718 | 1177313.1566
123 | 2610024.5266 | 1177343.9677 | 2609976.3519 | 1177331.6816 | 2609958.8468 | 1177320.7387
124 | 2609937.3035 | 1177303.9253 | 2609933.9148 | 1177292.1138 | 2609920.7854 | 1177274.2386
125 | 2609937.3035 | 1177303.9253 | 2609948.0137 | 1177287.7837
126 | 2609937.3035 | 1177303.9253 | 2609931.2923 | 1177306.917 | 2609922.9049 | 1177314.3848 | 2609917.5415 | 1177318.4447
127 | 2610024.5266 | 1177343.9677 | 2610026.803 | 1177335.2448 | 2610032.3534 | 1177324.4263
128 | 2609915.6927 | 1177862.2516 | 2609917.86 | 1177863.9005 | 2609925.7961 | 1177864.8515
129 | 2609915.6927 | 1177862.2516 | 2609913.814 | 1177871.0085 | 2609913.8845 | 1177883.893 | 2609912.9013 | 1177891.6953 | 2609911.9005 | 1177891.5714 | 2609911.1267 | 1177897.2166
130 | 2609966.0039 | 1177822.9255 | 2609957.3146 | 1177823.9228 | 2609950.3288 | 1177825.1564 | 2609943.5257 | 1177826.7793 | 2609938.0215 | 1177828.4155 | 2609932.5555 | 1177830.1185 | 2609926.3476 | 1177832.2205 | 2609923.4479 | 1177833.2791
131 | 2609925.7961 | 1177864.8515 | 2609932.0983 | 1177865.6067
132 | 2609909.0705 | 1177912.2169 | 2609911.1267 | 1177897.2166
133 | 2609966.0039 | 1177822.9255 | 2609965.9387 | 1177816.1776 | 2609966.309 | 1177813.9882 | 2609966.7789 | 1177813.1291
134 | 2609904.6221 | 1177948.464 | 2609908.1344 | 1177919.0459 | 2609909.0705 | 1177912.2169
135 | 2609804.5607 | 1177939.5984 | 2609796.0231 | 1177964.953 | 2609790.1005 | 1177984.3977
136 | 2609804.5607 | 1177939.5984 | 2609820.7285 | 1177943.5214
137 | 2609790.1005 | 1177984.3977 | 2609803.1478 | 1177987.8394
138 | 2609820.7285 | 1177943.5214 | 2609823.1956 | 1177944.12
139 | 2609803.1478 | 1177987.8394 | 2609803.2857 | 1177987.8758
140 | 2609848.2409 | 1177950.1971 | 2609823.1956 | 1177944.12
141 | 2609819.3595 | 1177992.1158 | 2609803.2857 | 1177987.8758
142 | 2609848.2409 | 1177950.1971 | 2609855.4105 | 1177953.277 | 2609853.3495 | 1177961.4445
143 | 2609848.2409 | 1177950.1971 | 2609852.9619 | 1177946.1249
144 | 2609859.32 | 1177945.5239 | 2609852.9619 | 1177946.1249
145 | 2609904.6221 | 1177948.464 | 2609904.16 | 1177952.3341 | 2609903.9182 | 1177955.3686 | 2609904.3802 | 1177957.8039 | 2609905.8598 | 1177959.4516 | 2609908.3875 | 1177960.3229 | 2609917.9237 | 1177960.3185
146 | 2609934.7862 | 1177960.3107 | 2609917.9237 | 1177960.3185
147 | 2609934.7862 | 1177960.3107 | 2609936.3624 | 1177940.8941
148 | 2609937.5067 | 1177926.7972 | 2609936.3624 | 1177940.8941
149 | 2609937.5067 | 1177926.7972 | 2609938.2646 | 1177917.4613 | 2609939.0279 | 1177908.4498
150 | 2609942.1031 | 1177879.8757 | 2609940.7737 | 1177887.8392 | 2609939.0279 | 1177908.4498
151 | 2609953.9409 | 1177861.7148 | 2609953.5464 | 1177861.7136 | 2609949.7169 | 1177862.5855 | 2609946.7799 | 1177864.3705 | 2609944.5366 | 1177867.1238 | 2609943.6753 | 1177870.4574 | 2609942.1031 | 1177879.8757
152 | 2609953.9409 | 1177861.7148 | 2609969.4317 | 1177861.7621 | 2609971.2859 | 1177861.9322
153 | 2609931.8898 | 1177761.0601 | 2609910.117 | 1177786.4244
154 | 2609865.9084 | 1177780.6396 | 2609871.4185 | 1177775.0282
155 | 2609820.523 | 1178088.8588 | 2609832.2939 | 1178079.761
156 | 2609839.2286 | 1178074.4012 | 2609832.2939 | 1178079.761
157 | 2609814.533 | 1178009.3946 | 2609839.2286 | 1178074.4012
158 | 2609814.533 | 1178009.3946 | 2609816.4399 | 1178002.568
159 | 2609816.4848 | 1178002.4071 | 2609816.4399 | 1178002.568
160 | 2609819.3595 | 1177992.1158 | 2609821.6511 | 1177983.9255
161 | 2609819.3595 | 1177992.1158 | 2609816.4889 | 1178002.3927
162 | 2609816.4889 | 1178002.3927 | 2609816.4848 | 1178002.4071
163 | 2609914.3695 | 1177277.0295 | 2609920.7854 | 1177274.2386

## bus_geodata
| x | y | coords
0 | 2609783.5616 | 1178257.5418
1 | 2609844.0367 | 1178370.3765
2 | 2609795.768 | 1178107.9921
3 | 2609866.9295 | 1178380.7929
4 | 2609809.1222 | 1178097.6705
5 | 2609777.7707 | 1178024.918
6 | 2609782.9298 | 1178007.9633
7 | 2609327.3494 | 1178028.2623
8 | 2609343.228 | 1178040.1834
9 | 2609295.4764 | 1178011.5522
10 | 2609381.4483 | 1178046.8799
11 | 2609294.442 | 1178003.5465
12 | 2609536.1192 | 1177983.1809
13 | 2609659.8903 | 1177878.2932
14 | 2609294.1883 | 1177991.7519
15 | 2609504.8754 | 1177823.7146
16 | 2609519.7953 | 1177816.9161
17 | 2609673.383 | 1177825.9734
18 | 2609558.9417 | 1177799.2665
19 | 2609582.2137 | 1177791.0881
20 | 2609558.0239 | 1177799.6718
21 | 2609584.7972 | 1177780.887
22 | 2609534.8297 | 1177810.034
23 | 2609602.9064 | 1177790.4095
24 | 2609636.7602 | 1177796.812
25 | 2609594.9186 | 1177777.9127
26 | 2609522.7708 | 1177815.554
27 | 2609359.5075 | 1177001.4444
28 | 2609363.5051 | 1176996.4272
29 | 2609353.7718 | 1177008.643
30 | 2609385.8468 | 1176960.8472
31 | 2609341.498 | 1177021.4977
32 | 2609573.0325 | 1177451.7787
33 | 2609458.1854 | 1177005.4981
34 | 2609598.5762 | 1177450.0244
35 | 2609398.8322 | 1177552.7317
36 | 2609503.1047 | 1177583.2984
37 | 2609534.3654 | 1177587.872
38 | 2609579.5543 | 1177599.6251
39 | 2609643.947 | 1177631.9276
40 | 2609613.9822 | 1177480.8586
41 | 2609638.9393 | 1177645.9338
42 | 2609616.8828 | 1177458.7964
43 | 2609910.703 | 1177320.52
44 | 2609632.9892 | 1177665.7162
45 | 2609626.4855 | 1177695.1541
46 | 2609660.2378 | 1177673.5004
47 | 2609511.4651 | 1177636.5866
48 | 2609534.6319 | 1177650.1871
49 | 2609527.5087 | 1177599.6264
50 | 2609553.2764 | 1177661.1328
51 | 2609596.0766 | 1177681.1165
52 | 2609602.2591 | 1177750.6105
53 | 2609601.0952 | 1177753.6935
54 | 2609620.2081 | 1177710.94
55 | 2609598.4349 | 1177761.7809
56 | 2609623.001 | 1177704.8202
57 | 2609651.0982 | 1177802.3938
58 | 2609663.7493 | 1177675.1915
59 | 2609676.0509 | 1177682.2045
60 | 2609690.9557 | 1177696.869
61 | 2609699.5327 | 1177705.5319
62 | 2609671.1396 | 1177811.0828
63 | 2609691.5855 | 1177820.0663
64 | 2609688.362 | 1177881.3145
65 | 2609724.0484 | 1177834.2073
66 | 2609756.672 | 1177848.4224
67 | 2609741.9189 | 1177841.9918
68 | 2609768.0552 | 1177853.3842
69 | 2609742.3584 | 1177853.7207
70 | 2609772.3158 | 1177855.2365
71 | 2609751.4521 | 1177857.606
72 | 2609787.1442 | 1177861.0837
73 | 2609796.6398 | 1177864.2271
74 | 2609692.5422 | 1177886.698
75 | 2609819.4336 | 1177868.1384
76 | 2609836.5247 | 1177867.6026
77 | 2609868.9906 | 1177858.3509
78 | 2609832.1317 | 1177886.0826
79 | 2609863.0057 | 1177850.237
80 | 2609870.4764 | 1177857.661
81 | 2609826.9444 | 1177893.8627
82 | 2609687.6007 | 1177733.2457
83 | 2609687.9422 | 1177732.4959
84 | 2609683.8611 | 1177741.4553
85 | 2609679.4137 | 1177748.5907
86 | 2609715.1531 | 1177717.5015
87 | 2609668.5769 | 1177759.1428
88 | 2609753.9538 | 1177737.6692
89 | 2609759.5726 | 1177707.8735
90 | 2609739.3358 | 1177673.0655
91 | 2609731.2214 | 1177656.0298
92 | 2609730.6069 | 1177654.2447
93 | 2609805.5527 | 1177766.3896
94 | 2609824.7492 | 1177798.6981
95 | 2609832.8378 | 1177749.8706
96 | 2609730.3704 | 1177648.6679
97 | 2609832.9306 | 1177810.3859
98 | 2609843.9178 | 1177743.1624
99 | 2609741.877 | 1177625.4864
100 | 2609744.3189 | 1177621.0165
101 | 2609857.5663 | 1177734.9639
102 | 2609862.4861 | 1177757.827
103 | 2609880.5153 | 1177721.1788
104 | 2609873.14 | 1177767.2188
105 | 2609885.1678 | 1177718.3841
106 | 2609876.2945 | 1177770.0623
107 | 2609841.1453 | 1177820.8294
108 | 2609873.6394 | 1177834.3052
109 | 2609920.2542 | 1177834.4449
110 | 2609818.8518 | 1177906.0903
111 | 2609924.177 | 1177697.713
112 | 2609959.6328 | 1177679.3976
113 | 2609969.1537 | 1177671.2545
114 | 2609884.6095 | 1177817.8693
115 | 2609895.3136 | 1177803.6698
116 | 2609946.718 | 1177313.1566
117 | 2609958.8468 | 1177320.7387
118 | 2609937.3035 | 1177303.9253
119 | 2610024.5266 | 1177343.9677
120 | 2610032.3534 | 1177324.4263
121 | 2609915.6927 | 1177862.2516
122 | 2609923.4479 | 1177833.2791
123 | 2609925.7961 | 1177864.8515
124 | 2609911.1267 | 1177897.2166
125 | 2609966.0039 | 1177822.9255
126 | 2609932.0983 | 1177865.6067
127 | 2609909.0705 | 1177912.2169
128 | 2609966.7789 | 1177813.1291
129 | 2609804.5607 | 1177939.5984
130 | 2609790.1005 | 1177984.3977
131 | 2609820.7285 | 1177943.5214
132 | 2609803.1478 | 1177987.8394
133 | 2609823.1956 | 1177944.12
134 | 2609803.2857 | 1177987.8758
135 | 2609848.2409 | 1177950.1971
136 | 2609853.3495 | 1177961.4445
137 | 2609852.9619 | 1177946.1249
138 | 2609859.32 | 1177945.5239
139 | 2609904.6221 | 1177948.464
140 | 2609917.9237 | 1177960.3185
141 | 2609934.7862 | 1177960.3107
142 | 2609936.3624 | 1177940.8941
143 | 2609937.5067 | 1177926.7972
144 | 2609939.0279 | 1177908.4498
145 | 2609942.1031 | 1177879.8757
146 | 2609953.9409 | 1177861.7148
147 | 2609971.2859 | 1177861.9322
148 | 2609910.117 | 1177786.4244
149 | 2609931.8898 | 1177761.0601
150 | 2609871.4185 | 1177775.0282
151 | 2609865.9084 | 1177780.6396
152 | 2609832.2939 | 1178079.761
153 | 2609820.523 | 1178088.8588
154 | 2609839.2286 | 1178074.4012
155 | 2609814.533 | 1178009.3946
156 | 2609816.4399 | 1178002.568
157 | 2609819.3595 | 1177992.1158
158 | 2609821.6511 | 1177983.9255
159 | 2609816.4889 | 1178002.3927
160 | 2609816.4848 | 1178002.4071
161 | 2609917.5415 | 1177318.4447
162 | 2609920.7854 | 1177274.2386
163 | 2609948.0137 | 1177287.7837
164 | 2609914.3695 | 1177277.0295
165 | 2609805.5527 | 1177766.3896

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1