## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_942-17_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_942-17_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_942-17_0_8_node_41 | 0.4 | n |  | TRUE
3 | bus_LV_942-17_0_8_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_942-17_0_8_node_55 | 0.4 | n |  | TRUE
5 | bus_LV_942-17_0_8_node_39 | 0.4 | n |  | TRUE
6 | bus_LV_942-17_0_8_node_56 | 0.4 | n |  | TRUE
7 | bus_LV_942-17_0_8_node_40 | 0.4 | n |  | TRUE
8 | bus_LV_942-17_0_8_node_3 | 0.4 | n |  | TRUE
9 | bus_LV_942-17_0_8_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_942-17_0_8_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_942-17_0_8_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_942-17_0_8_node_37 | 0.4 | n |  | TRUE
13 | bus_LV_942-17_0_8_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_942-17_0_8_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_942-17_0_8_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_942-17_0_8_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_942-17_0_8_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_942-17_0_8_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_942-17_0_8_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_942-17_0_8_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_942-17_0_8_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_942-17_0_8_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_942-17_0_8_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_942-17_0_8_node_32 | 0.4 | n |  | TRUE
25 | bus_LV_942-17_0_8_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_942-17_0_8_node_33 | 0.4 | n |  | TRUE
27 | bus_LV_942-17_0_8_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_942-17_0_8_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_942-17_0_8_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_942-17_0_8_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_942-17_0_8_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_942-17_0_8_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_942-17_0_8_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_942-17_0_8_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_942-17_0_8_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_942-17_0_8_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_942-17_0_8_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_942-17_0_8_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_942-17_0_8_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_942-17_0_8_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_942-17_0_8_node_48 | 0.4 | n |  | TRUE
42 | bus_LV_942-17_0_8_node_49 | 0.4 | n |  | TRUE
43 | bus_LV_942-17_0_8_node_50 | 0.4 | n |  | TRUE
44 | bus_LV_942-17_0_8_node_59 | 0.4 | n |  | TRUE
45 | bus_LV_942-17_0_8_node_58 | 0.4 | n |  | TRUE
46 | bus_LV_942-17_0_8_node_43 | 0.4 | n |  | TRUE
47 | bus_LV_942-17_0_8_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_942-17_0_8_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_942-17_0_8_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_942-17_0_8_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_942-17_0_8_node_57 | 0.4 | n |  | TRUE
52 | bus_LV_942-17_0_8_node_51 | 0.4 | n |  | TRUE
53 | bus_LV_942-17_0_8_node_52 | 0.4 | n |  | TRUE
54 | bus_LV_942-17_0_8_node_60 | 0.4 | n |  | TRUE
55 | bus_LV_942-17_0_8_node_53 | 0.4 | n |  | TRUE
56 | bus_LV_942-17_0_8_node_54 | 0.4 | n |  | TRUE
57 | bus_MV_283_0_node_31 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_942-17_0_8_load_0 | 0 | 0.034076 | 0.0085404 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_942-17_0_8_load_1 | 1 | 0.017835 | 0.0044699 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_942-17_0_8_load_2 | 3 | 0.034549 | 0.0086588 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_942-17_0_8_load_39 | 5 | 0.0055481 | 0.0013905 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_942-17_0_8_load_40 | 7 | 0.061004 | 0.015289 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_942-17_0_8_load_3 | 8 | 0.0026546 | 0.00066531 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_942-17_0_8_load_4 | 9 | 0.0039512 | 0.00099028 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_942-17_0_8_load_5 | 10 | 0.0080606 | 0.0020202 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_942-17_0_8_load_35 | 13 | 0.020365 | 0.0051038 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_942-17_0_8_load_24 | 14 | 0.0021279 | 0.00053331 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_942-17_0_8_load_23 | 15 | 0.0039197 | 0.00098237 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_942-17_0_8_load_9 | 16 | 0.0033032 | 0.00082787 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_942-17_0_8_load_10 | 17 | 0.0029542 | 0.0007404 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_942-17_0_8_load_11 | 18 | 0.007719 | 0.0019346 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_942-17_0_8_load_12 | 19 | 0.0028476 | 0.00071367 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_942-17_0_8_load_13 | 20 | 0.0035695 | 0.00089461 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_942-17_0_8_load_14 | 21 | 0.015723 | 0.0039405 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_942-17_0_8_load_25 | 22 | 0.0012087 | 0.00030293 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_942-17_0_8_load_32 | 24 | 0.001804 | 0.00045212 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_942-17_0_8_load_33 | 26 | 0.0076194 | 0.0019096 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_942-17_0_8_load_22 | 27 | 0.014538 | 0.0036435 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_942-17_0_8_load_16 | 28 | 0.012392 | 0.0031056 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_942-17_0_8_load_17 | 29 | 0.051175 | 0.012826 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_942-17_0_8_load_18 | 30 | 0.0017685 | 0.00044322 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_942-17_0_8_load_19 | 31 | 0.010589 | 0.0026537 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_942-17_0_8_load_31 | 33 | 0.00083242 | 0.00020862 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_942-17_0_8_load_29 | 34 | 0.003231 | 0.00080976 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_942-17_0_8_load_26 | 36 | 0.0015695 | 0.00039336 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_942-17_0_8_load_28 | 37 | 0.029253 | 0.0073315 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_942-17_0_8_load_30 | 38 | 0.00036443 | 9.1335e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_942-17_0_8_load_36 | 39 | 0.0021593 | 0.00054117 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_942-17_0_8_load_34 | 40 | 0.0082639 | 0.0020711 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_942-17_0_8_load_49 | 42 | 0.0076529 | 0.001918 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_942-17_0_8_load_50 | 43 | 0.030804 | 0.0077201 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_942-17_0_8_load_59 | 44 | 0.0043122 | 0.0010807 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_942-17_0_8_load_58 | 45 | 0.003235 | 0.00081077 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_942-17_0_8_load_43 | 46 | 0.002129 | 0.00053357 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_942-17_0_8_load_44 | 47 | 0.0075722 | 0.0018978 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_942-17_0_8_load_45 | 48 | 0.0024128 | 0.0006047 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_942-17_0_8_load_46 | 49 | 0.0054535 | 0.0013668 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_942-17_0_8_load_47 | 50 | 0.035833 | 0.0089806 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_942-17_0_8_load_57 | 51 | 0.0029827 | 0.00074754 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_942-17_0_8_load_52 | 53 | 0.0061323 | 0.0015369 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_942-17_0_8_load_60 | 54 | 0.005684 | 0.0014245 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_942-17_0_8_load_53 | 55 | 0.064413 | 0.016143 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_942-17_0_8_load_54 | 56 | 0.00029778 | 7.463e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 40 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_942-17_0_8_line_0 |  | 0 | 1 | 0.038669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_942-17_0_8_line_1 |  | 1 | 2 | 0.084298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_942-17_0_8_line_2 |  | 2 | 5 | 0.068153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_942-17_0_8_line_3 |  | 3 | 4 | 0.19092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_942-17_0_8_line_4 |  | 3 | 5 | 0.080966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_942-17_0_8_line_5 |  | 4 | 6 | 0.038761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_942-17_0_8_line_6 |  | 5 | 7 | 0.070133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_942-17_0_8_line_7 |  | 6 | 54 | 0.069329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_942-17_0_8_line_8 |  | 8 | 9 | 0.014605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_942-17_0_8_line_9 |  | 8 | 10 | 0.05901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_942-17_0_8_line_10 |  | 10 | 11 | 0.20287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_942-17_0_8_line_11 |  | 11 | 12 | 0.037136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_942-17_0_8_line_12 |  | 12 | 13 | 0.062958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_942-17_0_8_line_13 |  | 13 | 39 | 0.044417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_942-17_0_8_line_14 |  | 14 | 15 | 0.013317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_942-17_0_8_line_15 |  | 15 | 22 | 0.0065783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_942-17_0_8_line_16 |  | 16 | 17 | 0.01108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_942-17_0_8_line_17 |  | 16 | 18 | 0.012975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_942-17_0_8_line_18 |  | 17 | 19 | 0.011608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_942-17_0_8_line_19 |  | 18 | 20 | 0.01097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_942-17_0_8_line_20 |  | 19 | 21 | 0.050435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_942-17_0_8_line_21 |  | 20 | 22 | 0.018861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_942-17_0_8_line_22 |  | 21 | 23 | 0.048267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_942-17_0_8_line_23 |  | 23 | 24 | 0.01983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_942-17_0_8_line_24 |  | 23 | 25 | 0.030674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_942-17_0_8_line_25 |  | 24 | 26 | 0.025444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_942-17_0_8_line_26 |  | 25 | 27 | 0.017635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_942-17_0_8_line_27 |  | 26 | 40 | 0.0046519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_942-17_0_8_line_28 |  | 27 | 31 | 0.023903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_942-17_0_8_line_29 |  | 28 | 29 | 0.0080734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_942-17_0_8_line_30 |  | 28 | 30 | 0.018043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_942-17_0_8_line_31 |  | 29 | 31 | 0.013428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_942-17_0_8_line_32 |  | 30 | 32 | 0.050589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_942-17_0_8_line_33 |  | 32 | 33 | 0.025093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_942-17_0_8_line_34 |  | 32 | 34 | 0.02106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_942-17_0_8_line_35 |  | 34 | 35 | 0.0238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_942-17_0_8_line_36 |  | 35 | 38 | 0.013823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_942-17_0_8_line_37 |  | 35 | 36 | 0.017498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_942-17_0_8_line_38 |  | 36 | 37 | 0.010493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_942-17_0_8_line_39 |  | 38 | 39 | 0.022754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_942-17_0_8_line_40 |  | 40 | 41 | 0.041388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_942-17_0_8_line_41 |  | 41 | 42 | 0.024338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_942-17_0_8_line_42 |  | 41 | 43 | 0.072875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_942-17_0_8_line_43 |  | 42 | 51 | 0.039958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_942-17_0_8_line_44 |  | 43 | 52 | 0.045513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_942-17_0_8_line_45 |  | 44 | 45 | 0.00023666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_942-17_0_8_line_46 |  | 45 | 49 | 0.0071085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_942-17_0_8_line_47 |  | 46 | 47 | 0.031825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_942-17_0_8_line_48 |  | 46 | 48 | 0.019797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_942-17_0_8_line_49 |  | 47 | 49 | 0.023805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_942-17_0_8_line_50 |  | 48 | 50 | 0.0081759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_942-17_0_8_line_51 |  | 50 | 51 | 0.019154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_942-17_0_8_line_52 |  | 52 | 53 | 0.030853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_942-17_0_8_line_53 |  | 53 | 55 | 0.019453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_942-17_0_8_line_54 |  | 54 | 56 | 0.020134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_942-17_0_8_line_55 |  | 55 | 56 | 0.0092933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_942-17_0_8_trafo_34 | 0.63 MVA 20/0.4 kV | 57 | 40 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2613577.8794 | 1178797.1559 | 2613539.4797 | 1178801.7152
1 | 2613539.4797 | 1178801.7152 | 2613498.5391 | 1178728.0265
2 | 2613498.5391 | 1178728.0265 | 2613430.8945 | 1178736.3387
3 | 2613229.214 | 1178839.5195 | 2613418.7314 | 1178816.3861
4 | 2613418.7314 | 1178816.3861 | 2613430.8945 | 1178736.3387
5 | 2613205.7627 | 1178855.8319 | 2613204.8073 | 1178849.0708 | 2613215.7271 | 1178847.7941 | 2613229.9865 | 1178846.0467 | 2613229.214 | 1178839.5195
6 | 2613430.8945 | 1178736.3387 | 2613361.2856 | 1178744.8922
7 | 2613205.7627 | 1178855.8319 | 2613274.5855 | 1178847.4699
8 | 2613466.8081 | 1178946.4169 | 2613472.8057 | 1178944.3461 | 2613480.7846 | 1178942.2077
9 | 2613466.8081 | 1178946.4169 | 2613463.0807 | 1178947.7039 | 2613453.2392 | 1178951.9507 | 2613442.7212 | 1178958.0971 | 2613430.8245 | 1178965.8745 | 2613416.1793 | 1178976.2578
10 | 2613304.6219 | 1179141.5955 | 2613352.7674 | 1179050.6999 | 2613374.2166 | 1179010.3602 | 2613376.4313 | 1179007.2524 | 2613389.2002 | 1178995.3859 | 2613416.1793 | 1178976.2578
11 | 2613285.5442 | 1179125.434 | 2613284.4323 | 1179127.3436 | 2613291.4511 | 1179131.5724 | 2613301.613 | 1179137.7091 | 2613301.084 | 1179138.575 | 2613298.4849 | 1179142.8492 | 2613300.5371 | 1179144.0877 | 2613302.2852 | 1179141.2123 | 2613302.7376 | 1179140.4574 | 2613304.6219 | 1179141.5955
12 | 2613285.5442 | 1179125.434 | 2613308.9755 | 1179090.1343 | 2613319.9011 | 1179072.6822
13 | 2613319.9011 | 1179072.6822 | 2613343.4702 | 1179035.0339
14 | 2613673.3663 | 1178910.2406 | 2613660.0731 | 1178909.4526
15 | 2613653.5063 | 1178909.0633 | 2613660.0731 | 1178909.4526
16 | 2613610.83 | 1178905.8042 | 2613599.7687 | 1178905.159
17 | 2613623.7829 | 1178906.5597 | 2613610.83 | 1178905.8042
18 | 2613599.7687 | 1178905.159 | 2613588.1801 | 1178904.483
19 | 2613634.7095 | 1178907.5373 | 2613624.0996 | 1178906.5782 | 2613623.7829 | 1178906.5597
20 | 2613537.8444 | 1178906.2759 | 2613567.0229 | 1178903.948 | 2613588.0152 | 1178904.4734 | 2613588.1801 | 1178904.483
21 | 2613634.7095 | 1178907.5373 | 2613647.9377 | 1178908.7332 | 2613653.5063 | 1178909.0633
22 | 2613490.035 | 1178912.624 | 2613508.6066 | 1178909.275 | 2613526.5031 | 1178907.1808 | 2613537.8444 | 1178906.2759
23 | 2613490.035 | 1178912.624 | 2613484.2573 | 1178893.6549
24 | 2613490.035 | 1178912.624 | 2613486.9465 | 1178913.6065 | 2613469.3221 | 1178920.4483 | 2613461.9857 | 1178924.9342
25 | 2613484.2573 | 1178893.6549 | 2613483.1262 | 1178889.9414 | 2613478.4473 | 1178871.0213 | 2613478.0207 | 1178868.9935
26 | 2613461.9857 | 1178924.9342 | 2613452.6772 | 1178909.9558
27 | 2613477.063 | 1178864.4413 | 2613478.0207 | 1178868.9935
28 | 2613432.4086 | 1178912.6741 | 2613442.9357 | 1178906.4934 | 2613446.8338 | 1178905.635 | 2613449.8575 | 1178906.3532 | 2613451.5875 | 1178908.2025 | 2613452.6772 | 1178909.9558
29 | 2613420.8285 | 1178919.473 | 2613424.811 | 1178926.4958
30 | 2613433.7116 | 1178942.1911 | 2613424.811 | 1178926.4958
31 | 2613420.8285 | 1178919.473 | 2613420.8285 | 1178919.473 | 2613432.4086 | 1178912.6741
32 | 2613433.7116 | 1178942.1911 | 2613401.1383 | 1178962.0954 | 2613391.0302 | 1178969.4767
33 | 2613391.0302 | 1178969.4767 | 2613378.8635 | 1178947.5162
34 | 2613391.0302 | 1178969.4767 | 2613382.3728 | 1178977.2058 | 2613376.0927 | 1178984.2733
35 | 2613362.8785 | 1179004.0318 | 2613370.4154 | 1178991.7089 | 2613376.0927 | 1178984.2733
36 | 2613362.8785 | 1179004.0318 | 2613355.5438 | 1179015.7479
37 | 2613362.8785 | 1179004.0318 | 2613357.007 | 1178999.1163 | 2613351.6824 | 1178995.6361 | 2613348.7016 | 1178993.8412
38 | 2613339.7121 | 1178988.4281 | 2613348.7016 | 1178993.8412
39 | 2613343.4702 | 1179035.0339 | 2613355.5438 | 1179015.7479
40 | 2613471.2502 | 1178823.4809 | 2613473.2134 | 1178840.6607 | 2613474.8149 | 1178852.1479 | 2613476.5122 | 1178861.8233 | 2613477.063 | 1178864.4413
41 | 2613471.2502 | 1178823.4809 | 2613495.4159 | 1178820.5904
42 | 2613471.2502 | 1178823.4809 | 2613398.9135 | 1178832.3183
43 | 2613495.4159 | 1178820.5904 | 2613535.0913 | 1178815.8448
44 | 2613353.7359 | 1178837.8377 | 2613398.9135 | 1178832.3183
45 | 2613643.8575 | 1178807.8947 | 2613643.6304 | 1178807.9611
46 | 2613636.6583 | 1178809.0567 | 2613636.6583 | 1178809.0567 | 2613640.4632 | 1178808.8875 | 2613643.6304 | 1178807.9611
47 | 2613581.8843 | 1178810.2478 | 2613613.4836 | 1178806.4682
48 | 2613581.8843 | 1178810.2478 | 2613562.2278 | 1178812.5989
49 | 2613636.6583 | 1178809.0567 | 2613632.6727 | 1178808.0583 | 2613628.9407 | 1178806.349 | 2613625.3977 | 1178805.5517 | 2613619.4918 | 1178805.7495 | 2613613.4836 | 1178806.4682
50 | 2613554.1098 | 1178813.57 | 2613562.2278 | 1178812.5989
51 | 2613554.1098 | 1178813.57 | 2613535.0913 | 1178815.8448
52 | 2613353.7359 | 1178837.8377 | 2613333.1033 | 1178840.36 | 2613323.1098 | 1178841.5742
53 | 2613323.1098 | 1178841.5742 | 2613303.7984 | 1178843.9205
54 | 2613274.5855 | 1178847.4699 | 2613294.5729 | 1178845.0414
55 | 2613303.7984 | 1178843.9205 | 2613294.5729 | 1178845.0414

## bus_geodata
| x | y | coords
0 | 2613577.8794 | 1178797.1559
1 | 2613539.4797 | 1178801.7152
2 | 2613498.5391 | 1178728.0265
3 | 2613418.7314 | 1178816.3861
4 | 2613229.214 | 1178839.5195
5 | 2613430.8945 | 1178736.3387
6 | 2613205.7627 | 1178855.8319
7 | 2613361.2856 | 1178744.8922
8 | 2613466.8081 | 1178946.4169
9 | 2613480.7846 | 1178942.2077
10 | 2613416.1793 | 1178976.2578
11 | 2613304.6219 | 1179141.5955
12 | 2613285.5442 | 1179125.434
13 | 2613319.9011 | 1179072.6822
14 | 2613673.3663 | 1178910.2406
15 | 2613660.0731 | 1178909.4526
16 | 2613610.83 | 1178905.8042
17 | 2613599.7687 | 1178905.159
18 | 2613623.7829 | 1178906.5597
19 | 2613588.1801 | 1178904.483
20 | 2613634.7095 | 1178907.5373
21 | 2613537.8444 | 1178906.276
22 | 2613653.5063 | 1178909.0633
23 | 2613490.035 | 1178912.624
24 | 2613484.2573 | 1178893.6549
25 | 2613461.9857 | 1178924.9342
26 | 2613478.0207 | 1178868.9935
27 | 2613452.6772 | 1178909.9558
28 | 2613424.811 | 1178926.4958
29 | 2613420.8285 | 1178919.473
30 | 2613433.7116 | 1178942.1911
31 | 2613432.4086 | 1178912.6741
32 | 2613391.0302 | 1178969.4767
33 | 2613378.8635 | 1178947.5162
34 | 2613376.0927 | 1178984.2733
35 | 2613362.8785 | 1179004.0318
36 | 2613348.7016 | 1178993.8412
37 | 2613339.7121 | 1178988.4281
38 | 2613355.5438 | 1179015.7479
39 | 2613343.4702 | 1179035.0339
40 | 2613477.063 | 1178864.4413
41 | 2613471.2502 | 1178823.4809
42 | 2613495.4159 | 1178820.5904
43 | 2613398.9135 | 1178832.3183
44 | 2613643.8575 | 1178807.8947
45 | 2613643.6304 | 1178807.9611
46 | 2613581.8843 | 1178810.2478
47 | 2613613.4836 | 1178806.4682
48 | 2613562.2278 | 1178812.5989
49 | 2613636.6583 | 1178809.0567
50 | 2613554.1098 | 1178813.57
51 | 2613535.0913 | 1178815.8448
52 | 2613353.7359 | 1178837.8377
53 | 2613323.1098 | 1178841.5742
54 | 2613274.5855 | 1178847.4699
55 | 2613303.7984 | 1178843.9205
56 | 2613294.5729 | 1178845.0414
57 | 2613471.2502 | 1178823.4809

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1