## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2472-1_1_2_node_128 | 0.4 | n |  | TRUE
1 | bus_LV_2472-1_1_2_node_127 | 0.4 | n |  | TRUE
2 | bus_LV_2472-1_1_2_node_130 | 0.4 | n |  | TRUE
3 | bus_LV_2472-1_1_2_node_193 | 0.4 | n |  | TRUE
4 | bus_LV_2472-1_1_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2472-1_1_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2472-1_1_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2472-1_1_2_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2472-1_1_2_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_2472-1_1_2_node_173 | 0.4 | n |  | TRUE
10 | bus_LV_2472-1_1_2_node_132 | 0.4 | n |  | TRUE
11 | bus_LV_2472-1_1_2_node_158 | 0.4 | n |  | TRUE
12 | bus_LV_2472-1_1_2_node_133 | 0.4 | n |  | TRUE
13 | bus_LV_2472-1_1_2_node_134 | 0.4 | n |  | TRUE
14 | bus_LV_2472-1_1_2_node_135 | 0.4 | n |  | TRUE
15 | bus_LV_2472-1_1_2_node_136 | 0.4 | n |  | TRUE
16 | bus_LV_2472-1_1_2_node_137 | 0.4 | n |  | TRUE
17 | bus_LV_2472-1_1_2_node_47 | 0.4 | n |  | TRUE
18 | bus_LV_2472-1_1_2_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_2472-1_1_2_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_2472-1_1_2_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_2472-1_1_2_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_2472-1_1_2_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_2472-1_1_2_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_2472-1_1_2_node_51 | 0.4 | n |  | TRUE
25 | bus_LV_2472-1_1_2_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_2472-1_1_2_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_2472-1_1_2_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_2472-1_1_2_node_159 | 0.4 | n |  | TRUE
29 | bus_LV_2472-1_1_2_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_2472-1_1_2_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_2472-1_1_2_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_2472-1_1_2_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_2472-1_1_2_node_221 | 0.4 | n |  | TRUE
34 | bus_LV_2472-1_1_2_node_155 | 0.4 | n |  | TRUE
35 | bus_LV_2472-1_1_2_node_92 | 0.4 | n |  | TRUE
36 | bus_LV_2472-1_1_2_node_156 | 0.4 | n |  | TRUE
37 | bus_LV_2472-1_1_2_node_38 | 0.4 | n |  | TRUE
38 | bus_LV_2472-1_1_2_node_157 | 0.4 | n |  | TRUE
39 | bus_LV_2472-1_1_2_node_190 | 0.4 | n |  | TRUE
40 | bus_LV_2472-1_1_2_node_183 | 0.4 | n |  | TRUE
41 | bus_LV_2472-1_1_2_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_2472-1_1_2_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_2472-1_1_2_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_2472-1_1_2_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_2472-1_1_2_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_2472-1_1_2_node_208 | 0.4 | n |  | TRUE
47 | bus_LV_2472-1_1_2_node_170 | 0.4 | n |  | TRUE
48 | bus_LV_2472-1_1_2_node_168 | 0.4 | n |  | TRUE
49 | bus_LV_2472-1_1_2_node_169 | 0.4 | n |  | TRUE
50 | bus_LV_2472-1_1_2_node_171 | 0.4 | n |  | TRUE
51 | bus_LV_2472-1_1_2_node_192 | 0.4 | n |  | TRUE
52 | bus_LV_2472-1_1_2_node_174 | 0.4 | n |  | TRUE
53 | bus_LV_2472-1_1_2_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_2472-1_1_2_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_2472-1_1_2_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_2472-1_1_2_node_175 | 0.4 | n |  | TRUE
57 | bus_LV_2472-1_1_2_node_219 | 0.4 | n |  | TRUE
58 | bus_LV_2472-1_1_2_node_138 | 0.4 | n |  | TRUE
59 | bus_LV_2472-1_1_2_node_139 | 0.4 | n |  | TRUE
60 | bus_LV_2472-1_1_2_node_140 | 0.4 | n |  | TRUE
61 | bus_LV_2472-1_1_2_node_141 | 0.4 | n |  | TRUE
62 | bus_LV_2472-1_1_2_node_113 | 0.4 | n |  | TRUE
63 | bus_LV_2472-1_1_2_node_142 | 0.4 | n |  | TRUE
64 | bus_LV_2472-1_1_2_node_194 | 0.4 | n |  | TRUE
65 | bus_LV_2472-1_1_2_node_224 | 0.4 | n |  | TRUE
66 | bus_LV_2472-1_1_2_node_87 | 0.4 | n |  | TRUE
67 | bus_LV_2472-1_1_2_node_88 | 0.4 | n |  | TRUE
68 | bus_LV_2472-1_1_2_node_89 | 0.4 | n |  | TRUE
69 | bus_LV_2472-1_1_2_node_91 | 0.4 | n |  | TRUE
70 | bus_LV_2472-1_1_2_node_112 | 0.4 | n |  | TRUE
71 | bus_LV_2472-1_1_2_node_110 | 0.4 | n |  | TRUE
72 | bus_LV_2472-1_1_2_node_220 | 0.4 | n |  | TRUE
73 | bus_LV_2472-1_1_2_node_111 | 0.4 | n |  | TRUE
74 | bus_LV_2472-1_1_2_node_114 | 0.4 | n |  | TRUE
75 | bus_MV_285_0_node_4 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2472-1_1_2_load_128 | 0 | 0.00093845 | 0.0002352 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2472-1_1_2_load_127 | 1 | 0.0012126 | 0.00030391 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2472-1_1_2_load_130 | 2 | 0.0005869 | 0.00014709 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2472-1_1_2_load_193 | 3 | 0.00099708 | 0.00024989 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2472-1_1_2_load_4 | 4 | 0.0032552 | 0.00081584 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2472-1_1_2_load_6 | 6 | 0.0018158 | 0.00045509 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2472-1_1_2_load_7 | 7 | 0.0013247 | 0.000332 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2472-1_1_2_load_8 | 8 | 0.001495 | 0.00037468 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2472-1_1_2_load_173 | 9 | 0.0012968 | 0.00032502 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2472-1_1_2_load_132 | 10 | 0.00083878 | 0.00021022 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2472-1_1_2_load_158 | 11 | 0.00087889 | 0.00022027 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2472-1_1_2_load_133 | 12 | 0.0023998 | 0.00060145 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2472-1_1_2_load_134 | 13 | 0.0024195 | 0.00060638 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2472-1_1_2_load_135 | 14 | 0.0027854 | 0.00069808 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2472-1_1_2_load_136 | 15 | 0.0042401 | 0.0010627 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2472-1_1_2_load_137 | 16 | 0.00218 | 0.00054635 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2472-1_1_2_load_47 | 17 | 0.0026742 | 0.00067021 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2472-1_1_2_load_14 | 18 | 0.003987 | 0.00099924 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2472-1_1_2_load_15 | 19 | 0.00271 | 0.00067919 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2472-1_1_2_load_16 | 20 | 0.0075219 | 0.0018852 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2472-1_1_2_load_17 | 21 | 0.0018392 | 0.00046096 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2472-1_1_2_load_18 | 22 | 0.010551 | 0.0026442 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2472-1_1_2_load_21 | 23 | 0.0012034 | 0.00030159 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2472-1_1_2_load_51 | 24 | 0.003936 | 0.00098646 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2472-1_1_2_load_19 | 25 | 0.0026837 | 0.00067259 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2472-1_1_2_load_20 | 26 | 0.0013415 | 0.00033622 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2472-1_1_2_load_22 | 27 | 0.0018967 | 0.00047537 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2472-1_1_2_load_159 | 28 | 0.0013394 | 0.00033569 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2472-1_1_2_load_23 | 29 | 0.0011486 | 0.00028786 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2472-1_1_2_load_27 | 31 | 0.0010094 | 0.00025297 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2472-1_1_2_load_28 | 32 | 0.0012385 | 0.0003104 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2472-1_1_2_load_221 | 33 | 0.0014288 | 0.00035809 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2472-1_1_2_load_155 | 34 | 0.0031169 | 0.00078117 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2472-1_1_2_load_92 | 35 | 0.0019309 | 0.00048392 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2472-1_1_2_load_156 | 36 | 0.0024253 | 0.00060784 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2472-1_1_2_load_38 | 37 | 0.0035317 | 0.00088514 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2472-1_1_2_load_157 | 38 | 0.00498 | 0.0012481 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2472-1_1_2_load_190 | 39 | 0.0014148 | 0.00035457 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2472-1_1_2_load_183 | 40 | 0.0027313 | 0.00068452 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2472-1_1_2_load_34 | 41 | 0.0016904 | 0.00042366 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2472-1_1_2_load_35 | 42 | 0.0017257 | 0.00043249 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2472-1_1_2_load_39 | 45 | 0.0023087 | 0.00057861 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2472-1_1_2_load_208 | 46 | 0.0015609 | 0.0003912 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2472-1_1_2_load_170 | 47 | 0.0045513 | 0.0011407 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2472-1_1_2_load_168 | 48 | 0.0019147 | 0.00047986 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2472-1_1_2_load_169 | 49 | 0.0055911 | 0.0014013 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2472-1_1_2_load_171 | 50 | 0.0022592 | 0.00056622 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2472-1_1_2_load_192 | 51 | 0.0019974 | 0.00050059 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2472-1_1_2_load_174 | 52 | 0.0010944 | 0.00027429 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2472-1_1_2_load_46 | 53 | 0.0019833 | 0.00049706 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2472-1_1_2_load_48 | 54 | 0.0024296 | 0.00060892 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2472-1_1_2_load_50 | 55 | 0.0025848 | 0.00064782 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2472-1_1_2_load_219 | 57 | 0.0015393 | 0.00038579 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2472-1_1_2_load_138 | 58 | 0.0024567 | 0.00061571 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2472-1_1_2_load_139 | 59 | 0.001901 | 0.00047645 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2472-1_1_2_load_141 | 61 | 0.0029864 | 0.00074847 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2472-1_1_2_load_113 | 62 | 0.0027922 | 0.0006998 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2472-1_1_2_load_142 | 63 | 0.0029061 | 0.00072833 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2472-1_1_2_load_194 | 64 | 0.0011512 | 0.00028853 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2472-1_1_2_load_224 | 65 | 0.0028657 | 0.00071822 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2472-1_1_2_load_87 | 66 | 0.0019162 | 0.00048024 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2472-1_1_2_load_88 | 67 | 0.0015079 | 0.0003779 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2472-1_1_2_load_112 | 70 | 0.0032804 | 0.00082214 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2472-1_1_2_load_110 | 71 | 0.0012629 | 0.00031651 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2472-1_1_2_load_220 | 72 | 0.0012305 | 0.0003084 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2472-1_1_2_load_114 | 74 | 0.003935 | 0.0009862 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 63 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2472-1_1_2_line_0 |  | 0 | 1 | 0.026981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2472-1_1_2_line_1 |  | 0 | 2 | 0.011906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2472-1_1_2_line_2 |  | 2 | 3 | 0.017189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2472-1_1_2_line_3 |  | 3 | 64 | 0.0064247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2472-1_1_2_line_4 |  | 4 | 5 | 0.038088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2472-1_1_2_line_5 |  | 4 | 6 | 0.01325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2472-1_1_2_line_6 |  | 5 | 7 | 0.022203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2472-1_1_2_line_7 |  | 5 | 8 | 0.0057746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2472-1_1_2_line_8 |  | 7 | 9 | 0.022905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2472-1_1_2_line_9 |  | 9 | 52 | 0.018459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2472-1_1_2_line_10 |  | 10 | 11 | 0.018023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2472-1_1_2_line_11 |  | 11 | 31 | 0.0035218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2472-1_1_2_line_12 |  | 12 | 13 | 0.0099631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2472-1_1_2_line_13 |  | 12 | 14 | 0.0032561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2472-1_1_2_line_14 |  | 13 | 15 | 0.0062214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2472-1_1_2_line_15 |  | 14 | 16 | 0.021525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2472-1_1_2_line_16 |  | 14 | 17 | 0.073628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2472-1_1_2_line_17 |  | 16 | 34 | 0.0012806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2472-1_1_2_line_18 |  | 17 | 53 | 0.0026456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2472-1_1_2_line_19 |  | 18 | 19 | 0.0043402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2472-1_1_2_line_20 |  | 18 | 20 | 0.036599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2472-1_1_2_line_21 |  | 19 | 21 | 0.01596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2472-1_1_2_line_22 |  | 20 | 22 | 0.011948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2472-1_1_2_line_23 |  | 21 | 23 | 0.0031208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2472-1_1_2_line_24 |  | 22 | 24 | 0.024725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2472-1_1_2_line_25 |  | 23 | 25 | 0.01315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2472-1_1_2_line_26 |  | 24 | 38 | 0.012029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2472-1_1_2_line_27 |  | 25 | 26 | 0.045077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2472-1_1_2_line_28 |  | 26 | 27 | 0.0034843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2472-1_1_2_line_29 |  | 27 | 28 | 0.0036127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2472-1_1_2_line_30 |  | 28 | 40 | 0.021761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2472-1_1_2_line_31 |  | 29 | 30 | 0.01621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2472-1_1_2_line_32 |  | 30 | 31 | 0.01743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2472-1_1_2_line_33 |  | 30 | 32 | 0.013854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2472-1_1_2_line_34 |  | 32 | 33 | 0.022666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2472-1_1_2_line_35 |  | 33 | 72 | 0.022053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2472-1_1_2_line_36 |  | 34 | 35 | 0.022218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2472-1_1_2_line_37 |  | 35 | 68 | 0.021678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2472-1_1_2_line_38 |  | 36 | 37 | 0.0015481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2472-1_1_2_line_39 |  | 37 | 43 | 0.020547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2472-1_1_2_line_40 |  | 38 | 39 | 0.020746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2472-1_1_2_line_41 |  | 39 | 44 | 0.012072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2472-1_1_2_line_42 |  | 40 | 56 | 0.019579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2472-1_1_2_line_43 |  | 41 | 42 | 0.021739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2472-1_1_2_line_44 |  | 41 | 43 | 0.017808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2472-1_1_2_line_45 |  | 42 | 44 | 0.015585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2472-1_1_2_line_46 |  | 43 | 45 | 0.012379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2472-1_1_2_line_47 |  | 44 | 46 | 0.0042957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2472-1_1_2_line_48 |  | 45 | 47 | 0.032422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2472-1_1_2_line_49 |  | 46 | 65 | 0.022088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2472-1_1_2_line_50 |  | 47 | 48 | 0.00054896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2472-1_1_2_line_51 |  | 48 | 49 | 0.027293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2472-1_1_2_line_52 |  | 49 | 50 | 0.0038844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2472-1_1_2_line_53 |  | 50 | 51 | 0.026118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2472-1_1_2_line_54 |  | 51 | 61 | 0.0017886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2472-1_1_2_line_55 |  | 52 | 56 | 0.024859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2472-1_1_2_line_56 |  | 53 | 54 | 0.018849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2472-1_1_2_line_57 |  | 54 | 55 | 0.0067626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2472-1_1_2_line_58 |  | 56 | 57 | 0.011869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2472-1_1_2_line_59 |  | 57 | 64 | 0.024862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2472-1_1_2_line_60 |  | 58 | 59 | 0.020539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2472-1_1_2_line_61 |  | 58 | 60 | 0.01056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2472-1_1_2_line_62 |  | 59 | 61 | 0.010479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2472-1_1_2_line_63 |  | 60 | 62 | 0.021508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2472-1_1_2_line_64 |  | 60 | 63 | 0.030626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_2472-1_1_2_line_65 |  | 62 | 73 | 0.018193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2472-1_1_2_line_66 |  | 66 | 67 | 0.028217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2472-1_1_2_line_67 |  | 66 | 68 | 0.011587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2472-1_1_2_line_68 |  | 68 | 69 | 0.021565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2472-1_1_2_line_69 |  | 69 | 70 | 0.023415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2472-1_1_2_line_70 |  | 69 | 71 | 0.014812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2472-1_1_2_line_71 |  | 70 | 72 | 0.032988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2472-1_1_2_line_72 |  | 71 | 73 | 0.029322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2472-1_1_2_line_73 |  | 73 | 74 | 0.04465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2472-1_1_2_trafo_142 | 0.63 MVA 20/0.4 kV | 75 | 63 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2617738.9769 | 1255613.5222 | 2617718.0113 | 1255596.5392
1 | 2617738.9769 | 1255613.5222 | 2617748.2281 | 1255621.0161
2 | 2617761.5845 | 1255631.8354 | 2617748.2281 | 1255621.0161
3 | 2617761.5845 | 1255631.8354 | 2617766.5768 | 1255635.8794
4 | 2617873.3563 | 1255656.3711 | 2617875.0633 | 1255663.0251 | 2617878.4579 | 1255670.2624 | 2617883.6868 | 1255674.4365 | 2617898.7506 | 1255681.2529
5 | 2617910.8223 | 1255686.7153 | 2617898.7506 | 1255681.2529
6 | 2617873.3563 | 1255656.3711 | 2617855.4649 | 1255647.2001 | 2617853.409 | 1255646.7831
7 | 2617873.3563 | 1255656.3711 | 2617878.5282 | 1255654.4298 | 2617878.7779 | 1255654.4116
8 | 2617853.409 | 1255646.7831 | 2617845.0034 | 1255645.0784 | 2617830.8848 | 1255642.6356
9 | 2617812.6965 | 1255639.4888 | 2617830.8848 | 1255642.6356
10 | 2617753.063 | 1255595.8437 | 2617735.141 | 1255593.938
11 | 2617753.063 | 1255595.8437 | 2617756.5651 | 1255596.2162
12 | 2617937.3525 | 1255564.7666 | 2617927.3973 | 1255564.3704
13 | 2617924.1437 | 1255564.2458 | 2617924.7368 | 1255564.2645 | 2617927.3973 | 1255564.3704
14 | 2617937.3525 | 1255564.7666 | 2617943.569 | 1255565.0139
15 | 2617902.6292 | 1255563.5666 | 2617924.1437 | 1255564.2458
16 | 2617924.1437 | 1255564.2458 | 2617925.9033 | 1255490.639
17 | 2617902.6292 | 1255563.5666 | 2617901.3493 | 1255563.5262
18 | 2617928.5071 | 1255490.1704 | 2617925.9033 | 1255490.639
19 | 2617913.067 | 1255714.9715 | 2617909.189 | 1255713.0224
20 | 2617944.5404 | 1255733.6283 | 2617916.9003 | 1255716.8982 | 2617913.067 | 1255714.9715
21 | 2617909.189 | 1255713.0224 | 2617894.9292 | 1255705.8551
22 | 2617944.5404 | 1255733.6283 | 2617954.7619 | 1255739.8153
23 | 2617892.1408 | 1255704.4536 | 2617894.9292 | 1255705.8551
24 | 2617954.7619 | 1255739.8153 | 2617975.9143 | 1255752.6185
25 | 2617892.1408 | 1255704.4536 | 2617880.3918 | 1255698.5483
26 | 2617986.2055 | 1255758.8476 | 2617975.9143 | 1255752.6185
27 | 2617880.3918 | 1255698.5483 | 2617840.1157 | 1255678.3048
28 | 2617840.1157 | 1255678.3048 | 2617837.0025 | 1255676.7401
29 | 2617837.0025 | 1255676.7401 | 2617833.7746 | 1255675.1177
30 | 2617814.3316 | 1255665.3453 | 2617833.7746 | 1255675.1177
31 | 2617767.4893 | 1255587.3187 | 2617765.6731 | 1255584.3335 | 2617767.1513 | 1255571.7043
32 | 2617767.4893 | 1255587.3187 | 2617763.5387 | 1255596.9577 | 2617756.5651 | 1255596.2162
33 | 2617767.4893 | 1255587.3187 | 2617772.2344 | 1255589.3898 | 2617780.911 | 1255589.3532
34 | 2617803.5771 | 1255589.2576 | 2617780.911 | 1255589.3532
35 | 2617825.6299 | 1255589.1832 | 2617824.6277 | 1255589.1688 | 2617803.5771 | 1255589.2576
36 | 2617901.3493 | 1255563.5262 | 2617879.1421 | 1255562.8251
37 | 2617859.8357 | 1255568.0939 | 2617861.7075 | 1255565.1086 | 2617864.7987 | 1255562.9053 | 2617870.6145 | 1255562.5559 | 2617879.1421 | 1255562.8251
38 | 2618063.9138 | 1255746.9806 | 2618064.1031 | 1255747.1975 | 2618064.887 | 1255748.1842
39 | 2618050.4026 | 1255731.501 | 2618063.9138 | 1255746.9806
40 | 2618003.9536 | 1255769.5903 | 2617986.2055 | 1255758.8476
41 | 2618015.1305 | 1255773.7665 | 2618008.0993 | 1255772.0996 | 2618003.9536 | 1255769.5903
42 | 2617796.8379 | 1255656.5526 | 2617814.3316 | 1255665.3453
43 | 2618025.2446 | 1255761.9522 | 2618038.486 | 1255744.7106
44 | 2618050.4026 | 1255731.501 | 2618041.1042 | 1255741.3015 | 2618038.486 | 1255744.7106
45 | 2618015.1305 | 1255773.7665 | 2618019.5935 | 1255769.3104 | 2618025.2446 | 1255761.9522
46 | 2618050.4026 | 1255731.501 | 2618041.7691 | 1255722.63
47 | 2618015.1305 | 1255773.7665 | 2618013.0328 | 1255777.5152
48 | 2618041.7691 | 1255722.63 | 2618019.1562 | 1255699.3953
49 | 2618000.0631 | 1255795.3316 | 2618010.3914 | 1255782.2356 | 2618013.0328 | 1255777.5152
50 | 2618018.7734 | 1255699.0019 | 2618019.1562 | 1255699.3953
51 | 2617998.5855 | 1255680.6989 | 2618010.203 | 1255690.1959 | 2618018.7734 | 1255699.0019
52 | 2617998.5855 | 1255680.6989 | 2617995.5781 | 1255678.2404
53 | 2617975.3568 | 1255661.71 | 2617995.5781 | 1255678.2404
54 | 2617973.972 | 1255660.578 | 2617975.3568 | 1255661.71
55 | 2617796.8379 | 1255656.5526 | 2617802.7486 | 1255644.6291 | 2617808.1766 | 1255640.2646 | 2617812.6965 | 1255639.4888 | 2617812.6965 | 1255639.4888
56 | 2617928.5071 | 1255490.1704 | 2617938.2244 | 1255488.4214 | 2617946.9022 | 1255486.1283
57 | 2617953.4197 | 1255484.3355 | 2617952.7844 | 1255484.5739 | 2617946.9022 | 1255486.1283
58 | 2617796.8379 | 1255656.5526 | 2617786.6813 | 1255650.4108
59 | 2617786.6813 | 1255650.4108 | 2617778.1382 | 1255645.2447 | 2617766.5768 | 1255635.8794
60 | 2617949.9567 | 1255640.9462 | 2617965.8586 | 1255653.9455
61 | 2617941.7809 | 1255634.2626 | 2617949.9567 | 1255640.9462
62 | 2617973.972 | 1255660.578 | 2617965.8586 | 1255653.9455
63 | 2617941.7809 | 1255634.2626 | 2617925.4066 | 1255620.3171
64 | 2617941.7809 | 1255634.2626 | 2617939.3055 | 1255649.81 | 2617938.6944 | 1255652.3765 | 2617937.6596 | 1255655.3865 | 2617933.5499 | 1255657.709 | 2617929.2191 | 1255658.011
65 | 2617911.556 | 1255608.5209 | 2617925.4066 | 1255620.3171
66 | 2617849.4858 | 1255562.8854 | 2617824.2806 | 1255550.2012
67 | 2617859.8357 | 1255568.0939 | 2617849.4858 | 1255562.8854
68 | 2617877.8472 | 1255580.0338 | 2617859.8357 | 1255568.0939
69 | 2617877.8472 | 1255580.0338 | 2617875.5129 | 1255583.8293 | 2617871.6773 | 1255587.7981 | 2617866.6863 | 1255589.7733 | 2617858.6148 | 1255589.6573
70 | 2617877.8472 | 1255580.0338 | 2617889.1605 | 1255589.5946
71 | 2617858.6148 | 1255589.6573 | 2617825.6299 | 1255589.1832
72 | 2617911.556 | 1255608.5209 | 2617889.1605 | 1255589.5946
73 | 2617904.1001 | 1255637.5623 | 2617892.9823 | 1255635.5163 | 2617894.1167 | 1255629.4712 | 2617911.556 | 1255608.5209

## bus_geodata
| x | y | coords
0 | 2617738.9769 | 1255613.5222
1 | 2617718.0113 | 1255596.5392
2 | 2617748.2281 | 1255621.0161
3 | 2617761.5845 | 1255631.8354
4 | 2617898.7506 | 1255681.2529
5 | 2617873.3563 | 1255656.3711
6 | 2617910.8223 | 1255686.7153
7 | 2617853.409 | 1255646.7831
8 | 2617878.7779 | 1255654.4116
9 | 2617830.8848 | 1255642.6356
10 | 2617735.141 | 1255593.938
11 | 2617753.063 | 1255595.8437
12 | 2617927.3973 | 1255564.3704
13 | 2617937.3525 | 1255564.7666
14 | 2617924.1437 | 1255564.2458
15 | 2617943.569 | 1255565.0139
16 | 2617902.6292 | 1255563.5666
17 | 2617925.9033 | 1255490.639
18 | 2617913.067 | 1255714.9715
19 | 2617909.189 | 1255713.0224
20 | 2617944.5404 | 1255733.6283
21 | 2617894.9292 | 1255705.8551
22 | 2617954.7619 | 1255739.8153
23 | 2617892.1408 | 1255704.4536
24 | 2617975.9143 | 1255752.6185
25 | 2617880.3918 | 1255698.5483
26 | 2617840.1157 | 1255678.3048
27 | 2617837.0025 | 1255676.7401
28 | 2617833.7746 | 1255675.1177
29 | 2617767.1513 | 1255571.7043
30 | 2617767.4893 | 1255587.3187
31 | 2617756.5651 | 1255596.2162
32 | 2617780.911 | 1255589.3532
33 | 2617803.5771 | 1255589.2576
34 | 2617901.3493 | 1255563.5262
35 | 2617879.1421 | 1255562.8251
36 | 2618064.887 | 1255748.1842
37 | 2618063.9138 | 1255746.9806
38 | 2617986.2055 | 1255758.8476
39 | 2618003.9536 | 1255769.5903
40 | 2617814.3316 | 1255665.3453
41 | 2618038.486 | 1255744.7106
42 | 2618025.2446 | 1255761.9522
43 | 2618050.4026 | 1255731.501
44 | 2618015.1305 | 1255773.7665
45 | 2618041.7691 | 1255722.63
46 | 2618013.0328 | 1255777.5152
47 | 2618019.1562 | 1255699.3953
48 | 2618018.7734 | 1255699.0019
49 | 2617998.5855 | 1255680.6989
50 | 2617995.5781 | 1255678.2404
51 | 2617975.3568 | 1255661.71
52 | 2617812.6965 | 1255639.4888
53 | 2617928.5071 | 1255490.1704
54 | 2617946.9022 | 1255486.1283
55 | 2617953.4197 | 1255484.3355
56 | 2617796.8379 | 1255656.5526
57 | 2617786.6813 | 1255650.4108
58 | 2617949.9567 | 1255640.9462
59 | 2617965.8586 | 1255653.9455
60 | 2617941.7809 | 1255634.2626
61 | 2617973.972 | 1255660.578
62 | 2617925.4066 | 1255620.3171
63 | 2617929.2191 | 1255658.011
64 | 2617766.5768 | 1255635.8794
65 | 2618000.0631 | 1255795.3316
66 | 2617849.4858 | 1255562.8854
67 | 2617824.2806 | 1255550.2012
68 | 2617859.8357 | 1255568.0939
69 | 2617877.8472 | 1255580.0338
70 | 2617858.6148 | 1255589.6573
71 | 2617889.1605 | 1255589.5946
72 | 2617825.6299 | 1255589.1832
73 | 2617911.556 | 1255608.5209
74 | 2617904.1001 | 1255637.5623
75 | 2617941.7809 | 1255634.2626

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97313 | -0.51872 | 0.00093845 | 0.0002352
1 | 0.9731 | -0.51932 | 0.0012126 | 0.00030391
2 | 0.97315 | -0.51825 | 0.0005869 | 0.00014709
3 | 0.9732 | -0.51738 | 0.00099708 | 0.00024989
4 | 0.97252 | -0.5307 | 0.0032552 | 0.00081584
5 | 0.9727 | -0.52714 | 0 | 0
6 | 0.9725 | -0.53115 | 0.0018158 | 0.00045509
7 | 0.97284 | -0.52446 | 0.0013247 | 0.000332
8 | 0.97269 | -0.5273 | 0.001495 | 0.00037468
9 | 0.97301 | -0.52113 | 0.0012968 | 0.00032502
10 | 0.99339 | -0.12656 | 0.00083878 | 0.00021022
11 | 0.99341 | -0.1263 | 0.00087889 | 0.00022027
12 | 0.99199 | -0.15376 | 0.0023998 | 0.00060145
13 | 0.99193 | -0.15494 | 0.0024195 | 0.00060638
14 | 0.99201 | -0.15324 | 0.0027854 | 0.00069808
15 | 0.9919 | -0.1554 | 0.0042401 | 0.0010627
16 | 0.99244 | -0.14504 | 0.00218 | 0.00054635
17 | 0.99136 | -0.16586 | 0.0026742 | 0.00067021
18 | 0.97623 | -0.45751 | 0.003987 | 0.00099924
19 | 0.9761 | -0.46009 | 0.00271 | 0.00067919
20 | 0.97748 | -0.43314 | 0.0075219 | 0.0018852
21 | 0.97566 | -0.46878 | 0.0018392 | 0.00046096
22 | 0.97796 | -0.42356 | 0.010551 | 0.0026442
23 | 0.97558 | -0.47037 | 0.0012034 | 0.00030159
24 | 0.97922 | -0.39902 | 0.003936 | 0.00098646
25 | 0.97525 | -0.47681 | 0.0026837 | 0.00067259
26 | 0.97424 | -0.49668 | 0.0013415 | 0.00033622
27 | 0.97417 | -0.49813 | 0.0018967 | 0.00047537
28 | 0.9741 | -0.49951 | 0.0013394 | 0.00033569
29 | 0.99344 | -0.12568 | 0.0011486 | 0.00028786
30 | 0.99346 | -0.12535 | 0 | 0
31 | 0.99341 | -0.12619 | 0.0010094 | 0.00025297
32 | 0.99351 | -0.1244 | 0.0012385 | 0.0003104
33 | 0.99361 | -0.12235 | 0.0014288 | 0.00035809
34 | 0.99246 | -0.1445 | 0.0031169 | 0.00078117
35 | 0.99301 | -0.13396 | 0.0019309 | 0.00048392
36 | 0.98535 | -0.2799 | 0.0024253 | 0.00060784
37 | 0.98535 | -0.27983 | 0.0035317 | 0.00088514
38 | 0.97987 | -0.38625 | 0.00498 | 0.0012481
39 | 0.98109 | -0.36239 | 0.0014148 | 0.00035457
40 | 0.97371 | -0.50728 | 0.0027313 | 0.00068452
41 | 0.98426 | -0.3009 | 0.0016904 | 0.00042366
42 | 0.98283 | -0.32871 | 0.0017257 | 0.00043249
43 | 0.98546 | -0.27763 | 0 | 0
44 | 0.98182 | -0.34822 | 0 | 0
45 | 0.98637 | -0.26017 | 0.0023087 | 0.00057861
46 | 0.9818 | -0.34856 | 0.0015609 | 0.0003912
47 | 0.9888 | -0.21326 | 0.0045513 | 0.0011407
48 | 0.98885 | -0.21242 | 0.0019147 | 0.00047986
49 | 0.99106 | -0.16998 | 0.0055911 | 0.0014013
50 | 0.99139 | -0.16357 | 0.0022592 | 0.00056622
51 | 0.9937 | -0.11954 | 0.0019974 | 0.00050059
52 | 0.97316 | -0.51801 | 0.0010944 | 0.00027429
53 | 0.99135 | -0.16619 | 0.0019833 | 0.00049706
54 | 0.99126 | -0.16787 | 0.0024296 | 0.00060892
55 | 0.99124 | -0.16818 | 0.0025848 | 0.00064782
56 | 0.9734 | -0.5133 | 0 | 0
57 | 0.97333 | -0.5147 | 0.0015393 | 0.00038579
58 | 0.99678 | -0.061055 | 0.0024567 | 0.00061571
59 | 0.99483 | -0.097941 | 0.001901 | 0.00047645
60 | 0.9978 | -0.041692 | 0 | 0
61 | 0.99386 | -0.11647 | 0.0029864 | 0.00074847
62 | 0.99679 | -0.061001 | 0.0027922 | 0.0006998
63 | 1 | 0 | -0.15967 | -0.040443
64 | 0.97322 | -0.51694 | 0.0011512 | 0.00028853
65 | 0.98175 | -0.34971 | 0.0028657 | 0.00071822
66 | 0.99354 | -0.12365 | 0.0019162 | 0.00048024
67 | 0.9935 | -0.12441 | 0.0015079 | 0.0003779
68 | 0.99358 | -0.12295 | 0 | 0
69 | 0.99421 | -0.11071 | 0 | 0
70 | 0.99398 | -0.11528 | 0.0032804 | 0.00082214
71 | 0.9948 | -0.099425 | 0.0012629 | 0.00031651
72 | 0.99374 | -0.11981 | 0.0012305 | 0.0003084
73 | 0.99599 | -0.076472 | 0 | 0
74 | 0.99583 | -0.07956 | 0.003935 | 0.0009862
75 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0012127 | 0.0003036 | -0.0012126 | -0.00030391 | 3.4787e-08 | -3.1293e-07 | 0.0018542 | 0.0018543 | 0.0018543 | 0.97313 | -0.51872 | 0.9731 | -0.51932 | 0.50942
1 | -0.0021511 | -0.0005388 | 0.0021512 | 0.00053868 | 4.83e-08 | -1.17e-07 | 0.0032892 | 0.0032891 | 0.0032892 | 0.97313 | -0.51872 | 0.97315 | -0.51825 | 0.90362
2 | -0.0027381 | -0.00068577 | 0.0027382 | 0.00068563 | 1.1297e-07 | -1.4127e-07 | 0.0041865 | 0.0041864 | 0.0041865 | 0.97315 | -0.51825 | 0.9732 | -0.51738 | 1.1501
3 | -0.0037352 | -0.00093552 | 0.0037353 | 0.00093549 | 7.8578e-08 | -2.9541e-08 | 0.005711 | 0.0057109 | 0.005711 | 0.9732 | -0.51738 | 0.97322 | -0.51694 | 1.5689
4 | -0.0050711 | -0.0012708 | 0.005072 | 0.0012709 | 8.5986e-07 | 7.7615e-08 | 0.007759 | 0.0077589 | 0.007759 | 0.97252 | -0.5307 | 0.9727 | -0.52714 | 2.1316
5 | 0.0018159 | 0.00045495 | -0.0018158 | -0.00045509 | 3.8355e-08 | -1.3986e-07 | 0.0027783 | 0.0027784 | 0.0027784 | 0.97252 | -0.5307 | 0.9725 | -0.53115 | 0.7633
6 | -0.006567 | -0.0016455 | 0.0065678 | 0.0016457 | 8.4025e-07 | 2.6212e-07 | 0.010046 | 0.010046 | 0.010046 | 0.9727 | -0.52714 | 0.97284 | -0.52446 | 2.7599
7 | 0.001495 | 0.00037462 | -0.001495 | -0.00037468 | 1.1327e-08 | -6.443e-08 | 0.002287 | 0.002287 | 0.002287 | 0.9727 | -0.52714 | 0.97269 | -0.5273 | 0.62831
8 | -0.0078925 | -0.0019778 | 0.0078938 | 0.0019783 | 1.2518e-06 | 5.1668e-07 | 0.012072 | 0.012072 | 0.012072 | 0.97284 | -0.52446 | 0.97301 | -0.52113 | 3.3165
9 | -0.0091906 | -0.0023033 | 0.009192 | 0.0023039 | 1.3674e-06 | 6.4584e-07 | 0.014055 | 0.014055 | 0.014055 | 0.97301 | -0.52113 | 0.97316 | -0.51801 | 3.8613
10 | -0.00083878 | -0.00021022 | 0.00083879 | 0.00020999 | 1.0668e-08 | -2.2651e-07 | 0.0012564 | 0.0012563 | 0.0012564 | 0.99339 | -0.12656 | 0.99341 | -0.1263 | 0.34517
11 | -0.0017177 | -0.00043026 | 0.0017177 | 0.00043022 | 8.7421e-09 | -4.0002e-08 | 0.0025728 | 0.0025728 | 0.0025728 | 0.99341 | -0.1263 | 0.99341 | -0.12619 | 0.70682
12 | 0.00666 | 0.0016691 | -0.0066596 | -0.001669 | 3.7289e-07 | 1.1003e-07 | 0.0099902 | 0.0099903 | 0.0099903 | 0.99199 | -0.15376 | 0.99193 | -0.15494 | 2.7446
13 | -0.0090598 | -0.0022706 | 0.00906 | 0.0022707 | 2.2551e-07 | 1.0229e-07 | 0.01359 | 0.01359 | 0.01359 | 0.99199 | -0.15376 | 0.99201 | -0.15324 | 3.7335
14 | 0.0042402 | 0.0010626 | -0.0042401 | -0.0010627 | 9.4393e-08 | -1.9894e-08 | 0.0063608 | 0.0063608 | 0.0063608 | 0.99193 | -0.15494 | 0.9919 | -0.1554 | 1.7475
15 | -0.021524 | -0.0053955 | 0.021532 | 0.0054006 | 8.414e-06 | 5.1069e-06 | 0.032286 | 0.032286 | 0.032286 | 0.99201 | -0.15324 | 0.99244 | -0.14504 | 8.8697
16 | 0.0096783 | 0.0024268 | -0.0096725 | -0.002424 | 5.8195e-06 | 2.7745e-06 | 0.014518 | 0.014518 | 0.014518 | 0.99201 | -0.15324 | 0.99136 | -0.16586 | 3.9885
17 | -0.023712 | -0.005947 | 0.023713 | 0.0059474 | 6.0704e-07 | 3.7196e-07 | 0.035554 | 0.035554 | 0.035554 | 0.99244 | -0.14504 | 0.99246 | -0.1445 | 9.7677
18 | 0.0069983 | 0.0017538 | -0.0069982 | -0.0017538 | 1.0947e-07 | 3.5949e-08 | 0.010504 | 0.010504 | 0.010504 | 0.99136 | -0.16586 | 0.99135 | -0.16619 | 2.8858
19 | 0.032525 | 0.0081751 | -0.032521 | -0.0081726 | 4.0017e-06 | 2.5068e-06 | 0.049585 | 0.049585 | 0.049585 | 0.97623 | -0.45751 | 0.9761 | -0.46009 | 13.6222
20 | -0.036512 | -0.0091743 | 0.036555 | 0.0092011 | 4.2522e-05 | 2.6756e-05 | 0.055662 | 0.055662 | 0.055662 | 0.97623 | -0.45751 | 0.97748 | -0.43314 | 15.2917
21 | 0.029811 | 0.0074934 | -0.029799 | -0.0074857 | 1.2365e-05 | 7.7141e-06 | 0.045453 | 0.045454 | 0.045454 | 0.9761 | -0.46009 | 0.97566 | -0.46878 | 12.4872
22 | -0.044077 | -0.011086 | 0.044097 | 0.011099 | 2.0181e-05 | 1.2766e-05 | 0.067112 | 0.067112 | 0.067112 | 0.97748 | -0.43314 | 0.97796 | -0.42356 | 18.4374
23 | 0.02796 | 0.0070247 | -0.027957 | -0.0070234 | 2.1287e-06 | 1.3234e-06 | 0.042648 | 0.042648 | 0.042648 | 0.97566 | -0.46878 | 0.97558 | -0.47037 | 11.7166
24 | -0.054647 | -0.013743 | 0.054712 | 0.013784 | 6.413e-05 | 4.0733e-05 | 0.083165 | 0.083165 | 0.083165 | 0.97796 | -0.42356 | 0.97922 | -0.39902 | 22.8477
25 | 0.026754 | 0.0067218 | -0.026746 | -0.0067167 | 8.2138e-06 | 5.0927e-06 | 0.040813 | 0.040813 | 0.040813 | 0.97558 | -0.47037 | 0.97525 | -0.47681 | 11.2124
26 | -0.058648 | -0.01477 | 0.058683 | 0.014793 | 3.585e-05 | 2.2792e-05 | 0.089147 | 0.089146 | 0.089147 | 0.97922 | -0.39902 | 0.97987 | -0.38625 | 24.4908
27 | 0.024062 | 0.0060441 | -0.024039 | -0.0060301 | 2.2791e-05 | 1.4024e-05 | 0.036718 | 0.036719 | 0.036719 | 0.97525 | -0.47681 | 0.97424 | -0.49668 | 10.0875
28 | 0.022698 | 0.0056939 | -0.022696 | -0.0056929 | 1.5706e-06 | 9.6177e-07 | 0.03467 | 0.03467 | 0.03467 | 0.97424 | -0.49668 | 0.97417 | -0.49813 | 9.5246
29 | 0.0208 | 0.0052176 | -0.020798 | -0.0052167 | 1.3676e-06 | 8.3029e-07 | 0.031772 | 0.031772 | 0.031772 | 0.97417 | -0.49813 | 0.9741 | -0.49951 | 8.7287
30 | 0.019459 | 0.004881 | -0.019452 | -0.0048767 | 7.211e-06 | 4.3442e-06 | 0.029726 | 0.029727 | 0.029727 | 0.9741 | -0.49951 | 0.97371 | -0.50728 | 8.1666
31 | -0.0011486 | -0.00028786 | 0.0011486 | 0.00028766 | 1.799e-08 | -1.9837e-07 | 0.0017204 | 0.0017203 | 0.0017204 | 0.99344 | -0.12568 | 0.99346 | -0.12535 | 0.47263
32 | 0.0027272 | 0.00068304 | -0.0027271 | -0.00068319 | 1.0906e-07 | -1.5588e-07 | 0.0040846 | 0.0040847 | 0.0040847 | 0.99346 | -0.12535 | 0.99341 | -0.12619 | 1.1222
33 | -0.0038758 | -0.0009707 | 0.0038759 | 0.00097063 | 1.7507e-07 | -6.7352e-08 | 0.0058049 | 0.0058049 | 0.0058049 | 0.99346 | -0.12535 | 0.99351 | -0.1244 | 1.5948
34 | -0.0051145 | -0.001281 | 0.005115 | 0.0012811 | 4.9871e-07 | 2.5628e-08 | 0.0076599 | 0.0076598 | 0.0076599 | 0.99351 | -0.1244 | 0.99361 | -0.12235 | 2.1044
35 | -0.0065438 | -0.0016392 | 0.0065446 | 0.0016394 | 7.9416e-07 | 2.2259e-07 | 0.0097995 | 0.0097994 | 0.0097995 | 0.99361 | -0.12235 | 0.99374 | -0.11981 | 2.6922
36 | -0.02683 | -0.0067285 | 0.026843 | 0.0067369 | 1.3483e-05 | 8.3419e-06 | 0.040228 | 0.040227 | 0.040228 | 0.99246 | -0.1445 | 0.99301 | -0.13396 | 11.0515
37 | -0.028774 | -0.0072208 | 0.028789 | 0.0072302 | 1.5115e-05 | 9.3932e-06 | 0.043121 | 0.043121 | 0.043121 | 0.99301 | -0.13396 | 0.99358 | -0.12295 | 11.8464
38 | -0.0024253 | -0.00060784 | 0.0024253 | 0.00060782 | 7.7872e-09 | -1.4735e-08 | 0.0036626 | 0.0036626 | 0.0036626 | 0.98535 | -0.2799 | 0.98535 | -0.27983 | 1.0062
39 | -0.005957 | -0.001493 | 0.0059577 | 0.0014931 | 6.2354e-07 | 1.3732e-07 | 0.008996 | 0.0089959 | 0.008996 | 0.98535 | -0.27983 | 0.98546 | -0.27763 | 2.4714
40 | -0.063663 | -0.016041 | 0.063736 | 0.016088 | 7.2762e-05 | 4.6306e-05 | 0.096709 | 0.096709 | 0.096709 | 0.97987 | -0.38625 | 0.98109 | -0.36239 | 26.5684
41 | -0.065151 | -0.016442 | 0.065195 | 0.01647 | 4.4239e-05 | 2.8161e-05 | 0.098855 | 0.098855 | 0.098855 | 0.98109 | -0.36239 | 0.98182 | -0.34822 | 27.1579
42 | 0.01672 | 0.0041922 | -0.016716 | -0.0041894 | 4.794e-06 | 2.8247e-06 | 0.025553 | 0.025553 | 0.025553 | 0.97371 | -0.50728 | 0.9734 | -0.5133 | 7.02
43 | 0.071508 | 0.018114 | -0.071413 | -0.018054 | 9.5399e-05 | 6.078e-05 | 0.10818 | 0.10818 | 0.10818 | 0.98426 | -0.3009 | 0.98283 | -0.32871 | 29.7188
44 | -0.073199 | -0.018538 | 0.073281 | 0.01859 | 8.1883e-05 | 5.2179e-05 | 0.11073 | 0.11073 | 0.11073 | 0.98426 | -0.3009 | 0.98546 | -0.27763 | 30.4208
45 | 0.069687 | 0.017621 | -0.069622 | -0.01758 | 6.5126e-05 | 4.1484e-05 | 0.10556 | 0.10556 | 0.10556 | 0.98283 | -0.32871 | 0.98182 | -0.34822 | 29.001
46 | -0.079238 | -0.020083 | 0.079305 | 0.020126 | 6.6541e-05 | 4.2429e-05 | 0.11973 | 0.11973 | 0.11973 | 0.98546 | -0.27763 | 0.98637 | -0.26017 | 32.8922
47 | 0.0044269 | 0.0011092 | -0.0044268 | -0.0011092 | 7.2511e-08 | -7.9187e-09 | 0.0067091 | 0.0067092 | 0.0067092 | 0.98182 | -0.34822 | 0.9818 | -0.34856 | 1.8432
48 | -0.081613 | -0.020704 | 0.081798 | 0.020822 | 0.00018457 | 0.00011771 | 0.12321 | 0.12321 | 0.12321 | 0.98637 | -0.26017 | 0.9888 | -0.21326 | 33.849
49 | 0.0028659 | 0.00071804 | -0.0028657 | -0.00071822 | 1.5627e-07 | -1.793e-07 | 0.0043434 | 0.0043435 | 0.0043435 | 0.9818 | -0.34856 | 0.98175 | -0.34971 | 1.1933
50 | -0.086349 | -0.021963 | 0.086353 | 0.021965 | 3.4822e-06 | 2.2216e-06 | 0.13006 | 0.13006 | 0.13006 | 0.9888 | -0.21326 | 0.98885 | -0.21242 | 35.7306
51 | -0.088268 | -0.022445 | 0.088448 | 0.02256 | 0.00018089 | 0.00011542 | 0.13294 | 0.13294 | 0.13294 | 0.98885 | -0.21242 | 0.99106 | -0.16998 | 36.5221
52 | -0.094039 | -0.023961 | 0.094069 | 0.02398 | 2.9097e-05 | 1.8572e-05 | 0.14133 | 0.14133 | 0.14133 | 0.99106 | -0.16998 | 0.99139 | -0.16357 | 38.8283
53 | -0.096328 | -0.024546 | 0.096533 | 0.024677 | 0.00020515 | 0.00013096 | 0.14473 | 0.14473 | 0.14473 | 0.99139 | -0.16357 | 0.9937 | -0.11954 | 39.7598
54 | -0.09853 | -0.025178 | 0.098545 | 0.025187 | 1.4635e-05 | 9.3434e-06 | 0.14772 | 0.14772 | 0.14772 | 0.9937 | -0.11954 | 0.99386 | -0.11647 | 40.5815
55 | -0.010286 | -0.0025782 | 0.010289 | 0.0025794 | 2.3062e-06 | 1.167e-06 | 0.015729 | 0.015728 | 0.015729 | 0.97316 | -0.51801 | 0.9734 | -0.5133 | 4.321
56 | 0.0050149 | 0.0012567 | -0.0050145 | -0.0012567 | 4.005e-07 | 1.3319e-08 | 0.0075273 | 0.0075274 | 0.0075274 | 0.99135 | -0.16619 | 0.99126 | -0.16787 | 2.068
57 | 0.0025849 | 0.00064775 | -0.0025848 | -0.00064782 | 3.8182e-08 | -6.2739e-08 | 0.0038802 | 0.0038802 | 0.0038802 | 0.99126 | -0.16787 | 0.99124 | -0.16818 | 1.066
58 | 0.0064268 | 0.00161 | -0.0064264 | -0.0016098 | 4.2959e-07 | 1.2741e-07 | 0.0098243 | 0.0098243 | 0.0098243 | 0.9734 | -0.5133 | 0.97333 | -0.5147 | 2.699
59 | 0.0048871 | 0.001224 | -0.0048866 | -0.001224 | 5.204e-07 | 2.4084e-08 | 0.007471 | 0.0074711 | 0.0074711 | 0.97333 | -0.5147 | 0.97322 | -0.51694 | 2.0525
60 | 0.10371 | 0.026588 | -0.10352 | -0.02647 | 0.00018512 | 0.00011821 | 0.15503 | 0.15503 | 0.15503 | 0.99678 | -0.061055 | 0.99483 | -0.097941 | 42.591
61 | -0.10617 | -0.027204 | 0.10626 | 0.027268 | 9.9734e-05 | 6.3692e-05 | 0.1587 | 0.1587 | 0.1587 | 0.99678 | -0.061055 | 0.9978 | -0.041692 | 43.5985
62 | 0.10162 | 0.025994 | -0.10153 | -0.025936 | 9.1018e-05 | 5.8116e-05 | 0.15219 | 0.15219 | 0.15219 | 0.99483 | -0.097941 | 0.99386 | -0.11647 | 41.8099
63 | 0.051438 | 0.012972 | -0.05139 | -0.012942 | 4.7495e-05 | 3.0116e-05 | 0.076738 | 0.076738 | 0.076738 | 0.9978 | -0.041692 | 0.99679 | -0.061001 | 21.0818
64 | -0.1577 | -0.04024 | 0.15802 | 0.040443 | 0.0003183 | 0.00020291 | 0.23544 | 0.23544 | 0.23544 | 0.9978 | -0.041692 | 1 | 0 | 32.3401
65 | 0.048598 | 0.012242 | -0.048562 | -0.01222 | 3.5929e-05 | 2.2758e-05 | 0.07257 | 0.07257 | 0.07257 | 0.99679 | -0.061001 | 0.99599 | -0.076472 | 19.9367
66 | 0.0015079 | 0.00037757 | -0.0015079 | -0.0003779 | 5.3964e-08 | -3.3087e-07 | 0.0022582 | 0.0022584 | 0.0022584 | 0.99354 | -0.12365 | 0.9935 | -0.12441 | 0.62043
67 | -0.0034241 | -0.00085781 | 0.0034242 | 0.00085773 | 1.1426e-07 | -7.6931e-08 | 0.0051281 | 0.005128 | 0.0051281 | 0.99354 | -0.12365 | 0.99358 | -0.12295 | 1.4088
68 | -0.032213 | -0.0080879 | 0.032232 | 0.0080997 | 1.8826e-05 | 1.1769e-05 | 0.048249 | 0.048249 | 0.048249 | 0.99358 | -0.12295 | 0.99421 | -0.11071 | 13.2551
69 | 0.01106 | 0.0027718 | -0.011057 | -0.0027706 | 2.4058e-06 | 1.2362e-06 | 0.016553 | 0.016553 | 0.016553 | 0.99421 | -0.11071 | 0.99398 | -0.11528 | 4.5474
70 | -0.043292 | -0.010871 | 0.043315 | 0.010886 | 2.3325e-05 | 1.4736e-05 | 0.064801 | 0.064801 | 0.064801 | 0.99421 | -0.11071 | 0.9948 | -0.099425 | 17.8025
71 | 0.0077768 | 0.0019484 | -0.0077751 | -0.0019478 | 1.6766e-06 | 6.4557e-07 | 0.011642 | 0.011642 | 0.011642 | 0.99398 | -0.11528 | 0.99374 | -0.11981 | 3.1984
72 | -0.044578 | -0.011203 | 0.044627 | 0.011234 | 4.8904e-05 | 3.0917e-05 | 0.06669 | 0.06669 | 0.06669 | 0.9948 | -0.099425 | 0.99599 | -0.076472 | 18.3215
73 | 0.0039356 | 0.00098599 | -0.003935 | -0.0009862 | 5.7886e-07 | -2.1053e-07 | 0.0058796 | 0.0058799 | 0.0058799 | 0.99599 | -0.076472 | 0.99583 | -0.07956 | 1.6153

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.16258 | 0.041171

## res_load
| p_mw | q_mvar
0 | 0.00093845 | 0.0002352
1 | 0.0012126 | 0.00030391
2 | 0.0005869 | 0.00014709
3 | 0.00099708 | 0.00024989
4 | 0.0032552 | 0.00081584
5 | 0.0018158 | 0.00045509
6 | 0.0013247 | 0.000332
7 | 0.001495 | 0.00037468
8 | 0.0012968 | 0.00032502
9 | 0.00083878 | 0.00021022
10 | 0.00087889 | 0.00022027
11 | 0.0023998 | 0.00060145
12 | 0.0024195 | 0.00060638
13 | 0.0027854 | 0.00069808
14 | 0.0042401 | 0.0010627
15 | 0.00218 | 0.00054635
16 | 0.0026742 | 0.00067021
17 | 0.003987 | 0.00099924
18 | 0.00271 | 0.00067919
19 | 0.0075219 | 0.0018852
20 | 0.0018392 | 0.00046096
21 | 0.010551 | 0.0026442
22 | 0.0012034 | 0.00030159
23 | 0.003936 | 0.00098646
24 | 0.0026837 | 0.00067259
25 | 0.0013415 | 0.00033622
26 | 0.0018967 | 0.00047537
27 | 0.0013394 | 0.00033569
28 | 0.0011486 | 0.00028786
29 | 0.0010094 | 0.00025297
30 | 0.0012385 | 0.0003104
31 | 0.0014288 | 0.00035809
32 | 0.0031169 | 0.00078117
33 | 0.0019309 | 0.00048392
34 | 0.0024253 | 0.00060784
35 | 0.0035317 | 0.00088514
36 | 0.00498 | 0.0012481
37 | 0.0014148 | 0.00035457
38 | 0.0027313 | 0.00068452
39 | 0.0016904 | 0.00042366
40 | 0.0017257 | 0.00043249
41 | 0.0023087 | 0.00057861
42 | 0.0015609 | 0.0003912
43 | 0.0045513 | 0.0011407
44 | 0.0019147 | 0.00047986
45 | 0.0055911 | 0.0014013
46 | 0.0022592 | 0.00056622
47 | 0.0019974 | 0.00050059
48 | 0.0010944 | 0.00027429
49 | 0.0019833 | 0.00049706
50 | 0.0024296 | 0.00060892
51 | 0.0025848 | 0.00064782
52 | 0.0015393 | 0.00038579
53 | 0.0024567 | 0.00061571
54 | 0.001901 | 0.00047645
55 | 0.0029864 | 0.00074847
56 | 0.0027922 | 0.0006998
57 | 0.0029061 | 0.00072833
58 | 0.0011512 | 0.00028853
59 | 0.0028657 | 0.00071822
60 | 0.0019162 | 0.00048024
61 | 0.0015079 | 0.0003779
62 | 0.0032804 | 0.00082214
63 | 0.0012629 | 0.00031651
64 | 0.0012305 | 0.0003084
65 | 0.003935 | 0.0009862

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1