## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2472-2_1_3_node_5 | 0.4 | n |  | TRUE
1 | bus_LV_2472-2_1_3_node_6 | 0.4 | n |  | TRUE
2 | bus_LV_2472-2_1_3_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_2472-2_1_3_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_2472-2_1_3_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_2472-2_1_3_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_2472-2_1_3_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_2472-2_1_3_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_2472-2_1_3_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_2472-2_1_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_2472-2_1_3_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_2472-2_1_3_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_2472-2_1_3_node_96 | 0.4 | n |  | TRUE
13 | bus_LV_2472-2_1_3_node_171 | 0.4 | n |  | TRUE
14 | bus_LV_2472-2_1_3_node_116 | 0.4 | n |  | TRUE
15 | bus_LV_2472-2_1_3_node_74 | 0.4 | n |  | TRUE
16 | bus_LV_2472-2_1_3_node_197 | 0.4 | n |  | TRUE
17 | bus_LV_2472-2_1_3_node_115 | 0.4 | n |  | TRUE
18 | bus_LV_2472-2_1_3_node_44 | 0.4 | n |  | TRUE
19 | bus_LV_2472-2_1_3_node_45 | 0.4 | n |  | TRUE
20 | bus_LV_2472-2_1_3_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_2472-2_1_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_2472-2_1_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_2472-2_1_3_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_2472-2_1_3_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_2472-2_1_3_node_205 | 0.4 | n |  | TRUE
26 | bus_LV_2472-2_1_3_node_209 | 0.4 | n |  | TRUE
27 | bus_LV_2472-2_1_3_node_195 | 0.4 | n |  | TRUE
28 | bus_LV_2472-2_1_3_node_208 | 0.4 | n |  | TRUE
29 | bus_LV_2472-2_1_3_node_38 | 0.4 | n |  | TRUE
30 | bus_LV_2472-2_1_3_node_39 | 0.4 | n |  | TRUE
31 | bus_LV_2472-2_1_3_node_40 | 0.4 | n |  | TRUE
32 | bus_LV_2472-2_1_3_node_41 | 0.4 | n |  | TRUE
33 | bus_LV_2472-2_1_3_node_42 | 0.4 | n |  | TRUE
34 | bus_LV_2472-2_1_3_node_43 | 0.4 | n |  | TRUE
35 | bus_LV_2472-2_1_3_node_66 | 0.4 | n |  | TRUE
36 | bus_LV_2472-2_1_3_node_164 | 0.4 | n |  | TRUE
37 | bus_LV_2472-2_1_3_node_178 | 0.4 | n |  | TRUE
38 | bus_LV_2472-2_1_3_node_227 | 0.4 | n |  | TRUE
39 | bus_LV_2472-2_1_3_node_108 | 0.4 | n |  | TRUE
40 | bus_LV_2472-2_1_3_node_165 | 0.4 | n |  | TRUE
41 | bus_LV_2472-2_1_3_node_170 | 0.4 | n |  | TRUE
42 | bus_LV_2472-2_1_3_node_59 | 0.4 | n |  | TRUE
43 | bus_LV_2472-2_1_3_node_57 | 0.4 | n |  | TRUE
44 | bus_LV_2472-2_1_3_node_46 | 0.4 | n |  | TRUE
45 | bus_LV_2472-2_1_3_node_160 | 0.4 | n |  | TRUE
46 | bus_LV_2472-2_1_3_node_162 | 0.4 | n |  | TRUE
47 | bus_LV_2472-2_1_3_node_158 | 0.4 | n |  | TRUE
48 | bus_LV_2472-2_1_3_node_203 | 0.4 | n |  | TRUE
49 | bus_LV_2472-2_1_3_node_202 | 0.4 | n |  | TRUE
50 | bus_LV_2472-2_1_3_node_58 | 0.4 | n |  | TRUE
51 | bus_LV_2472-2_1_3_node_60 | 0.4 | n |  | TRUE
52 | bus_LV_2472-2_1_3_node_75 | 0.4 | n |  | TRUE
53 | bus_LV_2472-2_1_3_node_97 | 0.4 | n |  | TRUE
54 | bus_LV_2472-2_1_3_node_117 | 0.4 | n |  | TRUE
55 | bus_LV_2472-2_1_3_node_152 | 0.4 | n |  | TRUE
56 | bus_LV_2472-2_1_3_node_110 | 0.4 | n |  | TRUE
57 | bus_LV_2472-2_1_3_node_106 | 0.4 | n |  | TRUE
58 | bus_LV_2472-2_1_3_node_218 | 0.4 | n |  | TRUE
59 | bus_LV_2472-2_1_3_node_118 | 0.4 | n |  | TRUE
60 | bus_LV_2472-2_1_3_node_126 | 0.4 | n |  | TRUE
61 | bus_LV_2472-2_1_3_node_201 | 0.4 | n |  | TRUE
62 | bus_LV_2472-2_1_3_node_125 | 0.4 | n |  | TRUE
63 | bus_LV_2472-2_1_3_node_109 | 0.4 | n |  | TRUE
64 | bus_LV_2472-2_1_3_node_91 | 0.4 | n |  | TRUE
65 | bus_LV_2472-2_1_3_node_92 | 0.4 | n |  | TRUE
66 | bus_LV_2472-2_1_3_node_93 | 0.4 | n |  | TRUE
67 | bus_LV_2472-2_1_3_node_94 | 0.4 | n |  | TRUE
68 | bus_LV_2472-2_1_3_node_95 | 0.4 | n |  | TRUE
69 | bus_LV_2472-2_1_3_node_191 | 0.4 | n |  | TRUE
70 | bus_LV_2472-2_1_3_node_144 | 0.4 | n |  | TRUE
71 | bus_LV_2472-2_1_3_node_192 | 0.4 | n |  | TRUE
72 | bus_LV_2472-2_1_3_node_145 | 0.4 | n |  | TRUE
73 | bus_LV_2472-2_1_3_node_219 | 0.4 | n |  | TRUE
74 | bus_LV_2472-2_1_3_node_98 | 0.4 | n |  | TRUE
75 | bus_LV_2472-2_1_3_node_99 | 0.4 | n |  | TRUE
76 | bus_LV_2472-2_1_3_node_101 | 0.4 | n |  | TRUE
77 | bus_LV_2472-2_1_3_node_102 | 0.4 | n |  | TRUE
78 | bus_LV_2472-2_1_3_node_174 | 0.4 | n |  | TRUE
79 | bus_LV_2472-2_1_3_node_175 | 0.4 | n |  | TRUE
80 | bus_LV_2472-2_1_3_node_107 | 0.4 | n |  | TRUE
81 | bus_LV_2472-2_1_3_node_220 | 0.4 | n |  | TRUE
82 | bus_LV_2472-2_1_3_node_229 | 0.4 | n |  | TRUE
83 | bus_LV_2472-2_1_3_node_230 | 0.4 | n |  | TRUE
84 | bus_LV_2472-2_1_3_node_186 | 0.4 | n |  | TRUE
85 | bus_LV_2472-2_1_3_node_188 | 0.4 | n |  | TRUE
86 | bus_LV_2472-2_1_3_node_185 | 0.4 | n |  | TRUE
87 | bus_LV_2472-2_1_3_node_148 | 0.4 | n |  | TRUE
88 | bus_LV_2472-2_1_3_node_149 | 0.4 | n |  | TRUE
89 | bus_LV_2472-2_1_3_node_150 | 0.4 | n |  | TRUE
90 | bus_LV_2472-2_1_3_node_151 | 0.4 | n |  | TRUE
91 | bus_LV_2472-2_1_3_node_153 | 0.4 | n |  | TRUE
92 | bus_LV_2472-2_1_3_node_159 | 0.4 | n |  | TRUE
93 | bus_LV_2472-2_1_3_node_161 | 0.4 | n |  | TRUE
94 | bus_LV_2472-2_1_3_node_182 | 0.4 | n |  | TRUE
95 | bus_LV_2472-2_1_3_node_223 | 0.4 | n |  | TRUE
96 | bus_LV_2472-2_1_3_node_211 | 0.4 | n |  | TRUE
97 | bus_LV_2472-2_1_3_node_180 | 0.4 | n |  | TRUE
98 | bus_LV_2472-2_1_3_node_222 | 0.4 | n |  | TRUE
99 | bus_LV_2472-2_1_3_node_166 | 0.4 | n |  | TRUE
100 | bus_LV_2472-2_1_3_node_167 | 0.4 | n |  | TRUE
101 | bus_LV_2472-2_1_3_node_168 | 0.4 | n |  | TRUE
102 | bus_LV_2472-2_1_3_node_169 | 0.4 | n |  | TRUE
103 | bus_LV_2472-2_1_3_node_194 | 0.4 | n |  | TRUE
104 | bus_LV_2472-2_1_3_node_198 | 0.4 | n |  | TRUE
105 | bus_LV_2472-2_1_3_node_196 | 0.4 | n |  | TRUE
106 | bus_LV_2472-2_1_3_node_207 | 0.4 | n |  | TRUE
107 | bus_LV_2472-2_1_3_node_179 | 0.4 | n |  | TRUE
108 | bus_LV_2472-2_1_3_node_212 | 0.4 | n |  | TRUE
109 | bus_LV_2472-2_1_3_node_187 | 0.4 | n |  | TRUE
110 | bus_LV_2472-2_1_3_node_189 | 0.4 | n |  | TRUE
111 | bus_LV_2472-2_1_3_node_190 | 0.4 | n |  | TRUE
112 | bus_LV_2472-2_1_3_node_221 | 0.4 | n |  | TRUE
113 | bus_LV_2472-2_1_3_node_193 | 0.4 | n |  | TRUE
114 | bus_LV_2472-2_1_3_node_210 | 0.4 | n |  | TRUE
115 | bus_MV_285_0_node_8 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2472-2_1_3_load_5 | 0 | 0.0016333 | 0.00040935 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2472-2_1_3_load_6 | 1 | 0.0017223 | 0.00043164 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2472-2_1_3_load_7 | 2 | 0.00094839 | 0.00023769 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2472-2_1_3_load_8 | 3 | 0.0014774 | 0.00037027 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2472-2_1_3_load_9 | 4 | 0.0022218 | 0.00055683 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2472-2_1_3_load_15 | 5 | 0.00099137 | 0.00024846 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2472-2_1_3_load_16 | 6 | 0.0013367 | 0.000335 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2472-2_1_3_load_10 | 7 | 0.00021433 | 5.3716e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2472-2_1_3_load_11 | 8 | 0.00012949 | 3.2454e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2472-2_1_3_load_13 | 10 | 0.0082051 | 0.0020564 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2472-2_1_3_load_96 | 12 | 0.006278 | 0.0015734 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2472-2_1_3_load_171 | 13 | 0.00026596 | 6.6655e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2472-2_1_3_load_116 | 14 | 0.00033367 | 8.3625e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2472-2_1_3_load_115 | 17 | 0.015334 | 0.0038431 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2472-2_1_3_load_44 | 18 | 0.0022389 | 0.00056112 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2472-2_1_3_load_45 | 19 | 0.0008483 | 0.0002126 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2472-2_1_3_load_17 | 20 | 0.0019473 | 0.00048805 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2472-2_1_3_load_18 | 21 | 0.0010959 | 0.00027466 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2472-2_1_3_load_20 | 23 | 0.0010759 | 0.00026966 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2472-2_1_3_load_205 | 25 | 0.0010209 | 0.00025586 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2472-2_1_3_load_209 | 26 | 0.0012456 | 0.00031217 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2472-2_1_3_load_195 | 27 | 0.0016261 | 0.00040754 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2472-2_1_3_load_38 | 29 | 0.0013635 | 0.00034172 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2472-2_1_3_load_39 | 30 | 0.004434 | 0.0011113 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2472-2_1_3_load_41 | 32 | 0.0011773 | 0.00029505 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2472-2_1_3_load_42 | 33 | 0.0010741 | 0.00026919 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2472-2_1_3_load_164 | 36 | 0.0010041 | 0.00025166 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2472-2_1_3_load_227 | 38 | 0.00087841 | 0.00022015 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2472-2_1_3_load_165 | 40 | 0.00099001 | 0.00024812 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2472-2_1_3_load_170 | 41 | 0.0015388 | 0.00038566 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2472-2_1_3_load_59 | 42 | 0.0063099 | 0.0015814 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2472-2_1_3_load_57 | 43 | 0.0062966 | 0.0015781 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2472-2_1_3_load_46 | 44 | 0.0045137 | 0.0011312 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2472-2_1_3_load_158 | 47 | 0.0020541 | 0.00051481 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2472-2_1_3_load_203 | 48 | 0.0018971 | 0.00047546 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2472-2_1_3_load_58 | 50 | 0.012261 | 0.003073 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2472-2_1_3_load_75 | 52 | 0.011205 | 0.0028081 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2472-2_1_3_load_97 | 53 | 0.0062896 | 0.0015763 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2472-2_1_3_load_152 | 55 | 0.00059699 | 0.00014962 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2472-2_1_3_load_110 | 56 | 0.0023606 | 0.00059163 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2472-2_1_3_load_106 | 57 | 0.0012132 | 0.00030407 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2472-2_1_3_load_218 | 58 | 0.020487 | 0.0051345 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2472-2_1_3_load_201 | 61 | 0.003977 | 0.00099672 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2472-2_1_3_load_109 | 63 | 0.0084898 | 0.0021277 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2472-2_1_3_load_91 | 64 | 0.0010811 | 0.00027094 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2472-2_1_3_load_92 | 65 | 0.0020823 | 0.00052187 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2472-2_1_3_load_93 | 66 | 0.0029829 | 0.00074759 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2472-2_1_3_load_94 | 67 | 0.0031427 | 0.00078764 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2472-2_1_3_load_95 | 68 | 0.0029405 | 0.00073697 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2472-2_1_3_load_191 | 69 | 0.001864 | 0.00046717 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2472-2_1_3_load_144 | 70 | 0.00081768 | 0.00020493 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2472-2_1_3_load_145 | 72 | 0.001096 | 0.0002747 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2472-2_1_3_load_219 | 73 | 0.00096751 | 0.00024248 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2472-2_1_3_load_98 | 74 | 0.0019097 | 0.00047862 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2472-2_1_3_load_101 | 76 | 0.0013228 | 0.00033153 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2472-2_1_3_load_102 | 77 | 0.0043912 | 0.0011005 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2472-2_1_3_load_174 | 78 | 0.001763 | 0.00044184 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2472-2_1_3_load_175 | 79 | 0.0010937 | 0.00027411 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2472-2_1_3_load_107 | 80 | 0.00068484 | 0.00017164 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2472-2_1_3_load_220 | 81 | 0.0035639 | 0.00089319 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2472-2_1_3_load_229 | 82 | 0.01664 | 0.0041705 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2472-2_1_3_load_230 | 83 | 0.014631 | 0.0036669 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2472-2_1_3_load_185 | 86 | 0.0011391 | 0.00028548 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2472-2_1_3_load_148 | 87 | 0.00049789 | 0.00012478 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2472-2_1_3_load_149 | 88 | 0.00094496 | 0.00023683 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2472-2_1_3_load_151 | 90 | 0.00095552 | 0.00023948 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2472-2_1_3_load_153 | 91 | 0.00077474 | 0.00019417 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2472-2_1_3_load_159 | 92 | 0.0027414 | 0.00068706 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2472-2_1_3_load_161 | 93 | 0.0014063 | 0.00035245 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2472-2_1_3_load_223 | 95 | 0.00064156 | 0.00016079 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2472-2_1_3_load_211 | 96 | 0.000886 | 0.00022205 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2472-2_1_3_load_180 | 97 | 0.0010638 | 0.0002666 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2472-2_1_3_load_166 | 99 | 0.0016751 | 0.00041982 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2472-2_1_3_load_167 | 100 | 0.0013371 | 0.0003351 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2472-2_1_3_load_169 | 102 | 0.0020181 | 0.00050579 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2472-2_1_3_load_194 | 103 | 0.0020934 | 0.00052466 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2472-2_1_3_load_198 | 104 | 0.0003283 | 8.2279e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2472-2_1_3_load_196 | 105 | 0.0092703 | 0.0023234 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2472-2_1_3_load_207 | 106 | 0.0010869 | 0.0002724 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2472-2_1_3_load_179 | 107 | 0.0017843 | 0.00044718 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2472-2_1_3_load_212 | 108 | 0.004014 | 0.001006 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2472-2_1_3_load_189 | 110 | 0.0016213 | 0.00040633 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2472-2_1_3_load_190 | 111 | 0.0010811 | 0.00027095 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2472-2_1_3_load_221 | 112 | 0.0017956 | 0.00045002 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2472-2_1_3_load_193 | 113 | 0.0033238 | 0.00083302 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2472-2_1_3_load_210 | 114 | 0.00082692 | 0.00020725 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2472-2_1_3_line_0 |  | 0 | 1 | 0.011626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2472-2_1_3_line_1 |  | 0 | 2 | 0.0027752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2472-2_1_3_line_2 |  | 1 | 3 | 0.0042305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2472-2_1_3_line_3 |  | 2 | 4 | 0.028306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2472-2_1_3_line_4 |  | 3 | 5 | 0.011587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2472-2_1_3_line_5 |  | 5 | 6 | 0.0035661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2472-2_1_3_line_6 |  | 6 | 18 | 0.0094009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2472-2_1_3_line_7 |  | 7 | 8 | 0.018801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2472-2_1_3_line_8 |  | 7 | 9 | 0.046121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2472-2_1_3_line_9 |  | 8 | 10 | 0.0079708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2472-2_1_3_line_10 |  | 9 | 11 | 0.004124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2472-2_1_3_line_11 |  | 10 | 12 | 0.022926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2472-2_1_3_line_12 |  | 11 | 13 | 0.014127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2472-2_1_3_line_13 |  | 11 | 14 | 0.026413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2472-2_1_3_line_14 |  | 12 | 15 | 0.017175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2472-2_1_3_line_15 |  | 13 | 16 | 0.026497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2472-2_1_3_line_16 |  | 14 | 17 | 0.036264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2472-2_1_3_line_17 |  | 15 | 53 | 0.01133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2472-2_1_3_line_18 |  | 15 | 51 | 0.007228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2472-2_1_3_line_19 |  | 16 | 104 | 0.0046513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2472-2_1_3_line_20 |  | 16 | 105 | 0.02265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2472-2_1_3_line_21 |  | 18 | 19 | 0.00295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2472-2_1_3_line_22 |  | 19 | 44 | 0.0022937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2472-2_1_3_line_23 |  | 20 | 21 | 0.0073931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2472-2_1_3_line_24 |  | 20 | 22 | 0.013058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2472-2_1_3_line_25 |  | 21 | 23 | 0.03564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2472-2_1_3_line_26 |  | 22 | 24 | 0.038977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2472-2_1_3_line_27 |  | 23 | 25 | 0.025882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2472-2_1_3_line_28 |  | 24 | 26 | 0.040253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2472-2_1_3_line_29 |  | 25 | 27 | 0.025704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2472-2_1_3_line_30 |  | 26 | 28 | 0.014202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2472-2_1_3_line_31 |  | 27 | 37 | 0.011811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2472-2_1_3_line_32 |  | 28 | 114 | 0.038132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2472-2_1_3_line_33 |  | 28 | 106 | 0.019112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2472-2_1_3_line_34 |  | 29 | 30 | 0.0034735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2472-2_1_3_line_35 |  | 29 | 31 | 0.027324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2472-2_1_3_line_36 |  | 30 | 32 | 0.024583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2472-2_1_3_line_37 |  | 31 | 33 | 0.01015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2472-2_1_3_line_38 |  | 31 | 34 | 0.026415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2472-2_1_3_line_39 |  | 32 | 35 | 0.013067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2472-2_1_3_line_40 |  | 33 | 36 | 0.0096084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2472-2_1_3_line_41 |  | 34 | 37 | 0.003904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2472-2_1_3_line_42 |  | 35 | 38 | 0.0099557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2472-2_1_3_line_43 |  | 35 | 39 | 0.009829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2472-2_1_3_line_44 |  | 36 | 40 | 0.015578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2472-2_1_3_line_45 |  | 37 | 41 | 0.016649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2472-2_1_3_line_46 |  | 38 | 55 | 0.016322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2472-2_1_3_line_47 |  | 39 | 56 | 0.024485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2472-2_1_3_line_48 |  | 39 | 57 | 0.013459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2472-2_1_3_line_49 |  | 41 | 101 | 0.013299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2472-2_1_3_line_50 |  | 42 | 43 | 0.0068085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2472-2_1_3_line_51 |  | 43 | 50 | 0.018757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2472-2_1_3_line_52 |  | 44 | 45 | 0.022811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2472-2_1_3_line_53 |  | 45 | 46 | 0.029599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2472-2_1_3_line_54 |  | 45 | 47 | 0.0039247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2472-2_1_3_line_55 |  | 46 | 95 | 0.075564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2472-2_1_3_line_56 |  | 47 | 92 | 0.0005977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2472-2_1_3_line_57 |  | 48 | 49 | 0.015215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2472-2_1_3_line_58 |  | 49 | 61 | 0.0060433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2472-2_1_3_line_59 |  | 50 | 51 | 0.018414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2472-2_1_3_line_60 |  | 51 | 52 | 0.019449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2472-2_1_3_line_61 |  | 52 | 54 | 0.032062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2472-2_1_3_line_62 |  | 53 | 58 | 0.0015841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2472-2_1_3_line_63 |  | 54 | 59 | 0.00895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2472-2_1_3_line_64 |  | 55 | 89 | 0.013332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2472-2_1_3_line_65 |  | 56 | 81 | 0.0053162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2472-2_1_3_line_66 |  | 57 | 80 | 0.016137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2472-2_1_3_line_67 |  | 58 | 73 | 0.018997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2472-2_1_3_line_68 |  | 59 | 82 | 0.006313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2472-2_1_3_line_69 |  | 60 | 61 | 0.025594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2472-2_1_3_line_70 |  | 60 | 62 | 0.051708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2472-2_1_3_line_71 |  | 62 | 63 | 0.0017851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2472-2_1_3_line_72 |  | 63 | 80 | 0.032634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2472-2_1_3_line_73 |  | 64 | 65 | 0.018905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2472-2_1_3_line_74 |  | 64 | 66 | 0.0071183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2472-2_1_3_line_75 |  | 65 | 67 | 0.024506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2472-2_1_3_line_76 |  | 66 | 68 | 0.0059427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2472-2_1_3_line_77 |  | 67 | 69 | 0.011927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2472-2_1_3_line_78 |  | 68 | 70 | 0.016602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2472-2_1_3_line_79 |  | 69 | 71 | 0.038588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2472-2_1_3_line_80 |  | 70 | 72 | 0.0075403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2472-2_1_3_line_81 |  | 71 | 113 | 0.02147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2472-2_1_3_line_82 |  | 72 | 84 | 0.026681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2472-2_1_3_line_83 |  | 73 | 91 | 0.0019111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2472-2_1_3_line_84 |  | 74 | 75 | 0.058742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2472-2_1_3_line_85 |  | 75 | 76 | 0.054499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2472-2_1_3_line_86 |  | 75 | 77 | 0.040009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2472-2_1_3_line_87 |  | 76 | 78 | 0.019539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2472-2_1_3_line_88 |  | 78 | 79 | 0.018424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2472-2_1_3_line_89 |  | 79 | 106 | 0.012524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2472-2_1_3_line_90 |  | 82 | 83 | 0.037772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2472-2_1_3_line_91 |  | 84 | 85 | 0.043591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2472-2_1_3_line_92 |  | 84 | 86 | 0.015153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2472-2_1_3_line_93 |  | 85 | 112 | 0.020229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2472-2_1_3_line_94 |  | 86 | 109 | 0.037464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2472-2_1_3_line_95 |  | 87 | 88 | 0.00808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2472-2_1_3_line_96 |  | 87 | 89 | 0.03181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2472-2_1_3_line_97 |  | 88 | 90 | 0.0026785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2472-2_1_3_line_98 |  | 89 | 91 | 0.013272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2472-2_1_3_line_99 |  | 92 | 93 | 0.014618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2472-2_1_3_line_100 |  | 93 | 94 | 0.011726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2472-2_1_3_line_101 |  | 94 | 96 | 0.014375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2472-2_1_3_line_102 |  | 94 | 97 | 0.007752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2472-2_1_3_line_103 |  | 95 | 98 | 0.038167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2472-2_1_3_line_104 |  | 96 | 108 | 0.0165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2472-2_1_3_line_105 |  | 97 | 107 | 0.0085719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2472-2_1_3_line_106 |  | 98 | 112 | 0.022427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2472-2_1_3_line_107 |  | 99 | 100 | 0.015478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2472-2_1_3_line_108 |  | 99 | 101 | 0.016325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2472-2_1_3_line_109 |  | 101 | 102 | 0.014812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2472-2_1_3_line_110 |  | 102 | 103 | 0.0049902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2472-2_1_3_line_111 |  | 104 | 111 | 0.021453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2472-2_1_3_line_112 |  | 109 | 110 | 0.01039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2472-2_1_3_line_113 |  | 109 | 111 | 0.017537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2472-2_1_3_trafo_96 | 0.63 MVA 20/0.4 kV | 115 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2617214.6171 | 1255330.3075 | 2617218.8026 | 1255330.0986 | 2617223.803 | 1255330.102 | 2617226.2026 | 1255330.5132
1 | 2617214.6171 | 1255330.3075 | 2617211.8453 | 1255330.4457
2 | 2617226.2026 | 1255330.5132 | 2617227.3008 | 1255330.7014 | 2617230.1684 | 1255331.9214
3 | 2617211.8453 | 1255330.4457 | 2617210.7993 | 1255330.4979 | 2617202.2359 | 1255331.585 | 2617193.5574 | 1255333.3499 | 2617183.811 | 1255334.0333
4 | 2617239.6032 | 1255338.5082 | 2617238.3987 | 1255337.3047 | 2617235.1031 | 1255334.6044 | 2617231.3007 | 1255332.4031 | 2617230.1684 | 1255331.9214
5 | 2617242.0975 | 1255341.054 | 2617241.9031 | 1255340.8061 | 2617239.6032 | 1255338.5082
6 | 2617242.0975 | 1255341.054 | 2617244.8036 | 1255344.5058 | 2617246.8977 | 1255348.0031 | 2617247.3084 | 1255348.8468
7 | 2617283.5074 | 1255495.8301 | 2617284.6773 | 1255477.0655
8 | 2617260.5465 | 1255444.7961 | 2617277.0593 | 1255451.3818 | 2617283.0076 | 1255457.3475 | 2617284.2113 | 1255460.9867 | 2617284.6773 | 1255477.0655 | 2617284.6773 | 1255477.0655
9 | 2617283.5074 | 1255495.8301 | 2617283.0114 | 1255503.7854
10 | 2617260.5465 | 1255444.7961 | 2617256.5372 | 1255443.7837
11 | 2617281.5848 | 1255526.6674 | 2617283.0114 | 1255503.7854
12 | 2617256.5372 | 1255443.7837 | 2617242.7977 | 1255440.4972
13 | 2617256.5372 | 1255443.7837 | 2617256.0993 | 1255459.4929 | 2617254.3494 | 1255470.0465
14 | 2617280.516 | 1255543.8089 | 2617281.5848 | 1255526.6674
15 | 2617216.3687 | 1255438.5971 | 2617242.7977 | 1255440.4972
16 | 2617245.333 | 1255504.9423 | 2617245.8048 | 1255503.5813 | 2617247.1307 | 1255498.8931 | 2617249.877 | 1255493.3085 | 2617251.102 | 1255489.6318 | 2617254.3494 | 1255470.0465
17 | 2617280.516 | 1255543.8089 | 2617287.6257 | 1255544.5857 | 2617291.787 | 1255544.9634
18 | 2617279.8013 | 1255551.0005 | 2617280.516 | 1255543.8089
19 | 2617216.3687 | 1255438.5971 | 2617211.7198 | 1255438.7435
20 | 2617216.3687 | 1255438.5971 | 2617214.3535 | 1255449.543 | 2617212.8299 | 1255452.1626 | 2617210.1402 | 1255453.8114 | 2617204.8809 | 1255454.7079
21 | 2617247.3084 | 1255348.8468 | 2617248.5996 | 1255351.4993
22 | 2617249.285 | 1255353.6882 | 2617248.5996 | 1255351.4993 | 2617248.5996 | 1255351.4993
23 | 2617347.6375 | 1255738.0052 | 2617346.4 | 1255732.7268 | 2617346.251 | 1255730.7609
24 | 2617352.8733 | 1255749.8904 | 2617348.359 | 1255741.0825 | 2617347.6375 | 1255738.0052
25 | 2617346.251 | 1255730.7609 | 2617345.8481 | 1255725.4425 | 2617348.7389 | 1255695.2741
26 | 2617352.8733 | 1255749.8904 | 2617363.8236 | 1255767.9456 | 2617370.7513 | 1255784.4324
27 | 2617351.2077 | 1255669.5098 | 2617348.7389 | 1255695.2741
28 | 2617370.7513 | 1255784.4324 | 2617382.6354 | 1255745.9732
29 | 2617335.5122 | 1255649.1544 | 2617351.2077 | 1255669.5098 | 2617351.2077 | 1255669.5098
30 | 2617386.8162 | 1255732.4002 | 2617385.7654 | 1255735.8439 | 2617382.6354 | 1255745.9732
31 | 2617328.2999 | 1255639.8009 | 2617335.5122 | 1255649.1544
32 | 2617386.8162 | 1255732.4002 | 2617393.2481 | 1255735.3655 | 2617395.8617 | 1255741.6329 | 2617399.8549 | 1255758.3779 | 2617401.6724 | 1255765.1834
33 | 2617386.8162 | 1255732.4002 | 2617383.7102 | 1255713.5426
34 | 2617351.4149 | 1255585.3163 | 2617349.9861 | 1255588.4824
35 | 2617342.9436 | 1255614.7492 | 2617346.9981 | 1255595.1035 | 2617349.9861 | 1255588.4824
36 | 2617361.5266 | 1255562.9094 | 2617351.4149 | 1255585.3163
37 | 2617342.9436 | 1255614.7492 | 2617351.652 | 1255619.9629
38 | 2617328.4018 | 1255635.8986 | 2617341.4901 | 1255621.8163 | 2617342.9436 | 1255614.7492
39 | 2617366.9016 | 1255550.9989 | 2617361.5266 | 1255562.9094
40 | 2617359.8958 | 1255624.8985 | 2617351.652 | 1255619.9629
41 | 2617328.4018 | 1255635.8986 | 2617328.2999 | 1255639.8009
42 | 2617366.9016 | 1255550.9989 | 2617357.0063 | 1255549.9037
43 | 2617366.9016 | 1255550.9989 | 2617374.2815 | 1255544.4828
44 | 2617373.7317 | 1255631.8616 | 2617368.9773 | 1255630.3356 | 2617359.8958 | 1255624.8985
45 | 2617328.2999 | 1255639.8009 | 2617326.9029 | 1255640.3972 | 2617325.6031 | 1255641.3052 | 2617314.8578 | 1255649.5506
46 | 2617340.754 | 1255548.413 | 2617352.4562 | 1255549.4001 | 2617357.0063 | 1255549.9037
47 | 2617374.2815 | 1255544.4828 | 2617383.2625 | 1255550.0684 | 2617395.8855 | 1255555.9092
48 | 2617374.2815 | 1255544.4828 | 2617373.5655 | 1255531.0429
49 | 2617304.0027 | 1255657.1972 | 2617306.503 | 1255655.8036 | 2617310.1004 | 1255653.2012 | 2617314.8578 | 1255649.5506
50 | 2617290.003 | 1255586.2074 | 2617293.0482 | 1255592.2969
51 | 2617290.003 | 1255586.2074 | 2617282.3978 | 1255570.9992 | 2617282.1721 | 1255569.2609
52 | 2617255.4983 | 1255375.6243 | 2617253.2028 | 1255366.2002 | 2617249.285 | 1255353.6882
53 | 2617255.4983 | 1255375.6243 | 2617248.0167 | 1255375.6025 | 2617241.7766 | 1255376.5962 | 2617235.3461 | 1255378.1897 | 2617226.7009 | 1255381.5002
54 | 2617255.4983 | 1255375.6243 | 2617259.4093 | 1255375.9533
55 | 2617226.7009 | 1255381.5002 | 2617222.5032 | 1255377.7966 | 2617220.6032 | 1255377.6021 | 2617217.5025 | 1255377.9044 | 2617211.6998 | 1255378.8994 | 2617202.9009 | 1255380.5973 | 2617195.8978 | 1255382.0002 | 2617168.1032 | 1255385.3998 | 2617160.2035 | 1255386.5 | 2617153.2595 | 1255387.1315
56 | 2617260.0049 | 1255376.0034 | 2617259.4093 | 1255375.9533
57 | 2617325.4019 | 1255425.9501 | 2617327.9414 | 1255416.3511 | 2617329.2936 | 1255411.241
58 | 2617325.4019 | 1255425.9501 | 2617331.25 | 1255427.4735
59 | 2617279.8013 | 1255551.0005 | 2617282.1721 | 1255569.2609
60 | 2617279.8013 | 1255551.0005 | 2617260.6915 | 1255547.3856
61 | 2617234.2423 | 1255555.8047 | 2617236.6834 | 1255551.4534 | 2617238.9042 | 1255547.6684 | 2617241.3984 | 1255545.7966 | 2617245.6392 | 1255545.0084 | 2617250.9094 | 1255545.5351 | 2617260.6915 | 1255547.3856
62 | 2617291.787 | 1255544.9634 | 2617293.3646 | 1255545.1067
63 | 2617229.8681 | 1255563.6195 | 2617234.2423 | 1255555.8047
64 | 2617327.4688 | 1255547.2924 | 2617340.754 | 1255548.413
65 | 2617401.0594 | 1255557.131 | 2617395.8855 | 1255555.9092
66 | 2617373.3296 | 1255514.91 | 2617373.4379 | 1255528.6476 | 2617373.5655 | 1255531.0429
67 | 2617293.3646 | 1255545.1067 | 2617304.4546 | 1255546.1135 | 2617312.3061 | 1255546.5157
68 | 2617229.8681 | 1255563.6195 | 2617228.46 | 1255568.0517 | 2617228.3219 | 1255569.7084
69 | 2617343.1247 | 1255444.314 | 2617344.4542 | 1255438.4251 | 2617344.0135 | 1255434.3877 | 2617342.8072 | 1255431.6602 | 2617340.9416 | 1255429.9981 | 2617331.25 | 1255427.4735
70 | 2617343.1247 | 1255444.314 | 2617345.8503 | 1255445.8897 | 2617373.9867 | 1255467.3639 | 2617373.4036 | 1255473.3329 | 2617373.0584 | 1255480.4922
71 | 2617373.0584 | 1255480.4922 | 2617373.0725 | 1255482.2772
72 | 2617373.3296 | 1255514.91 | 2617373.0725 | 1255482.2772
73 | 2617124.4666 | 1255543.3495 | 2617127.2733 | 1255524.6539
74 | 2617128.3301 | 1255517.6145 | 2617127.2733 | 1255524.6539
75 | 2617124.4666 | 1255543.3495 | 2617124.3621 | 1255544.0459 | 2617123.9662 | 1255550.5491 | 2617123.9653 | 1255558.7101 | 2617124.2549 | 1255567.8308
76 | 2617128.3301 | 1255517.6145 | 2617129.2123 | 1255511.7377
77 | 2617124.2549 | 1255567.8308 | 2617124.6334 | 1255579.7514
78 | 2617131.5716 | 1255495.3081 | 2617131.498 | 1255496.5126 | 2617129.2123 | 1255511.7377
79 | 2617125.807 | 1255618.3217 | 2617125.4034 | 1255603.9999 | 2617124.6334 | 1255579.7514
80 | 2617132.0318 | 1255487.7819 | 2617131.5716 | 1255495.3081
81 | 2617125.807 | 1255618.3217 | 2617142.6389 | 1255610.9098 | 2617145.3473 | 1255609.447
82 | 2617124.4003 | 1255462.803 | 2617126.8793 | 1255466.2124 | 2617129.5634 | 1255471.7016 | 2617130.6689 | 1255475.4073 | 2617131.6557 | 1255481.0694 | 2617132.1471 | 1255485.8963 | 2617132.0318 | 1255487.7819
83 | 2617314.2146 | 1255546.6134 | 2617312.3061 | 1255546.5157
84 | 2617399.5086 | 1255611.5013 | 2617401.5965 | 1255614.4649 | 2617402.4647 | 1255626.998 | 2617402.7938 | 1255635.6714 | 2617403.3421 | 1255638.9975 | 2617404.9652 | 1255641.0036 | 2617407.5786 | 1255642.2454 | 2617412.5436 | 1255641.3482 | 2617425.757 | 1255636.0946 | 2617431.4757 | 1255635.3762
85 | 2617399.5086 | 1255611.5013 | 2617395.9093 | 1255622.4425 | 2617390.5643 | 1255650.0563 | 2617385.862 | 1255664.1465
86 | 2617399.5086 | 1255611.5013 | 2617415.0986 | 1255580.2039 | 2617418.5711 | 1255576.546
87 | 2617380.6862 | 1255682.8474 | 2617380.7037 | 1255679.6027 | 2617385.862 | 1255664.1465
88 | 2617380.6862 | 1255682.8474 | 2617380.6216 | 1255694.7904 | 2617381.6748 | 1255701.1848
89 | 2617381.6748 | 1255701.1848 | 2617383.7102 | 1255713.5426
90 | 2617228.3219 | 1255569.7084 | 2617228.1552 | 1255571.7088 | 2617228.3708 | 1255575.3785 | 2617230.7277 | 1255581.8674 | 2617245.1446 | 1255602.5183
91 | 2617119.4882 | 1255429.5779 | 2617111.7987 | 1255431.0567 | 2617112.8427 | 1255435.1847 | 2617114.4158 | 1255441.4934 | 2617115.9731 | 1255453.3169 | 2617116.758 | 1255455.7652 | 2617118.1995 | 1255458.0042 | 2617124.4003 | 1255462.803
92 | 2617124.4003 | 1255462.803 | 2617132.373 | 1255459.8685 | 2617138.3081 | 1255456.8523
93 | 2617119.4882 | 1255429.5779 | 2617119.801 | 1255423.0967 | 2617119.8043 | 1255411.5001 | 2617119.7238 | 1255409.3576
94 | 2617173.0864 | 1255443.4862 | 2617163.7963 | 1255445.5719 | 2617157.5536 | 1255447.4551 | 2617150.7344 | 1255450.5375 | 2617138.3081 | 1255456.8523
95 | 2617330.8216 | 1255507.5436 | 2617330.1425 | 1255515.595
96 | 2617327.4688 | 1255547.2924 | 2617330.1425 | 1255515.595
97 | 2617331.0467 | 1255504.8746 | 2617330.8216 | 1255507.5436
98 | 2617327.4688 | 1255547.2924 | 2617314.2146 | 1255546.6134
99 | 2617274.2325 | 1255379.1214 | 2617264.26 | 1255376.3613 | 2617260.0049 | 1255376.0034
100 | 2617285.5341 | 1255382.2493 | 2617274.2325 | 1255379.1214
101 | 2617285.5341 | 1255382.2493 | 2617289.5672 | 1255368.4518
102 | 2617285.5341 | 1255382.2493 | 2617293.0059 | 1255384.3143
103 | 2617115.0994 | 1255387.5039 | 2617146.301 | 1255387.4049 | 2617152.5011 | 1255387.2004 | 2617153.2595 | 1255387.1315
104 | 2617290.4698 | 1255352.644 | 2617292.3826 | 1255358.8203 | 2617289.5672 | 1255368.4518
105 | 2617293.0059 | 1255384.3143 | 2617301.2681 | 1255386.5976
106 | 2617115.0994 | 1255387.5039 | 2617117.6006 | 1255396.3058 | 2617119.0998 | 1255402.1029 | 2617119.6012 | 1255406.0959 | 2617119.7238 | 1255409.3576
107 | 2617288.1985 | 1255630.1999 | 2617294.8083 | 1255644.1951
108 | 2617304.0027 | 1255657.1972 | 2617302.3995 | 1255656.103 | 2617300.9019 | 1255654.9979 | 2617299.3976 | 1255653.6037 | 2617298.3998 | 1255651.7996 | 2617294.8083 | 1255644.1951
109 | 2617304.0027 | 1255657.1972 | 2617311.5386 | 1255669.9485
110 | 2617311.5386 | 1255669.9485 | 2617314.0775 | 1255674.2446
111 | 2617190.3994 | 1255440.6891 | 2617200.1973 | 1255439.1062 | 2617211.7198 | 1255438.7435
112 | 2617173.0864 | 1255443.4862 | 2617178.6507 | 1255449.2839 | 2617180.6911 | 1255450.4573
113 | 2617173.0864 | 1255443.4862 | 2617190.3994 | 1255440.6891

## bus_geodata
| x | y | coords
0 | 2617214.6171 | 1255330.3075
1 | 2617226.2026 | 1255330.5132
2 | 2617211.8453 | 1255330.4457
3 | 2617230.1684 | 1255331.9214
4 | 2617183.811 | 1255334.0333
5 | 2617239.6032 | 1255338.5082
6 | 2617242.0975 | 1255341.054
7 | 2617284.6773 | 1255477.0655
8 | 2617283.5074 | 1255495.8301
9 | 2617260.5465 | 1255444.7961
10 | 2617283.0114 | 1255503.7854
11 | 2617256.5372 | 1255443.7837
12 | 2617281.5848 | 1255526.6674
13 | 2617242.7977 | 1255440.4972
14 | 2617254.3494 | 1255470.0465
15 | 2617280.516 | 1255543.8089
16 | 2617216.3687 | 1255438.5971
17 | 2617245.333 | 1255504.9423
18 | 2617247.3084 | 1255348.8468
19 | 2617248.5996 | 1255351.4993
20 | 2617347.6375 | 1255738.0052
21 | 2617346.251 | 1255730.7609
22 | 2617352.8733 | 1255749.8904
23 | 2617348.7389 | 1255695.2741
24 | 2617370.7513 | 1255784.4324
25 | 2617351.2077 | 1255669.5098
26 | 2617382.6354 | 1255745.9732
27 | 2617335.5122 | 1255649.1544
28 | 2617386.8162 | 1255732.4002
29 | 2617349.9861 | 1255588.4824
30 | 2617351.4149 | 1255585.3163
31 | 2617342.9436 | 1255614.7492
32 | 2617361.5266 | 1255562.9094
33 | 2617351.652 | 1255619.9629
34 | 2617328.4018 | 1255635.8986
35 | 2617366.9016 | 1255550.9989
36 | 2617359.8958 | 1255624.8985
37 | 2617328.2999 | 1255639.8009
38 | 2617357.0063 | 1255549.9037
39 | 2617374.2815 | 1255544.4828
40 | 2617373.7317 | 1255631.8616
41 | 2617314.8578 | 1255649.5506
42 | 2617293.0482 | 1255592.2969
43 | 2617290.003 | 1255586.2074
44 | 2617249.285 | 1255353.6882
45 | 2617255.4983 | 1255375.6243
46 | 2617226.7009 | 1255381.5002
47 | 2617259.4093 | 1255375.9533
48 | 2617329.2936 | 1255411.241
49 | 2617325.4019 | 1255425.9501
50 | 2617282.1721 | 1255569.2609
51 | 2617279.8013 | 1255551.0005
52 | 2617260.6915 | 1255547.3856
53 | 2617291.787 | 1255544.9634
54 | 2617234.2423 | 1255555.8047
55 | 2617340.754 | 1255548.413
56 | 2617395.8855 | 1255555.9092
57 | 2617373.5655 | 1255531.0429
58 | 2617293.3646 | 1255545.1067
59 | 2617229.8681 | 1255563.6195
60 | 2617343.1247 | 1255444.314
61 | 2617331.25 | 1255427.4735
62 | 2617373.0584 | 1255480.4922
63 | 2617373.0725 | 1255482.2772
64 | 2617127.2733 | 1255524.6539
65 | 2617124.4666 | 1255543.3495
66 | 2617128.3301 | 1255517.6145
67 | 2617124.2549 | 1255567.8308
68 | 2617129.2123 | 1255511.7377
69 | 2617124.6334 | 1255579.7514
70 | 2617131.5716 | 1255495.3081
71 | 2617125.807 | 1255618.3217
72 | 2617132.0318 | 1255487.7819
73 | 2617312.3061 | 1255546.5157
74 | 2617431.4757 | 1255635.3762
75 | 2617399.5086 | 1255611.5013
76 | 2617385.862 | 1255664.1465
77 | 2617418.5711 | 1255576.546
78 | 2617380.6862 | 1255682.8474
79 | 2617381.6748 | 1255701.1848
80 | 2617373.3296 | 1255514.91
81 | 2617401.0594 | 1255557.131
82 | 2617228.3219 | 1255569.7084
83 | 2617245.1446 | 1255602.5183
84 | 2617124.4003 | 1255462.803
85 | 2617119.4882 | 1255429.5779
86 | 2617138.3081 | 1255456.8523
87 | 2617330.1425 | 1255515.595
88 | 2617330.8216 | 1255507.5436
89 | 2617327.4688 | 1255547.2924
90 | 2617331.0467 | 1255504.8746
91 | 2617314.2146 | 1255546.6134
92 | 2617260.0049 | 1255376.0034
93 | 2617274.2325 | 1255379.1214
94 | 2617285.5341 | 1255382.2493
95 | 2617153.2595 | 1255387.1315
96 | 2617289.5672 | 1255368.4518
97 | 2617293.0059 | 1255384.3143
98 | 2617115.0994 | 1255387.5039
99 | 2617294.8083 | 1255644.1951
100 | 2617288.1985 | 1255630.1999
101 | 2617304.0027 | 1255657.1972
102 | 2617311.5386 | 1255669.9485
103 | 2617314.0775 | 1255674.2446
104 | 2617211.7198 | 1255438.7435
105 | 2617204.8809 | 1255454.7079
106 | 2617383.7102 | 1255713.5426
107 | 2617301.2681 | 1255386.5976
108 | 2617290.4698 | 1255352.644
109 | 2617173.0864 | 1255443.4862
110 | 2617180.6911 | 1255450.4573
111 | 2617190.3994 | 1255440.6891
112 | 2617119.7238 | 1255409.3576
113 | 2617145.3473 | 1255609.447
114 | 2617401.6724 | 1255765.1834
115 | 2617280.516 | 1255543.8089

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97698 | -0.44405 | 0.0016333 | 0.00040935
1 | 0.97703 | -0.44303 | 0.0017223 | 0.00043164
2 | 0.97697 | -0.44421 | 0.00094839 | 0.00023769
3 | 0.97705 | -0.44252 | 0.0014774 | 0.00037027
4 | 0.97691 | -0.44536 | 0.0022218 | 0.00055683
5 | 0.97714 | -0.44083 | 0.00099137 | 0.00024846
6 | 0.97717 | -0.44024 | 0.0013367 | 0.000335
7 | 0.99601 | -0.075778 | 0.00021433 | 5.3716e-05
8 | 0.99745 | -0.048313 | 0.00012949 | 3.2454e-05
9 | 0.99247 | -0.14332 | 0 | 0
10 | 0.99806 | -0.036675 | 0.0082051 | 0.0020564
11 | 0.99216 | -0.14938 | 0 | 0
12 | 1 | 0 | -0.25638 | -0.06464
13 | 0.99128 | -0.16625 | 0.00026596 | 6.6655e-05
14 | 0.99178 | -0.15671 | 0.00033367 | 8.3625e-05
15 | 0.99874 | -0.024139 | 0 | 0
16 | 0.98963 | -0.19784 | 0 | 0
17 | 0.99127 | -0.16657 | 0.015334 | 0.0038431
18 | 0.97726 | -0.43847 | 0.0022389 | 0.00056112
19 | 0.97729 | -0.43779 | 0.0008483 | 0.0002126
20 | 0.98853 | -0.22085 | 0.0019473 | 0.00048805
21 | 0.98864 | -0.2188 | 0.0010959 | 0.00027466
22 | 0.98837 | -0.22403 | 0 | 0
23 | 0.98919 | -0.20819 | 0.0010759 | 0.00026966
24 | 0.98788 | -0.23353 | 0 | 0
25 | 0.98961 | -0.2 | 0.0010209 | 0.00025586
26 | 0.98738 | -0.24335 | 0.0012456 | 0.00031217
27 | 0.99005 | -0.19141 | 0.0016261 | 0.00040754
28 | 0.98721 | -0.2465 | 0 | 0
29 | 0.99189 | -0.15588 | 0.0013635 | 0.00034172
30 | 0.99199 | -0.15382 | 0.004434 | 0.0011113
31 | 0.99108 | -0.17146 | 0 | 0
32 | 0.99285 | -0.1373 | 0.0011773 | 0.00029505
33 | 0.99105 | -0.17201 | 0.0010741 | 0.00026919
34 | 0.99038 | -0.1851 | 0 | 0
35 | 0.99332 | -0.12827 | 0 | 0
36 | 0.99103 | -0.17235 | 0.0010041 | 0.00025166
37 | 0.99027 | -0.18712 | 0 | 0
38 | 0.99388 | -0.11749 | 0.00087841 | 0.00022015
39 | 0.99312 | -0.13212 | 0 | 0
40 | 0.99102 | -0.17263 | 0.00099001 | 0.00024812
41 | 0.99014 | -0.18968 | 0.0015388 | 0.00038566
42 | 0.99763 | -0.045553 | 0.0063099 | 0.0015814
43 | 0.99767 | -0.044801 | 0.0062966 | 0.0015781
44 | 0.97732 | -0.43723 | 0.0045137 | 0.0011312
45 | 0.9777 | -0.42977 | 0 | 0
46 | 0.97858 | -0.41258 | 0 | 0
47 | 0.97765 | -0.43077 | 0.0020541 | 0.00051481
48 | 0.99181 | -0.15753 | 0.0018971 | 0.00047546
49 | 0.99183 | -0.15702 | 0 | 0
50 | 0.99788 | -0.040661 | 0.012261 | 0.003073
51 | 0.9983 | -0.032649 | 0 | 0
52 | 0.99754 | -0.047109 | 0.011205 | 0.0028081
53 | 0.99777 | -0.042713 | 0.0062896 | 0.0015763
54 | 0.99663 | -0.064687 | 0 | 0
55 | 0.9948 | -0.09959 | 0.00059699 | 0.00014962
56 | 0.99298 | -0.13469 | 0.0023606 | 0.00059163
57 | 0.99292 | -0.13599 | 0.0012132 | 0.00030407
58 | 0.99764 | -0.045138 | 0.020487 | 0.0051345
59 | 0.99638 | -0.0696 | 0 | 0
60 | 0.99198 | -0.15415 | 0 | 0
61 | 0.99184 | -0.15681 | 0.003977 | 0.00099672
62 | 0.99226 | -0.14877 | 0 | 0
63 | 0.99227 | -0.14858 | 0.0084898 | 0.0021277
64 | 0.98365 | -0.31368 | 0.0010811 | 0.00027094
65 | 0.98347 | -0.31723 | 0.0020823 | 0.00052187
66 | 0.98373 | -0.31221 | 0.0029829 | 0.00074759
67 | 0.98328 | -0.32091 | 0.0031427 | 0.00078764
68 | 0.9838 | -0.31066 | 0.0029405 | 0.00073697
69 | 0.98322 | -0.32203 | 0.001864 | 0.00046717
70 | 0.98407 | -0.30545 | 0.00081768 | 0.00020493
71 | 0.9831 | -0.32434 | 0 | 0
72 | 0.9842 | -0.30298 | 0.001096 | 0.0002747
73 | 0.99648 | -0.067436 | 0.00096751 | 0.00024248
74 | 0.98618 | -0.26674 | 0.0019097 | 0.00047862
75 | 0.98628 | -0.26473 | 0 | 0
76 | 0.98659 | -0.25857 | 0.0013228 | 0.00033153
77 | 0.98612 | -0.26788 | 0.0043912 | 0.0011005
78 | 0.98673 | -0.2559 | 0.001763 | 0.00044184
79 | 0.98689 | -0.25281 | 0.0010937 | 0.00027411
80 | 0.9927 | -0.14029 | 0.00068484 | 0.00017164
81 | 0.99297 | -0.13502 | 0.0035639 | 0.00089319
82 | 0.9962 | -0.073067 | 0.01664 | 0.0041705
83 | 0.99569 | -0.082778 | 0.014631 | 0.0036669
84 | 0.98467 | -0.2937 | 0 | 0
85 | 0.98329 | -0.32064 | 0 | 0
86 | 0.98543 | -0.27909 | 0.0011391 | 0.00028548
87 | 0.9955 | -0.086196 | 0.00049789 | 0.00012478
88 | 0.99549 | -0.086466 | 0.00094496 | 0.00023683
89 | 0.99557 | -0.084854 | 0 | 0
90 | 0.99549 | -0.086511 | 0.00095552 | 0.00023948
91 | 0.99636 | -0.069649 | 0.00077474 | 0.00019417
92 | 0.97764 | -0.4309 | 0.0027414 | 0.00068706
93 | 0.97752 | -0.43334 | 0.0014063 | 0.00035245
94 | 0.97744 | -0.435 | 0 | 0
95 | 0.98081 | -0.36882 | 0.00064156 | 0.00016079
96 | 0.97737 | -0.43628 | 0.000886 | 0.00022205
97 | 0.97742 | -0.4354 | 0.0010638 | 0.0002666
98 | 0.98196 | -0.34635 | 0 | 0
99 | 0.99001 | -0.19224 | 0.0016751 | 0.00041982
100 | 0.98999 | -0.19261 | 0.0013371 | 0.0003351
101 | 0.99005 | -0.19137 | 0 | 0
102 | 0.99 | -0.19245 | 0.0020181 | 0.00050579
103 | 0.98999 | -0.19264 | 0.0020934 | 0.00052466
104 | 0.98938 | -0.20263 | 0.0003283 | 8.2279e-05
105 | 0.98944 | -0.20158 | 0.0092703 | 0.0023234
106 | 0.98701 | -0.25046 | 0.0010869 | 0.0002724
107 | 0.9774 | -0.43568 | 0.0017843 | 0.00044718
108 | 0.97731 | -0.43749 | 0.004014 | 0.001006
109 | 0.98733 | -0.24231 | 0 | 0
110 | 0.98731 | -0.24261 | 0.0016213 | 0.00040633
111 | 0.98824 | -0.22463 | 0.0010811 | 0.00027095
112 | 0.98264 | -0.33317 | 0.0017956 | 0.00045002
113 | 0.98304 | -0.32563 | 0.0033238 | 0.00083302
114 | 0.98719 | -0.24706 | 0.00082692 | 0.00020725
115 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0048036 | -0.0012036 | 0.0048039 | 0.0012036 | 2.3336e-07 | 3.7619e-09 | 0.0073162 | 0.0073162 | 0.0073162 | 0.97698 | -0.44405 | 0.97703 | -0.44303 | 2.0099
1 | 0.0031703 | 0.00079422 | -0.0031703 | -0.00079424 | 2.4264e-08 | -1.9222e-08 | 0.0048285 | 0.0048286 | 0.0048286 | 0.97698 | -0.44405 | 0.97697 | -0.44421 | 1.3265
2 | -0.0065261 | -0.0016352 | 0.0065263 | 0.0016353 | 1.5672e-07 | 4.7318e-08 | 0.0099392 | 0.0099391 | 0.0099392 | 0.97703 | -0.44303 | 0.97705 | -0.44252 | 2.7305
3 | 0.0022219 | 0.00055655 | -0.0022218 | -0.00055683 | 1.2156e-07 | -2.7662e-07 | 0.0033841 | 0.0033842 | 0.0033842 | 0.97697 | -0.44421 | 0.97691 | -0.44536 | 0.92972
4 | -0.0080037 | -0.0020055 | 0.0080043 | 0.0020058 | 6.456e-07 | 2.6805e-07 | 0.012189 | 0.012189 | 0.012189 | 0.97705 | -0.44252 | 0.97714 | -0.44083 | 3.3487
5 | -0.0089957 | -0.0022543 | 0.0089959 | 0.0022544 | 2.5095e-07 | 1.1594e-07 | 0.013699 | 0.013699 | 0.013699 | 0.97714 | -0.44083 | 0.97717 | -0.44024 | 3.7634
6 | -0.010333 | -0.0025894 | 0.010333 | 0.0025898 | 8.7275e-07 | 4.4078e-07 | 0.015734 | 0.015734 | 0.015734 | 0.97717 | -0.44024 | 0.97726 | -0.43847 | 4.3226
7 | -0.084213 | -0.021474 | 0.084325 | 0.021546 | 0.00011183 | 7.1328e-05 | 0.12594 | 0.12594 | 0.12594 | 0.99601 | -0.075778 | 0.99745 | -0.048313 | 34.6001
8 | 0.083999 | 0.021421 | -0.083726 | -0.021247 | 0.00027294 | 0.00017409 | 0.12562 | 0.12562 | 0.12562 | 0.99601 | -0.075778 | 0.99247 | -0.14332 | 34.5121
9 | -0.084455 | -0.021578 | 0.084502 | 0.021609 | 4.7557e-05 | 3.0333e-05 | 0.12614 | 0.12614 | 0.12614 | 0.99745 | -0.048313 | 0.99806 | -0.036675 | 34.6531
10 | 0.083726 | 0.021247 | -0.083702 | -0.021231 | 2.4406e-05 | 1.5567e-05 | 0.12562 | 0.12562 | 0.12562 | 0.99247 | -0.14332 | 0.99216 | -0.14938 | 34.5121
11 | -0.092707 | -0.023665 | 0.092872 | 0.02377 | 0.00016461 | 0.00010505 | 0.13837 | 0.13837 | 0.13837 | 0.99806 | -0.036675 | 1 | 0 | 38.0138
12 | 0.068021 | 0.017297 | -0.067966 | -0.017262 | 5.5231e-05 | 3.5165e-05 | 0.10211 | 0.10211 | 0.10211 | 0.99216 | -0.14938 | 0.99128 | -0.16625 | 28.051
13 | 0.01568 | 0.003934 | -0.015675 | -0.0039309 | 5.4787e-06 | 3.1654e-06 | 0.023519 | 0.023519 | 0.023519 | 0.99216 | -0.14938 | 0.99178 | -0.15671 | 6.4612
14 | 0.16186 | 0.04087 | -0.16167 | -0.040751 | 0.00018697 | 0.00011921 | 0.24095 | 0.24095 | 0.24095 | 1 | 0 | 0.99874 | -0.024139 | 33.0981
15 | 0.0677 | 0.017195 | -0.067597 | -0.01713 | 0.00010278 | 6.5441e-05 | 0.10171 | 0.10171 | 0.10171 | 0.99128 | -0.16625 | 0.98963 | -0.19784 | 27.9414
16 | 0.015341 | 0.0038472 | -0.015334 | -0.0038431 | 7.2053e-06 | 4.1437e-06 | 0.023018 | 0.023018 | 0.023018 | 0.99178 | -0.15671 | 0.99127 | -0.16657 | 6.3237
17 | 0.094212 | 0.023802 | -0.094128 | -0.023748 | 8.3794e-05 | 5.348e-05 | 0.14043 | 0.14043 | 0.14043 | 0.99874 | -0.024139 | 0.99777 | -0.042713 | 38.5805
18 | 0.067459 | 0.016949 | -0.067431 | -0.016932 | 2.7388e-05 | 1.7434e-05 | 0.10052 | 0.10052 | 0.10052 | 0.99874 | -0.024139 | 0.9983 | -0.032649 | 27.6158
19 | 0.058325 | 0.014806 | -0.058312 | -0.014797 | 1.3435e-05 | 8.5388e-06 | 0.087765 | 0.087765 | 0.087765 | 0.98963 | -0.19784 | 0.98938 | -0.20263 | 24.1113
20 | 0.009272 | 0.0023241 | -0.0092703 | -0.0023234 | 1.6509e-06 | 7.6562e-07 | 0.013942 | 0.013942 | 0.013942 | 0.98963 | -0.19784 | 0.98944 | -0.20158 | 3.8301
21 | -0.012572 | -0.0031509 | 0.012573 | 0.0031512 | 4.054e-07 | 2.2249e-07 | 0.019143 | 0.019143 | 0.019143 | 0.97726 | -0.43847 | 0.97729 | -0.43779 | 5.2591
22 | -0.013421 | -0.0033638 | 0.013421 | 0.003364 | 3.5918e-07 | 2.0113e-07 | 0.020435 | 0.020435 | 0.020435 | 0.97729 | -0.43779 | 0.97732 | -0.43723 | 5.614
23 | -0.015612 | -0.0039178 | 0.015614 | 0.0039186 | 1.5314e-06 | 8.8528e-07 | 0.023502 | 0.023502 | 0.023502 | 0.98853 | -0.22085 | 0.98864 | -0.2188 | 6.4567
24 | 0.013665 | 0.0034297 | -0.013663 | -0.0034285 | 2.0721e-06 | 1.1588e-06 | 0.020571 | 0.020571 | 0.020571 | 0.98853 | -0.22085 | 0.98837 | -0.22403 | 5.6514
25 | -0.016709 | -0.0041933 | 0.016718 | 0.0041982 | 8.4547e-06 | 4.9538e-06 | 0.025152 | 0.025151 | 0.025152 | 0.98864 | -0.2188 | 0.98919 | -0.20819 | 6.9098
26 | 0.013663 | 0.0034285 | -0.013656 | -0.0034251 | 6.1852e-06 | 3.4593e-06 | 0.020571 | 0.020571 | 0.020571 | 0.98837 | -0.22403 | 0.98788 | -0.23353 | 5.6514
27 | -0.017794 | -0.0044679 | 0.017801 | 0.004472 | 6.9555e-06 | 4.1191e-06 | 0.02677 | 0.02677 | 0.02677 | 0.98919 | -0.20819 | 0.98961 | -0.2 | 7.3544
28 | 0.013656 | 0.0034251 | -0.01365 | -0.0034215 | 6.3879e-06 | 3.5731e-06 | 0.020571 | 0.020571 | 0.020571 | 0.98788 | -0.23353 | 0.98738 | -0.24335 | 5.6515
29 | -0.018822 | -0.0047279 | 0.018829 | 0.0047325 | 7.7224e-06 | 4.6119e-06 | 0.028305 | 0.028305 | 0.028305 | 0.98961 | -0.2 | 0.99005 | -0.19141 | 7.7761
30 | 0.012404 | 0.0031093 | -0.012403 | -0.0031083 | 1.8613e-06 | 1.0096e-06 | 0.018694 | 0.018694 | 0.018694 | 0.98738 | -0.24335 | 0.98721 | -0.2465 | 5.1358
31 | -0.020456 | -0.00514 | 0.02046 | 0.0051426 | 4.1878e-06 | 2.5283e-06 | 0.030749 | 0.030749 | 0.030749 | 0.99005 | -0.19141 | 0.99027 | -0.18712 | 8.4475
32 | 0.00082694 | 0.00020677 | -0.00082692 | -0.00020725 | 2.2212e-08 | -4.7332e-07 | 0.0012463 | 0.0012464 | 0.0012464 | 0.98721 | -0.2465 | 0.98719 | -0.24706 | 0.34243
33 | 0.011576 | 0.0029016 | -0.011574 | -0.0029004 | 2.1819e-06 | 1.1521e-06 | 0.017448 | 0.017448 | 0.017448 | 0.98721 | -0.2465 | 0.98701 | -0.25046 | 4.7934
34 | -0.033602 | -0.0084527 | 0.033605 | 0.0084548 | 3.3114e-06 | 2.0745e-06 | 0.05042 | 0.05042 | 0.05042 | 0.99189 | -0.15588 | 0.99199 | -0.15382 | 13.8517
35 | 0.032238 | 0.008111 | -0.032214 | -0.008096 | 2.3978e-05 | 1.4993e-05 | 0.048375 | 0.048375 | 0.048375 | 0.99189 | -0.15588 | 0.99108 | -0.17146 | 13.2898
36 | -0.038039 | -0.009566 | 0.038069 | 0.0095849 | 3.0026e-05 | 1.8899e-05 | 0.057071 | 0.057071 | 0.057071 | 0.99199 | -0.15382 | 0.99285 | -0.1373 | 15.6789
37 | 0.0030683 | 0.00076859 | -0.0030682 | -0.00076867 | 8.0773e-08 | -7.9095e-08 | 0.0046067 | 0.0046067 | 0.0046067 | 0.99108 | -0.17146 | 0.99105 | -0.17201 | 1.2656
38 | 0.029146 | 0.0073274 | -0.029127 | -0.0073156 | 1.8976e-05 | 1.1804e-05 | 0.043768 | 0.043768 | 0.043768 | 0.99108 | -0.17146 | 0.99038 | -0.1851 | 12.0242
39 | -0.039246 | -0.00988 | 0.039263 | 0.0098907 | 1.6963e-05 | 1.0687e-05 | 0.058836 | 0.058836 | 0.058836 | 0.99285 | -0.1373 | 0.99332 | -0.12827 | 16.1636
40 | 0.0019942 | 0.00049948 | -0.0019941 | -0.00049958 | 3.23e-08 | -1.0313e-07 | 0.0029941 | 0.0029941 | 0.0029941 | 0.99105 | -0.17201 | 0.99103 | -0.17235 | 0.82255
41 | 0.029127 | 0.0073156 | -0.029124 | -0.0073138 | 2.8045e-06 | 1.7447e-06 | 0.043768 | 0.043768 | 0.043768 | 0.99038 | -0.1851 | 0.99027 | -0.18712 | 12.0242
42 | -0.061469 | -0.015461 | 0.061501 | 0.015481 | 3.1669e-05 | 2.0139e-05 | 0.092102 | 0.092102 | 0.092102 | 0.99332 | -0.12827 | 0.99388 | -0.11749 | 25.3026
43 | 0.022205 | 0.00557 | -0.022201 | -0.0055675 | 4.0789e-06 | 2.4833e-06 | 0.033266 | 0.033266 | 0.033266 | 0.99332 | -0.12827 | 0.99312 | -0.13212 | 9.139
44 | 0.00099002 | 0.00024793 | -0.00099001 | -0.00024812 | 1.2908e-08 | -1.9246e-07 | 0.0014864 | 0.0014865 | 0.0014865 | 0.99103 | -0.17235 | 0.99102 | -0.17263 | 0.40838
45 | 0.0086645 | 0.0021713 | -0.0086635 | -0.0021708 | 1.0583e-06 | 4.6314e-07 | 0.01302 | 0.01302 | 0.01302 | 0.99027 | -0.18712 | 0.99014 | -0.18968 | 3.5768
46 | -0.062379 | -0.015701 | 0.062432 | 0.015735 | 5.3413e-05 | 3.3972e-05 | 0.093417 | 0.093417 | 0.093417 | 0.99388 | -0.11749 | 0.9948 | -0.09959 | 25.6639
47 | 0.0059253 | 0.0014849 | -0.0059245 | -0.0014848 | 7.2371e-07 | 1.464e-07 | 0.008878 | 0.0088781 | 0.0088781 | 0.99312 | -0.13212 | 0.99298 | -0.13469 | 2.439
48 | 0.016276 | 0.0040826 | -0.016273 | -0.0040808 | 3.0019e-06 | 1.7471e-06 | 0.024388 | 0.024388 | 0.024388 | 0.99312 | -0.13212 | 0.99292 | -0.13599 | 6.7001
49 | 0.0071247 | 0.0017851 | -0.0071241 | -0.0017849 | 5.7174e-07 | 1.9487e-07 | 0.010707 | 0.010707 | 0.010707 | 0.99014 | -0.18968 | 0.99005 | -0.19137 | 2.9415
50 | -0.0063099 | -0.0015814 | 0.0063101 | 0.0015815 | 2.2616e-07 | 5.5837e-08 | 0.0094116 | 0.0094116 | 0.0094116 | 0.99763 | -0.045553 | 0.99767 | -0.044801 | 2.5856
51 | -0.012607 | -0.0031596 | 0.012609 | 0.0031609 | 2.4868e-06 | 1.3466e-06 | 0.018803 | 0.018803 | 0.018803 | 0.99767 | -0.044801 | 0.99788 | -0.040661 | 5.1657
52 | -0.017935 | -0.0044952 | 0.017941 | 0.004499 | 6.3785e-06 | 3.7963e-06 | 0.027307 | 0.027307 | 0.027307 | 0.97732 | -0.43723 | 0.9777 | -0.42977 | 7.5019
53 | -0.031894 | -0.0079961 | 0.031921 | 0.0080125 | 2.6155e-05 | 1.6368e-05 | 0.048543 | 0.048543 | 0.048543 | 0.9777 | -0.42977 | 0.97858 | -0.41258 | 13.3359
54 | 0.013953 | 0.0034971 | -0.013952 | -0.0034967 | 6.6371e-07 | 3.7555e-07 | 0.021236 | 0.021236 | 0.021236 | 0.9777 | -0.42977 | 0.97765 | -0.43077 | 5.834
55 | -0.031921 | -0.0080125 | 0.031987 | 0.0080543 | 6.6771e-05 | 4.1782e-05 | 0.048543 | 0.048542 | 0.048543 | 0.97858 | -0.41258 | 0.98081 | -0.36882 | 13.3359
56 | 0.011898 | 0.0029819 | -0.011898 | -0.0029819 | 7.3505e-08 | 3.9549e-08 | 0.018109 | 0.018109 | 0.018109 | 0.97765 | -0.43077 | 0.97764 | -0.4309 | 4.9751
57 | -0.0018971 | -0.00047546 | 0.0018972 | 0.0004753 | 4.6222e-08 | -1.6678e-07 | 0.0028463 | 0.0028462 | 0.0028463 | 0.99181 | -0.15753 | 0.99183 | -0.15702 | 0.78194
58 | -0.0018972 | -0.0004753 | 0.0018972 | 0.00047523 | 1.8358e-08 | -6.6245e-08 | 0.0028462 | 0.0028462 | 0.0028462 | 0.99183 | -0.15702 | 0.99184 | -0.15681 | 0.78192
59 | -0.024871 | -0.0062339 | 0.02488 | 0.0062397 | 9.4975e-06 | 5.8378e-06 | 0.037087 | 0.037087 | 0.037087 | 0.99788 | -0.040661 | 0.9983 | -0.032649 | 10.1887
60 | 0.042551 | 0.010692 | -0.042522 | -0.010674 | 2.9348e-05 | 1.8529e-05 | 0.063435 | 0.063435 | 0.063435 | 0.9983 | -0.032649 | 0.99754 | -0.047109 | 17.4271
61 | 0.031317 | 0.0078655 | -0.031291 | -0.0078491 | 2.6245e-05 | 1.6379e-05 | 0.046721 | 0.046721 | 0.046721 | 0.99754 | -0.047109 | 0.99663 | -0.064687 | 12.8355
62 | 0.087838 | 0.022172 | -0.087828 | -0.022165 | 1.0203e-05 | 6.509e-06 | 0.13105 | 0.13105 | 0.13105 | 0.99777 | -0.042713 | 0.99764 | -0.045138 | 36.0036
63 | 0.031291 | 0.0078491 | -0.031284 | -0.0078445 | 7.3263e-06 | 4.5722e-06 | 0.046721 | 0.046721 | 0.046721 | 0.99663 | -0.064687 | 0.99638 | -0.0696 | 12.8355
64 | -0.063029 | -0.015885 | 0.063074 | 0.015913 | 4.4468e-05 | 2.8287e-05 | 0.09431 | 0.09431 | 0.09431 | 0.9948 | -0.09959 | 0.99557 | -0.084854 | 25.9092
65 | 0.0035639 | 0.00089316 | -0.0035639 | -0.00089319 | 5.6861e-08 | -3.2377e-08 | 0.0053406 | 0.0053406 | 0.0053406 | 0.99298 | -0.13469 | 0.99297 | -0.13502 | 1.4672
66 | 0.01506 | 0.0037768 | -0.015057 | -0.003775 | 3.0826e-06 | 1.7642e-06 | 0.02257 | 0.02257 | 0.02257 | 0.99292 | -0.13599 | 0.9927 | -0.14029 | 6.2006
67 | 0.067341 | 0.017031 | -0.067269 | -0.016985 | 7.1948e-05 | 4.5799e-05 | 0.1005 | 0.1005 | 0.1005 | 0.99764 | -0.045138 | 0.99648 | -0.067436 | 27.6088
68 | 0.031284 | 0.0078445 | -0.031279 | -0.0078413 | 5.1677e-06 | 3.2251e-06 | 0.046721 | 0.046721 | 0.046721 | 0.99638 | -0.0696 | 0.9962 | -0.073067 | 12.8355
69 | 0.0058749 | 0.0014721 | -0.0058742 | -0.001472 | 7.4539e-07 | 1.4668e-07 | 0.0088125 | 0.0088127 | 0.0088127 | 0.99198 | -0.15415 | 0.99184 | -0.15681 | 2.4211
70 | -0.0058749 | -0.0014721 | 0.0058764 | 0.0014724 | 1.5058e-06 | 2.9602e-07 | 0.0088125 | 0.0088123 | 0.0088125 | 0.99198 | -0.15415 | 0.99226 | -0.14877 | 2.421
71 | -0.0058764 | -0.0014724 | 0.0058765 | 0.0014724 | 5.1983e-08 | 1.0212e-08 | 0.0088123 | 0.0088123 | 0.0088123 | 0.99226 | -0.14877 | 0.99227 | -0.14858 | 2.421
72 | -0.014366 | -0.0036001 | 0.014372 | 0.0036034 | 5.6798e-06 | 3.2134e-06 | 0.021544 | 0.021544 | 0.021544 | 0.99227 | -0.14858 | 0.9927 | -0.14029 | 5.9186
73 | 0.010417 | 0.0026108 | -0.010415 | -0.00261 | 1.7605e-06 | 8.8676e-07 | 0.015758 | 0.015758 | 0.015758 | 0.98365 | -0.31368 | 0.98347 | -0.31723 | 4.3292
74 | -0.011498 | -0.0028818 | 0.011499 | 0.0028822 | 8.0758e-07 | 4.2649e-07 | 0.017394 | 0.017394 | 0.017394 | 0.98365 | -0.31368 | 0.98373 | -0.31221 | 4.7785
75 | 0.0083329 | 0.0020881 | -0.0083314 | -0.0020875 | 1.4608e-06 | 6.2399e-07 | 0.012608 | 0.012608 | 0.012608 | 0.98347 | -0.31723 | 0.98328 | -0.32091 | 3.4637
76 | -0.014482 | -0.0036298 | 0.014483 | 0.0036304 | 1.0694e-06 | 6.0894e-07 | 0.021906 | 0.021906 | 0.021906 | 0.98373 | -0.31221 | 0.9838 | -0.31066 | 6.018
77 | 0.0051887 | 0.0012998 | -0.0051884 | -0.0012998 | 2.7574e-07 | 2.5203e-08 | 0.0078519 | 0.007852 | 0.007852 | 0.98328 | -0.32091 | 0.98322 | -0.32203 | 2.1571
78 | -0.017423 | -0.0043674 | 0.017428 | 0.0043699 | 4.3238e-06 | 2.5564e-06 | 0.026353 | 0.026353 | 0.026353 | 0.9838 | -0.31066 | 0.98407 | -0.30545 | 7.2399
79 | 0.0033244 | 0.00083263 | -0.003324 | -0.00083288 | 3.6627e-07 | -2.5494e-07 | 0.0050309 | 0.0050311 | 0.0050311 | 0.98322 | -0.32203 | 0.9831 | -0.32434 | 1.3822
80 | -0.018245 | -0.0045749 | 0.018247 | 0.0045761 | 2.1523e-06 | 1.2817e-06 | 0.02759 | 0.027589 | 0.02759 | 0.98407 | -0.30545 | 0.9842 | -0.30298 | 7.5795
81 | 0.003324 | 0.00083288 | -0.0033238 | -0.00083302 | 2.038e-07 | -1.4178e-07 | 0.0050311 | 0.0050312 | 0.0050312 | 0.9831 | -0.32434 | 0.98304 | -0.32563 | 1.3822
82 | -0.019343 | -0.0048508 | 0.019352 | 0.004856 | 8.5583e-06 | 5.1381e-06 | 0.029247 | 0.029246 | 0.029247 | 0.9842 | -0.30298 | 0.98467 | -0.2937 | 8.0348
83 | 0.066302 | 0.016742 | -0.066295 | -0.016738 | 7.0312e-06 | 4.4751e-06 | 0.099051 | 0.099051 | 0.099051 | 0.99648 | -0.067436 | 0.99636 | -0.069649 | 27.2119
84 | -0.0019097 | -0.00047862 | 0.0019099 | 0.00047799 | 1.8288e-07 | -6.3252e-07 | 0.0028815 | 0.0028812 | 0.0028815 | 0.98618 | -0.26674 | 0.98628 | -0.26473 | 0.79162
85 | -0.0063017 | -0.0015784 | 0.0063036 | 0.0015789 | 1.8472e-06 | 4.8647e-07 | 0.0095072 | 0.0095069 | 0.0095072 | 0.98628 | -0.26473 | 0.98659 | -0.25857 | 2.6119
86 | 0.0043918 | 0.0011004 | -0.0043912 | -0.0011005 | 6.5871e-07 | -8.8925e-08 | 0.0066259 | 0.0066261 | 0.0066261 | 0.98628 | -0.26473 | 0.98612 | -0.26788 | 1.8204
87 | -0.0076264 | -0.0019104 | 0.0076274 | 0.0019108 | 9.6935e-07 | 3.7084e-07 | 0.011502 | 0.011502 | 0.011502 | 0.98659 | -0.25857 | 0.98673 | -0.2559 | 3.1599
88 | -0.0093903 | -0.0023527 | 0.0093917 | 0.0023533 | 1.3854e-06 | 6.5127e-07 | 0.014161 | 0.01416 | 0.014161 | 0.98673 | -0.2559 | 0.98689 | -0.25281 | 3.8903
89 | -0.010485 | -0.0026274 | 0.010487 | 0.002628 | 1.1739e-06 | 5.9123e-07 | 0.01581 | 0.01581 | 0.01581 | 0.98689 | -0.25281 | 0.98701 | -0.25046 | 4.3433
90 | 0.014638 | 0.0036708 | -0.014631 | -0.0036669 | 6.7722e-06 | 3.8427e-06 | 0.021866 | 0.021866 | 0.021866 | 0.9962 | -0.073067 | 0.99569 | -0.082778 | 6.0071
91 | 0.034545 | 0.0087409 | -0.034501 | -0.0087129 | 4.46e-05 | 2.799e-05 | 0.052234 | 0.052234 | 0.052234 | 0.98467 | -0.2937 | 0.98329 | -0.32064 | 14.3501
92 | -0.053898 | -0.013597 | 0.053935 | 0.013621 | 3.7726e-05 | 2.3952e-05 | 0.08148 | 0.08148 | 0.08148 | 0.98467 | -0.2937 | 0.98543 | -0.27909 | 22.3847
93 | 0.034501 | 0.0087129 | -0.03448 | -0.0087 | 2.0698e-05 | 1.299e-05 | 0.052234 | 0.052234 | 0.052234 | 0.98329 | -0.32064 | 0.98264 | -0.33317 | 14.3501
94 | -0.055074 | -0.013906 | 0.055172 | 0.013968 | 9.7252e-05 | 6.1763e-05 | 0.0832 | 0.0832 | 0.0832 | 0.98543 | -0.27909 | 0.98733 | -0.24231 | 22.8573
95 | 0.0019005 | 0.00047618 | -0.0019005 | -0.00047627 | 2.4451e-08 | -8.9402e-08 | 0.0028407 | 0.0028407 | 0.0028407 | 0.9955 | -0.086196 | 0.99549 | -0.086466 | 0.78043
96 | -0.0023984 | -0.00060096 | 0.0023985 | 0.00060065 | 1.533e-07 | -3.155e-07 | 0.0035849 | 0.0035848 | 0.0035849 | 0.9955 | -0.086196 | 0.99557 | -0.084854 | 0.98487
97 | 0.00095552 | 0.00023944 | -0.00095552 | -0.00023948 | 2.049e-09 | -3.3512e-08 | 0.0014283 | 0.0014283 | 0.0014283 | 0.99549 | -0.086466 | 0.99549 | -0.086511 | 0.39238
98 | -0.065472 | -0.016513 | 0.06552 | 0.016544 | 4.7694e-05 | 3.0352e-05 | 0.097894 | 0.097894 | 0.097894 | 0.99557 | -0.084854 | 0.99636 | -0.069649 | 26.894
99 | 0.0091566 | 0.0022948 | -0.0091556 | -0.0022943 | 1.0647e-06 | 4.9814e-07 | 0.013937 | 0.013937 | 0.013937 | 0.97764 | -0.4309 | 0.97752 | -0.43334 | 3.8288
100 | 0.0077493 | 0.0019419 | -0.0077486 | -0.0019416 | 6.119e-07 | 2.4462e-07 | 0.011796 | 0.011796 | 0.011796 | 0.97752 | -0.43334 | 0.97744 | -0.435 | 3.2407
101 | 0.0049005 | 0.001228 | -0.0049002 | -0.001228 | 3.0002e-07 | 1.1854e-08 | 0.0074603 | 0.0074604 | 0.0074604 | 0.97744 | -0.435 | 0.97737 | -0.43628 | 2.0496
102 | 0.0028481 | 0.00071363 | -0.0028481 | -0.00071369 | 5.465e-08 | -6.2184e-08 | 0.0043358 | 0.0043359 | 0.0043359 | 0.97744 | -0.435 | 0.97742 | -0.4354 | 1.1912
103 | -0.032629 | -0.0082151 | 0.032664 | 0.008237 | 3.5091e-05 | 2.1976e-05 | 0.049516 | 0.049515 | 0.049516 | 0.98081 | -0.36882 | 0.98196 | -0.34635 | 13.6032
104 | 0.0040142 | 0.0010059 | -0.004014 | -0.001006 | 2.3111e-07 | -5.8861e-08 | 0.0061115 | 0.0061116 | 0.0061116 | 0.97737 | -0.43628 | 0.97731 | -0.43749 | 1.679
105 | 0.0017843 | 0.00044709 | -0.0017843 | -0.00044718 | 2.3719e-08 | -9.2253e-08 | 0.0027164 | 0.0027164 | 0.0027164 | 0.97742 | -0.4354 | 0.9774 | -0.43568 | 0.74627
106 | -0.032664 | -0.008237 | 0.032685 | 0.0082499 | 2.0619e-05 | 1.2912e-05 | 0.049515 | 0.049515 | 0.049515 | 0.98196 | -0.34635 | 0.98264 | -0.33317 | 13.6031
107 | 0.0013371 | 0.00033492 | -0.0013371 | -0.0003351 | 2.3442e-08 | -1.8401e-07 | 0.0020096 | 0.0020097 | 0.0020097 | 0.99001 | -0.19224 | 0.98999 | -0.19261 | 0.55212
108 | -0.0030122 | -0.00075474 | 0.0030123 | 0.00075461 | 1.2548e-07 | -1.2962e-07 | 0.0045274 | 0.0045273 | 0.0045274 | 0.99001 | -0.19224 | 0.99005 | -0.19137 | 1.2438
109 | 0.0041118 | 0.0010303 | -0.0041116 | -0.0010304 | 2.1212e-07 | -5.4703e-08 | 0.0061798 | 0.0061799 | 0.0061799 | 0.99005 | -0.19137 | 0.99 | -0.19245 | 1.6978
110 | 0.0020934 | 0.00052461 | -0.0020934 | -0.00052466 | 1.8527e-08 | -5.2307e-08 | 0.0031465 | 0.0031466 | 0.0031466 | 0.99 | -0.19245 | 0.98999 | -0.19264 | 0.86444
111 | 0.057983 | 0.014715 | -0.057922 | -0.014676 | 6.1273e-05 | 3.8939e-05 | 0.087271 | 0.087271 | 0.087271 | 0.98938 | -0.20263 | 0.98824 | -0.22463 | 23.9757
112 | 0.0016213 | 0.00040621 | -0.0016213 | -0.00040633 | 2.3262e-08 | -1.1798e-07 | 0.0024434 | 0.0024435 | 0.0024435 | 0.98733 | -0.24231 | 0.98731 | -0.24261 | 0.67129
113 | -0.056793 | -0.014374 | 0.056841 | 0.014405 | 4.8238e-05 | 3.0648e-05 | 0.085644 | 0.085644 | 0.085644 | 0.98733 | -0.24231 | 0.98824 | -0.22463 | 23.5285

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.26266 | 0.066214

## res_load
| p_mw | q_mvar
0 | 0.0016333 | 0.00040935
1 | 0.0017223 | 0.00043164
2 | 0.00094839 | 0.00023769
3 | 0.0014774 | 0.00037027
4 | 0.0022218 | 0.00055683
5 | 0.00099137 | 0.00024846
6 | 0.0013367 | 0.000335
7 | 0.00021433 | 5.3716e-05
8 | 0.00012949 | 3.2454e-05
9 | 0.0082051 | 0.0020564
10 | 0.006278 | 0.0015734
11 | 0.00026596 | 6.6655e-05
12 | 0.00033367 | 8.3625e-05
13 | 0.015334 | 0.0038431
14 | 0.0022389 | 0.00056112
15 | 0.0008483 | 0.0002126
16 | 0.0019473 | 0.00048805
17 | 0.0010959 | 0.00027466
18 | 0.0010759 | 0.00026966
19 | 0.0010209 | 0.00025586
20 | 0.0012456 | 0.00031217
21 | 0.0016261 | 0.00040754
22 | 0.0013635 | 0.00034172
23 | 0.004434 | 0.0011113
24 | 0.0011773 | 0.00029505
25 | 0.0010741 | 0.00026919
26 | 0.0010041 | 0.00025166
27 | 0.00087841 | 0.00022015
28 | 0.00099001 | 0.00024812
29 | 0.0015388 | 0.00038566
30 | 0.0063099 | 0.0015814
31 | 0.0062966 | 0.0015781
32 | 0.0045137 | 0.0011312
33 | 0.0020541 | 0.00051481
34 | 0.0018971 | 0.00047546
35 | 0.012261 | 0.003073
36 | 0.011205 | 0.0028081
37 | 0.0062896 | 0.0015763
38 | 0.00059699 | 0.00014962
39 | 0.0023606 | 0.00059163
40 | 0.0012132 | 0.00030407
41 | 0.020487 | 0.0051345
42 | 0.003977 | 0.00099672
43 | 0.0084898 | 0.0021277
44 | 0.0010811 | 0.00027094
45 | 0.0020823 | 0.00052187
46 | 0.0029829 | 0.00074759
47 | 0.0031427 | 0.00078764
48 | 0.0029405 | 0.00073697
49 | 0.001864 | 0.00046717
50 | 0.00081768 | 0.00020493
51 | 0.001096 | 0.0002747
52 | 0.00096751 | 0.00024248
53 | 0.0019097 | 0.00047862
54 | 0.0013228 | 0.00033153
55 | 0.0043912 | 0.0011005
56 | 0.001763 | 0.00044184
57 | 0.0010937 | 0.00027411
58 | 0.00068484 | 0.00017164
59 | 0.0035639 | 0.00089319
60 | 0.01664 | 0.0041705
61 | 0.014631 | 0.0036669
62 | 0.0011391 | 0.00028548
63 | 0.00049789 | 0.00012478
64 | 0.00094496 | 0.00023683
65 | 0.00095552 | 0.00023948
66 | 0.00077474 | 0.00019417
67 | 0.0027414 | 0.00068706
68 | 0.0014063 | 0.00035245
69 | 0.00064156 | 0.00016079
70 | 0.000886 | 0.00022205
71 | 0.0010638 | 0.0002666
72 | 0.0016751 | 0.00041982
73 | 0.0013371 | 0.0003351
74 | 0.0020181 | 0.00050579
75 | 0.0020934 | 0.00052466
76 | 0.0003283 | 8.2279e-05
77 | 0.0092703 | 0.0023234
78 | 0.0010869 | 0.0002724
79 | 0.0017843 | 0.00044718
80 | 0.004014 | 0.001006
81 | 0.0016213 | 0.00040633
82 | 0.0010811 | 0.00027095
83 | 0.0017956 | 0.00045002
84 | 0.0033238 | 0.00083302
85 | 0.00082692 | 0.00020725

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1