## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2475-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2475-3_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2475-3_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2475-3_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2475-3_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2475-3_0_3_node_74 | 0.4 | n |  | TRUE
6 | bus_LV_2475-3_0_3_node_88 | 0.4 | n |  | TRUE
7 | bus_LV_2475-3_0_3_node_75 | 0.4 | n |  | TRUE
8 | bus_LV_2475-3_0_3_node_65 | 0.4 | n |  | TRUE
9 | bus_LV_2475-3_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2475-3_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2475-3_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2475-3_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2475-3_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2475-3_0_3_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_2475-3_0_3_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_2475-3_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2475-3_0_3_node_112 | 0.4 | n |  | TRUE
18 | bus_LV_2475-3_0_3_node_42 | 0.4 | n |  | TRUE
19 | bus_LV_2475-3_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_2475-3_0_3_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_2475-3_0_3_node_123 | 0.4 | n |  | TRUE
22 | bus_LV_2475-3_0_3_node_83 | 0.4 | n |  | TRUE
23 | bus_LV_2475-3_0_3_node_41 | 0.4 | n |  | TRUE
24 | bus_LV_2475-3_0_3_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_2475-3_0_3_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2475-3_0_3_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_2475-3_0_3_node_50 | 0.4 | n |  | TRUE
28 | bus_LV_2475-3_0_3_node_48 | 0.4 | n |  | TRUE
29 | bus_LV_2475-3_0_3_node_49 | 0.4 | n |  | TRUE
30 | bus_LV_2475-3_0_3_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_2475-3_0_3_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_2475-3_0_3_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_2475-3_0_3_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_2475-3_0_3_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_2475-3_0_3_node_80 | 0.4 | n |  | TRUE
36 | bus_LV_2475-3_0_3_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_2475-3_0_3_node_81 | 0.4 | n |  | TRUE
38 | bus_LV_2475-3_0_3_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_2475-3_0_3_node_51 | 0.4 | n |  | TRUE
40 | bus_LV_2475-3_0_3_node_52 | 0.4 | n |  | TRUE
41 | bus_LV_2475-3_0_3_node_47 | 0.4 | n |  | TRUE
42 | bus_LV_2475-3_0_3_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_2475-3_0_3_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_2475-3_0_3_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_2475-3_0_3_node_25 | 0.4 | n |  | TRUE
46 | bus_LV_2475-3_0_3_node_30 | 0.4 | n |  | TRUE
47 | bus_LV_2475-3_0_3_node_99 | 0.4 | n |  | TRUE
48 | bus_LV_2475-3_0_3_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_2475-3_0_3_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_2475-3_0_3_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_2475-3_0_3_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_2475-3_0_3_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_2475-3_0_3_node_100 | 0.4 | n |  | TRUE
54 | bus_LV_2475-3_0_3_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_2475-3_0_3_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_2475-3_0_3_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_2475-3_0_3_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_2475-3_0_3_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_2475-3_0_3_node_87 | 0.4 | n |  | TRUE
60 | bus_LV_2475-3_0_3_node_60 | 0.4 | n |  | TRUE
61 | bus_LV_2475-3_0_3_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_2475-3_0_3_node_54 | 0.4 | n |  | TRUE
63 | bus_LV_2475-3_0_3_node_82 | 0.4 | n |  | TRUE
64 | bus_LV_2475-3_0_3_node_43 | 0.4 | n |  | TRUE
65 | bus_LV_2475-3_0_3_node_44 | 0.4 | n |  | TRUE
66 | bus_LV_2475-3_0_3_node_45 | 0.4 | n |  | TRUE
67 | bus_LV_2475-3_0_3_node_46 | 0.4 | n |  | TRUE
68 | bus_LV_2475-3_0_3_node_61 | 0.4 | n |  | TRUE
69 | bus_LV_2475-3_0_3_node_63 | 0.4 | n |  | TRUE
70 | bus_LV_2475-3_0_3_node_86 | 0.4 | n |  | TRUE
71 | bus_LV_2475-3_0_3_node_85 | 0.4 | n |  | TRUE
72 | bus_LV_2475-3_0_3_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_2475-3_0_3_node_55 | 0.4 | n |  | TRUE
74 | bus_LV_2475-3_0_3_node_57 | 0.4 | n |  | TRUE
75 | bus_LV_2475-3_0_3_node_58 | 0.4 | n |  | TRUE
76 | bus_LV_2475-3_0_3_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_2475-3_0_3_node_115 | 0.4 | n |  | TRUE
78 | bus_LV_2475-3_0_3_node_116 | 0.4 | n |  | TRUE
79 | bus_LV_2475-3_0_3_node_62 | 0.4 | n |  | TRUE
80 | bus_LV_2475-3_0_3_node_64 | 0.4 | n |  | TRUE
81 | bus_LV_2475-3_0_3_node_66 | 0.4 | n |  | TRUE
82 | bus_LV_2475-3_0_3_node_72 | 0.4 | n |  | TRUE
83 | bus_LV_2475-3_0_3_node_73 | 0.4 | n |  | TRUE
84 | bus_LV_2475-3_0_3_node_67 | 0.4 | n |  | TRUE
85 | bus_LV_2475-3_0_3_node_68 | 0.4 | n |  | TRUE
86 | bus_LV_2475-3_0_3_node_69 | 0.4 | n |  | TRUE
87 | bus_LV_2475-3_0_3_node_70 | 0.4 | n |  | TRUE
88 | bus_LV_2475-3_0_3_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_2475-3_0_3_node_102 | 0.4 | n |  | TRUE
90 | bus_LV_2475-3_0_3_node_93 | 0.4 | n |  | TRUE
91 | bus_LV_2475-3_0_3_node_128 | 0.4 | n |  | TRUE
92 | bus_LV_2475-3_0_3_node_111 | 0.4 | n |  | TRUE
93 | bus_LV_2475-3_0_3_node_122 | 0.4 | n |  | TRUE
94 | bus_LV_2475-3_0_3_node_127 | 0.4 | n |  | TRUE
95 | bus_LV_2475-3_0_3_node_109 | 0.4 | n |  | TRUE
96 | bus_LV_2475-3_0_3_node_90 | 0.4 | n |  | TRUE
97 | bus_LV_2475-3_0_3_node_92 | 0.4 | n |  | TRUE
98 | bus_LV_2475-3_0_3_node_89 | 0.4 | n |  | TRUE
99 | bus_LV_2475-3_0_3_node_113 | 0.4 | n |  | TRUE
100 | bus_LV_2475-3_0_3_node_119 | 0.4 | n |  | TRUE
101 | bus_LV_2475-3_0_3_node_117 | 0.4 | n |  | TRUE
102 | bus_LV_2475-3_0_3_node_76 | 0.4 | n |  | TRUE
103 | bus_LV_2475-3_0_3_node_77 | 0.4 | n |  | TRUE
104 | bus_LV_2475-3_0_3_node_78 | 0.4 | n |  | TRUE
105 | bus_LV_2475-3_0_3_node_126 | 0.4 | n |  | TRUE
106 | bus_LV_2475-3_0_3_node_79 | 0.4 | n |  | TRUE
107 | bus_LV_2475-3_0_3_node_125 | 0.4 | n |  | TRUE
108 | bus_LV_2475-3_0_3_node_101 | 0.4 | n |  | TRUE
109 | bus_LV_2475-3_0_3_node_106 | 0.4 | n |  | TRUE
110 | bus_LV_2475-3_0_3_node_110 | 0.4 | n |  | TRUE
111 | bus_LV_2475-3_0_3_node_108 | 0.4 | n |  | TRUE
112 | bus_LV_2475-3_0_3_node_104 | 0.4 | n |  | TRUE
113 | bus_LV_2475-3_0_3_node_120 | 0.4 | n |  | TRUE
114 | bus_LV_2475-3_0_3_node_91 | 0.4 | n |  | TRUE
115 | bus_LV_2475-3_0_3_node_94 | 0.4 | n |  | TRUE
116 | bus_LV_2475-3_0_3_node_95 | 0.4 | n |  | TRUE
117 | bus_LV_2475-3_0_3_node_96 | 0.4 | n |  | TRUE
118 | bus_LV_2475-3_0_3_node_97 | 0.4 | n |  | TRUE
119 | bus_LV_2475-3_0_3_node_98 | 0.4 | n |  | TRUE
120 | bus_LV_2475-3_0_3_node_114 | 0.4 | n |  | TRUE
121 | bus_LV_2475-3_0_3_node_124 | 0.4 | n |  | TRUE
122 | bus_LV_2475-3_0_3_node_103 | 0.4 | n |  | TRUE
123 | bus_LV_2475-3_0_3_node_105 | 0.4 | n |  | TRUE
124 | bus_LV_2475-3_0_3_node_107 | 0.4 | n |  | TRUE
125 | bus_LV_2475-3_0_3_node_121 | 0.4 | n |  | TRUE
126 | bus_LV_2475-3_0_3_node_118 | 0.4 | n |  | TRUE
127 | bus_MV_287_0_node_3 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2475-3_0_3_load_0 | 0 | 0.0037184 | 0.00093192 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2475-3_0_3_load_1 | 1 | 0.0020511 | 0.00051406 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2475-3_0_3_load_2 | 2 | 0.00053604 | 0.00013434 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2475-3_0_3_load_3 | 3 | 0.0013393 | 0.00033567 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2475-3_0_3_load_4 | 4 | 0.0022079 | 0.00055336 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2475-3_0_3_load_74 | 5 | 0.0021476 | 0.00053823 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2475-3_0_3_load_88 | 6 | 0.0018044 | 0.00045223 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2475-3_0_3_load_75 | 7 | 0.0016343 | 0.0004096 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2475-3_0_3_load_5 | 9 | 0.00049465 | 0.00012397 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2475-3_0_3_load_6 | 10 | 0.0018292 | 0.00045845 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2475-3_0_3_load_9 | 13 | 0.0013147 | 0.0003295 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2475-3_0_3_load_14 | 14 | 0.0013723 | 0.00034394 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2475-3_0_3_load_112 | 17 | 0.00066473 | 0.0001666 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2475-3_0_3_load_42 | 18 | 0.0015758 | 0.00039494 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2475-3_0_3_load_12 | 19 | 0.0022107 | 0.00055405 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2475-3_0_3_load_31 | 20 | 0.0017542 | 0.00043963 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2475-3_0_3_load_123 | 21 | 0.0013803 | 0.00034593 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2475-3_0_3_load_83 | 22 | 0.00042824 | 0.00010733 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2475-3_0_3_load_41 | 23 | 0.00055458 | 0.00013899 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2475-3_0_3_load_11 | 24 | 0.0011221 | 0.00028121 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2475-3_0_3_load_13 | 25 | 0.0028266 | 0.00070841 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2475-3_0_3_load_15 | 26 | 0.00099003 | 0.00024813 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2475-3_0_3_load_50 | 27 | 0.0028025 | 0.00070236 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2475-3_0_3_load_48 | 28 | 0.0029056 | 0.00072822 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2475-3_0_3_load_49 | 29 | 0.0034338 | 0.0008606 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2475-3_0_3_load_16 | 30 | 0.0019613 | 0.00049154 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2475-3_0_3_load_17 | 31 | 0.002681 | 0.00067192 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2475-3_0_3_load_18 | 32 | 0.00090889 | 0.00022779 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2475-3_0_3_load_19 | 33 | 0.0014972 | 0.00037523 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2475-3_0_3_load_20 | 34 | 0.00084912 | 0.00021281 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2475-3_0_3_load_80 | 35 | 0.0026028 | 0.00065232 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2475-3_0_3_load_21 | 36 | 0.0015894 | 0.00039833 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2475-3_0_3_load_81 | 37 | 0.0051314 | 0.001286 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2475-3_0_3_load_22 | 38 | 0.0018505 | 0.00046377 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2475-3_0_3_load_52 | 40 | 0.0019885 | 0.00049837 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2475-3_0_3_load_47 | 41 | 0.0023659 | 0.00059295 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2475-3_0_3_load_23 | 42 | 0.0018473 | 0.00046298 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2475-3_0_3_load_26 | 44 | 0.000712 | 0.00017844 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2475-3_0_3_load_25 | 45 | 0.0018094 | 0.00045349 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2475-3_0_3_load_30 | 46 | 0.0013924 | 0.00034897 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2475-3_0_3_load_99 | 47 | 0.0007191 | 0.00018022 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2475-3_0_3_load_28 | 49 | 0.0020508 | 0.00051398 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2475-3_0_3_load_29 | 50 | 0.002019 | 0.00050602 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2475-3_0_3_load_39 | 51 | 0.0018325 | 0.00045927 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2475-3_0_3_load_40 | 52 | 0.00098366 | 0.00024653 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2475-3_0_3_load_34 | 54 | 0.0020968 | 0.00052551 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2475-3_0_3_load_35 | 55 | 0.00089634 | 0.00022464 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2475-3_0_3_load_36 | 56 | 0.0021538 | 0.0005398 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2475-3_0_3_load_37 | 57 | 0.0025461 | 0.00063811 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2475-3_0_3_load_87 | 59 | 0.0022913 | 0.00057426 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2475-3_0_3_load_60 | 60 | 0.0015496 | 0.00038837 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2475-3_0_3_load_56 | 61 | 0.0022271 | 0.00055817 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2475-3_0_3_load_54 | 62 | 0.0039978 | 0.0010019 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2475-3_0_3_load_82 | 63 | 0.0012822 | 0.00032134 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2475-3_0_3_load_43 | 64 | 0.0015585 | 0.0003906 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2475-3_0_3_load_44 | 65 | 0.0031868 | 0.00079869 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2475-3_0_3_load_45 | 66 | 0.001835 | 0.00045989 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2475-3_0_3_load_46 | 67 | 0.00093371 | 0.00023401 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2475-3_0_3_load_61 | 68 | 0.0014744 | 0.00036952 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2475-3_0_3_load_63 | 69 | 0.0029791 | 0.00074664 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2475-3_0_3_load_86 | 70 | 0.0015423 | 0.00038654 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2475-3_0_3_load_85 | 71 | 0.00075267 | 0.00018864 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2475-3_0_3_load_53 | 72 | 0.0017785 | 0.00044573 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2475-3_0_3_load_55 | 73 | 0.0011767 | 0.0002949 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2475-3_0_3_load_57 | 74 | 0.00094053 | 0.00023572 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2475-3_0_3_load_58 | 75 | 0.0040721 | 0.0010206 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2475-3_0_3_load_59 | 76 | 0.0034184 | 0.00085672 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2475-3_0_3_load_115 | 77 | 0.00052724 | 0.00013214 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2475-3_0_3_load_62 | 79 | 0.0017141 | 0.00042958 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2475-3_0_3_load_66 | 81 | 0.0013879 | 0.00034784 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2475-3_0_3_load_72 | 82 | 0.0026835 | 0.00067256 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2475-3_0_3_load_73 | 83 | 0.0025192 | 0.00063136 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2475-3_0_3_load_67 | 84 | 0.0026114 | 0.00065449 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2475-3_0_3_load_68 | 85 | 0.00051388 | 0.00012879 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2475-3_0_3_load_70 | 87 | 0.00028835 | 7.2266e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2475-3_0_3_load_71 | 88 | 0.0021973 | 0.00055069 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2475-3_0_3_load_102 | 89 | 0.0016841 | 0.00042208 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2475-3_0_3_load_111 | 92 | 0.0059072 | 0.0014805 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2475-3_0_3_load_122 | 93 | 0.00064228 | 0.00016097 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2475-3_0_3_load_109 | 95 | 0.003501 | 0.00087743 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2475-3_0_3_load_90 | 96 | 0.0012075 | 0.00030263 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2475-3_0_3_load_92 | 97 | 0.0011609 | 0.00029094 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2475-3_0_3_load_89 | 98 | 0.0044367 | 0.0011119 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2475-3_0_3_load_119 | 100 | 0.0006703 | 0.00016799 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2475-3_0_3_load_117 | 101 | 0.00090869 | 0.00022774 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2475-3_0_3_load_76 | 102 | 0.0017291 | 0.00043335 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2475-3_0_3_load_77 | 103 | 0.0033958 | 0.00085107 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2475-3_0_3_load_126 | 105 | 0.0026925 | 0.00067479 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2475-3_0_3_load_125 | 107 | 0.0008008 | 0.0002007 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2475-3_0_3_load_101 | 108 | 0.0014225 | 0.00035651 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2475-3_0_3_load_106 | 109 | 0.0010891 | 0.00027294 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2475-3_0_3_load_110 | 110 | 0.0081616 | 0.0020455 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2475-3_0_3_load_108 | 111 | 0.0026797 | 0.0006716 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2475-3_0_3_load_104 | 112 | 0.0017468 | 0.00043778 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2475-3_0_3_load_120 | 113 | 0.0020646 | 0.00051744 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2475-3_0_3_load_91 | 114 | 0.0019503 | 0.00048879 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2475-3_0_3_load_94 | 115 | 0.0011876 | 0.00029765 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2475-3_0_3_load_95 | 116 | 0.0017937 | 0.00044956 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2475-3_0_3_load_96 | 117 | 0.00099252 | 0.00024875 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2475-3_0_3_load_97 | 118 | 0.0010022 | 0.00025117 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2475-3_0_3_load_98 | 119 | 0.0012634 | 0.00031663 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2475-3_0_3_load_114 | 120 | 0.0028423 | 0.00071234 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2475-3_0_3_load_124 | 121 | 0.0014175 | 0.00035525 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2475-3_0_3_load_103 | 122 | 0.001453 | 0.00036415 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2475-3_0_3_load_105 | 123 | 0.0047358 | 0.0011869 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2475-3_0_3_load_107 | 124 | 0.0027038 | 0.00067763 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2475-3_0_3_load_121 | 125 | 0.00066318 | 0.00016621 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2475-3_0_3_load_118 | 126 | 0.0021568 | 0.00054055 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 72 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2475-3_0_3_line_0 |  | 0 | 1 | 0.019449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2475-3_0_3_line_1 |  | 0 | 2 | 0.0051703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2475-3_0_3_line_2 |  | 1 | 3 | 0.026218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2475-3_0_3_line_3 |  | 2 | 4 | 0.0046434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2475-3_0_3_line_4 |  | 3 | 5 | 0.0023684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2475-3_0_3_line_5 |  | 4 | 6 | 0.027597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2475-3_0_3_line_6 |  | 5 | 7 | 0.02122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2475-3_0_3_line_7 |  | 6 | 8 | 0.030075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2475-3_0_3_line_8 |  | 7 | 50 | 0.028755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2475-3_0_3_line_9 |  | 8 | 69 | 0.025175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2475-3_0_3_line_10 |  | 8 | 27 | 0.054195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2475-3_0_3_line_11 |  | 9 | 10 | 0.010055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2475-3_0_3_line_12 |  | 9 | 11 | 0.0081654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2475-3_0_3_line_13 |  | 10 | 12 | 0.021352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2475-3_0_3_line_14 |  | 11 | 13 | 0.018995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2475-3_0_3_line_15 |  | 12 | 14 | 0.041643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2475-3_0_3_line_16 |  | 12 | 15 | 0.011631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2475-3_0_3_line_17 |  | 14 | 19 | 0.03141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2475-3_0_3_line_18 |  | 15 | 20 | 0.052013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2475-3_0_3_line_19 |  | 16 | 17 | 0.020868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2475-3_0_3_line_20 |  | 16 | 18 | 0.017842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2475-3_0_3_line_21 |  | 17 | 21 | 0.022598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2475-3_0_3_line_22 |  | 18 | 22 | 0.059719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2475-3_0_3_line_23 |  | 18 | 23 | 0.016143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2475-3_0_3_line_24 |  | 19 | 24 | 0.0047077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2475-3_0_3_line_25 |  | 21 | 121 | 0.012156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2475-3_0_3_line_26 |  | 22 | 63 | 0.012199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2475-3_0_3_line_27 |  | 23 | 57 | 0.013122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2475-3_0_3_line_28 |  | 24 | 25 | 0.03846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2475-3_0_3_line_29 |  | 25 | 26 | 0.014331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2475-3_0_3_line_30 |  | 26 | 27 | 0.02041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2475-3_0_3_line_31 |  | 26 | 28 | 0.026433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2475-3_0_3_line_32 |  | 28 | 29 | 0.017521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2475-3_0_3_line_33 |  | 30 | 31 | 0.0024129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2475-3_0_3_line_34 |  | 30 | 32 | 0.00036228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2475-3_0_3_line_35 |  | 31 | 33 | 0.00047814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2475-3_0_3_line_36 |  | 32 | 34 | 0.016329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2475-3_0_3_line_37 |  | 33 | 35 | 0.0044482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2475-3_0_3_line_38 |  | 34 | 36 | 0.016808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2475-3_0_3_line_39 |  | 35 | 37 | 0.028223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2475-3_0_3_line_40 |  | 36 | 38 | 0.007712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2475-3_0_3_line_41 |  | 37 | 58 | 0.011414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2475-3_0_3_line_42 |  | 38 | 39 | 0.042267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2475-3_0_3_line_43 |  | 39 | 40 | 0.0096764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2475-3_0_3_line_44 |  | 39 | 41 | 0.021673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2475-3_0_3_line_45 |  | 40 | 70 | 0.035415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2475-3_0_3_line_46 |  | 41 | 66 | 0.021612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2475-3_0_3_line_47 |  | 42 | 43 | 0.036274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2475-3_0_3_line_48 |  | 43 | 44 | 0.093421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2475-3_0_3_line_49 |  | 44 | 45 | 0.0093591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2475-3_0_3_line_50 |  | 45 | 46 | 0.076242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2475-3_0_3_line_51 |  | 46 | 47 | 0.0048242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2475-3_0_3_line_52 |  | 46 | 48 | 0.023418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2475-3_0_3_line_53 |  | 47 | 53 | 0.062482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2475-3_0_3_line_54 |  | 48 | 49 | 0.025627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2475-3_0_3_line_55 |  | 48 | 50 | 0.023571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2475-3_0_3_line_56 |  | 49 | 51 | 0.021384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2475-3_0_3_line_57 |  | 51 | 52 | 0.0048511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2475-3_0_3_line_58 |  | 52 | 61 | 0.029067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_2475-3_0_3_line_59 |  | 53 | 108 | 0.018158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2475-3_0_3_line_60 |  | 53 | 95 | 0.11322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2475-3_0_3_line_61 |  | 54 | 55 | 0.021812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2475-3_0_3_line_62 |  | 54 | 56 | 0.0033097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2475-3_0_3_line_63 |  | 55 | 57 | 0.013391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2475-3_0_3_line_64 |  | 56 | 58 | 0.020997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2475-3_0_3_line_65 |  | 58 | 59 | 0.0403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2475-3_0_3_line_66 |  | 59 | 60 | 0.00094908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2475-3_0_3_line_67 |  | 60 | 76 | 0.0037202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2475-3_0_3_line_68 |  | 61 | 62 | 0.0014332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_2475-3_0_3_line_69 |  | 62 | 72 | 0.061797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_2475-3_0_3_line_70 |  | 64 | 65 | 0.0019832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2475-3_0_3_line_71 |  | 64 | 66 | 0.014763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2475-3_0_3_line_72 |  | 65 | 67 | 0.017114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2475-3_0_3_line_73 |  | 67 | 68 | 0.010791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2475-3_0_3_line_74 |  | 69 | 79 | 0.027062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2475-3_0_3_line_75 |  | 70 | 71 | 0.020964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2475-3_0_3_line_76 |  | 72 | 73 | 0.042269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2475-3_0_3_line_77 |  | 73 | 74 | 0.0057655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2475-3_0_3_line_78 |  | 74 | 75 | 0.024031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2475-3_0_3_line_79 |  | 75 | 76 | 0.029791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2475-3_0_3_line_80 |  | 77 | 78 | 0.038817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2475-3_0_3_line_81 |  | 78 | 113 | 0.015548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2475-3_0_3_line_82 |  | 79 | 80 | 0.033117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2475-3_0_3_line_83 |  | 80 | 81 | 0.035263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2475-3_0_3_line_84 |  | 81 | 82 | 0.0023654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2475-3_0_3_line_85 |  | 82 | 83 | 0.031396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2475-3_0_3_line_86 |  | 83 | 99 | 0.0041756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2475-3_0_3_line_87 |  | 84 | 85 | 0.027458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2475-3_0_3_line_88 |  | 84 | 86 | 0.04923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2475-3_0_3_line_89 |  | 85 | 87 | 0.012617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2475-3_0_3_line_90 |  | 86 | 88 | 0.018836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2475-3_0_3_line_91 |  | 87 | 91 | 0.012761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2475-3_0_3_line_92 |  | 88 | 92 | 0.031147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2475-3_0_3_line_93 |  | 89 | 90 | 0.013725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2475-3_0_3_line_94 |  | 90 | 114 | 0.01124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2475-3_0_3_line_95 |  | 91 | 93 | 0.031701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2475-3_0_3_line_96 |  | 91 | 94 | 0.013861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2475-3_0_3_line_97 |  | 92 | 95 | 0.016701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2475-3_0_3_line_98 |  | 93 | 125 | 0.021134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2475-3_0_3_line_99 |  | 94 | 107 | 0.046963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2475-3_0_3_line_100 |  | 95 | 124 | 0.023752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2475-3_0_3_line_101 |  | 96 | 97 | 0.020841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2475-3_0_3_line_102 |  | 96 | 98 | 0.028481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2475-3_0_3_line_103 |  | 97 | 108 | 0.019333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2475-3_0_3_line_104 |  | 98 | 114 | 0.033833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2475-3_0_3_line_105 |  | 99 | 100 | 0.02356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2475-3_0_3_line_106 |  | 99 | 101 | 0.016263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2475-3_0_3_line_107 |  | 101 | 126 | 0.01459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2475-3_0_3_line_108 |  | 102 | 103 | 0.036347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2475-3_0_3_line_109 |  | 102 | 104 | 0.034565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2475-3_0_3_line_110 |  | 103 | 105 | 0.05893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2475-3_0_3_line_111 |  | 104 | 106 | 0.060931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2475-3_0_3_line_112 |  | 105 | 107 | 0.017589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2475-3_0_3_line_113 |  | 106 | 109 | 0.027671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2475-3_0_3_line_114 |  | 109 | 112 | 0.007977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2475-3_0_3_line_115 |  | 110 | 111 | 0.0069692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2475-3_0_3_line_116 |  | 111 | 124 | 0.00077528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2475-3_0_3_line_117 |  | 112 | 122 | 0.001114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2475-3_0_3_line_118 |  | 113 | 125 | 0.030666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2475-3_0_3_line_119 |  | 115 | 116 | 0.0083833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2475-3_0_3_line_120 |  | 115 | 117 | 0.01473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2475-3_0_3_line_121 |  | 116 | 118 | 0.023648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2475-3_0_3_line_122 |  | 117 | 119 | 0.018522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2475-3_0_3_line_123 |  | 118 | 120 | 0.026094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2475-3_0_3_line_124 |  | 119 | 121 | 0.018255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2475-3_0_3_line_125 |  | 122 | 123 | 0.0040137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2475-3_0_3_trafo_53 | 0.63 MVA 20/0.4 kV | 127 | 72 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2615796.5074 | 1255213.7001 | 2615785.5345 | 1255229.7584
1 | 2615796.5074 | 1255213.7001 | 2615799.4243 | 1255209.4312 | 2615799.4243 | 1255209.4312
2 | 2615785.5345 | 1255229.7584 | 2615780.2529 | 1255237.4878 | 2615772.6085 | 1255252.5111
3 | 2615799.4243 | 1255209.4312 | 2615803.0855 | 1255206.5753
4 | 2615771.5344 | 1255254.622 | 2615772.6085 | 1255252.5111
5 | 2615824.8454 | 1255189.6011 | 2615803.0855 | 1255206.5753
6 | 2615771.5344 | 1255254.622 | 2615761.9111 | 1255273.5344
7 | 2615848.5587 | 1255171.1032 | 2615824.8454 | 1255189.6011
8 | 2615748.8706 | 1255299.1626 | 2615761.9111 | 1255273.5344
9 | 2615848.5587 | 1255171.1032 | 2615867.3104 | 1255154.3063
10 | 2615848.5587 | 1255171.1032 | 2615854.8076 | 1255178.1246 | 2615864.7382 | 1255187.5573 | 2615876.3332 | 1255195.0599 | 2615891.6483 | 1255203.0807
11 | 2616019.6981 | 1255292.8783 | 2616016.8493 | 1255302.5209
12 | 2616014.5358 | 1255310.3517 | 2616016.8493 | 1255302.5209
13 | 2616025.7477 | 1255272.4011 | 2616019.6981 | 1255292.8783
14 | 2616014.5358 | 1255310.3517 | 2616021.0415 | 1255314.3163 | 2616026.2664 | 1255324.4221
15 | 2616025.7477 | 1255272.4011 | 2615990.3851 | 1255254.6385 | 2615988.5467 | 1255253.6868
16 | 2616031.3866 | 1255262.2207 | 2616025.7477 | 1255272.4011
17 | 2615960.653 | 1255239.2471 | 2615988.5467 | 1255253.6868
18 | 2616031.3866 | 1255262.2207 | 2616044.2573 | 1255221.7174 | 2616047.9415 | 1255212.9458
19 | 2616001.5083 | 1255372.7914 | 2615981.7445 | 1255366.0919
20 | 2616001.5083 | 1255372.7914 | 2615999.7484 | 1255390.546
21 | 2615981.7445 | 1255366.0919 | 2615960.3423 | 1255358.837
22 | 2615999.7484 | 1255390.546 | 2616058.7687 | 1255399.6561
23 | 2615998.1561 | 1255406.6099 | 2615999.7484 | 1255390.546
24 | 2615956.4723 | 1255237.0828 | 2615960.653 | 1255239.2471
25 | 2615960.3423 | 1255358.837 | 2615948.8302 | 1255354.9346
26 | 2616065.7994 | 1255409.4422 | 2616062.2522 | 1255406.0997 | 2616058.7687 | 1255399.6561
27 | 2615996.8617 | 1255419.6678 | 2615998.1561 | 1255406.6099
28 | 2615922.4003 | 1255219.2431 | 2615941.5269 | 1255229.3461 | 2615956.4723 | 1255237.0828
29 | 2615909.7287 | 1255212.5497 | 2615922.4003 | 1255219.2431
30 | 2615909.7287 | 1255212.5497 | 2615891.6483 | 1255203.0807
31 | 2615909.7287 | 1255212.5497 | 2615897.3917 | 1255235.9276
32 | 2615887.0033 | 1255249.4468 | 2615892.0809 | 1255245.9914 | 2615897.3917 | 1255235.9276
33 | 2615966.2326 | 1255521.4923 | 2615966.9044 | 1255519.1748
34 | 2615966.1317 | 1255521.8403 | 2615966.2326 | 1255521.4923
35 | 2615966.9044 | 1255519.1748 | 2615967.0375 | 1255518.7155
36 | 2615961.5855 | 1255537.5238 | 2615966.1317 | 1255521.8403
37 | 2615967.0375 | 1255518.7155 | 2615968.2759 | 1255514.4432
38 | 2615956.906 | 1255553.6671 | 2615961.5855 | 1255537.5238
39 | 2615968.2759 | 1255514.4432 | 2615970.6115 | 1255506.3861 | 2615976.4548 | 1255487.4317
40 | 2615956.906 | 1255553.6671 | 2615956.0261 | 1255556.7026 | 2615953.8364 | 1255560.6928
41 | 2615979.8175 | 1255476.5243 | 2615976.4548 | 1255487.4317
42 | 2615933.5018 | 1255597.7473 | 2615953.8364 | 1255560.6928
43 | 2615933.5018 | 1255597.7473 | 2615929.4309 | 1255606.5256
44 | 2615933.5018 | 1255597.7473 | 2615920.5497 | 1255587.5947 | 2615916.1222 | 1255584.8371
45 | 2615929.4309 | 1255606.5256 | 2615914.5316 | 1255638.6535
46 | 2615916.1222 | 1255584.8371 | 2615905.6871 | 1255578.3376 | 2615897.1902 | 1255574.5124 | 2615897.1902 | 1255574.5124
47 | 2615561.3662 | 1255282.4296 | 2615556.7838 | 1255275.4685 | 2615556.1084 | 1255268.3842 | 2615562.2698 | 1255248.4934
48 | 2615653.7126 | 1255296.5592 | 2615561.3662 | 1255282.4296
49 | 2615653.7126 | 1255296.5592 | 2615653.7126 | 1255296.5592 | 2615662.7301 | 1255299.0649
50 | 2615726.682 | 1255340.5733 | 2615662.7301 | 1255299.0649
51 | 2615726.682 | 1255340.5733 | 2615724.4215 | 1255344.8352
52 | 2615737.655 | 1255319.8852 | 2615726.682 | 1255340.5733
53 | 2615703.3594 | 1255403.261 | 2615710.1777 | 1255374.6267 | 2615717.0907 | 1255358.6566 | 2615724.4215 | 1255344.8352
54 | 2615737.655 | 1255319.8852 | 2615762.058 | 1255327.7099
55 | 2615737.655 | 1255319.8852 | 2615743.4893 | 1255309.7383 | 2615748.8706 | 1255299.1626
56 | 2615762.058 | 1255327.7099 | 2615762.4097 | 1255327.8227 | 2615782.3216 | 1255334.5405
57 | 2615786.9181 | 1255336.0913 | 2615782.3216 | 1255334.5405
58 | 2615786.9181 | 1255336.0913 | 2615793.1689 | 1255338.2002 | 2615809.4288 | 1255347.0159 | 2615812.5611 | 1255349.4622
59 | 2615703.3594 | 1255403.261 | 2615713.3733 | 1255403.988 | 2615720.8898 | 1255407.0545
60 | 2615703.3594 | 1255403.261 | 2615632.5486 | 1255491.6074
61 | 2615987.4155 | 1255453.4356 | 2615994.2335 | 1255432.717
62 | 2615987.4155 | 1255453.4356 | 2615986.3809 | 1255456.5795
63 | 2615996.8617 | 1255419.6678 | 2615996.1435 | 1255426.913 | 2615994.2335 | 1255432.717
64 | 2615979.8175 | 1255476.5243 | 2615986.3809 | 1255456.5795
65 | 2615979.8175 | 1255476.5243 | 2615947.6613 | 1255452.2337
66 | 2615946.904 | 1255451.6616 | 2615947.6613 | 1255452.2337
67 | 2615946.904 | 1255451.6616 | 2615943.9356 | 1255449.4193
68 | 2615813.6906 | 1255350.3444 | 2615812.5611 | 1255349.4622
69 | 2615862.3946 | 1255388.3812 | 2615813.6906 | 1255350.3444
70 | 2615882.8476 | 1255571.0161 | 2615881.3846 | 1255569.6772
71 | 2615882.8476 | 1255571.0161 | 2615882.8476 | 1255571.0161 | 2615897.1902 | 1255574.5124
72 | 2615881.3846 | 1255569.6772 | 2615878.2056 | 1255566.7676 | 2615870.0554 | 1255556.8916
73 | 2615862.903 | 1255548.8458 | 2615864.6968 | 1255550.3984 | 2615870.0554 | 1255556.8916
74 | 2615885.2359 | 1255134.1007 | 2615885.0785 | 1255134.3985 | 2615871.2927 | 1255150.7392 | 2615867.3104 | 1255154.3063
75 | 2615905.7119 | 1255657.6719 | 2615914.5316 | 1255638.6535
76 | 2615896.2097 | 1255413.7412 | 2615866.456 | 1255391.553 | 2615862.3946 | 1255388.3812
77 | 2615896.2097 | 1255413.7412 | 2615900.8315 | 1255417.1878
78 | 2615900.8315 | 1255417.1878 | 2615920.0957 | 1255431.5535
79 | 2615920.0957 | 1255431.5535 | 2615934.8684 | 1255442.5699 | 2615943.9356 | 1255449.4193
80 | 2615729.3686 | 1255672.1753 | 2615735.2744 | 1255669.0778 | 2615755.4026 | 1255649.3291 | 2615758.0074 | 1255646.3606
81 | 2615729.3686 | 1255672.1753 | 2615722.4905 | 1255672.2238 | 2615717.3364 | 1255670.5535 | 2615714.5732 | 1255668.8395
82 | 2615900.0923 | 1255104.5077 | 2615890.6351 | 1255123.8842 | 2615885.2359 | 1255134.1007
83 | 2615900.0923 | 1255104.5077 | 2615932.8965 | 1255117.4452
84 | 2615932.8965 | 1255117.4452 | 2615935.097 | 1255118.3131
85 | 2615935.097 | 1255118.3131 | 2615964.3036 | 1255129.8317
86 | 2615968.188 | 1255131.3637 | 2615964.3036 | 1255129.8317
87 | 2615649.5501 | 1255607.5829 | 2615661.733 | 1255582.9755
88 | 2615680.8238 | 1255537.602 | 2615662.6919 | 1255581.0386 | 2615661.733 | 1255582.9755
89 | 2615649.5501 | 1255607.5829 | 2615646.6558 | 1255613.429 | 2615644.7053 | 1255619.2019
90 | 2615680.8238 | 1255537.602 | 2615667.2831 | 1255524.5088
91 | 2615640.6206 | 1255631.2917 | 2615644.7053 | 1255619.2019
92 | 2615644.8916 | 1255502.8573 | 2615667.2831 | 1255524.5088
93 | 2615799.1404 | 1255489.1608 | 2615788.5881 | 1255497.9374
94 | 2615799.1404 | 1255489.1608 | 2615791.6138 | 1255480.8125
95 | 2615640.6206 | 1255631.2917 | 2615656.6798 | 1255635.926 | 2615670.6174 | 1255641.433 | 2615670.6174 | 1255641.433
96 | 2615640.6206 | 1255631.2917 | 2615637.1538 | 1255644.7138
97 | 2615632.5486 | 1255491.6074 | 2615644.3314 | 1255502.3157 | 2615644.8916 | 1255502.8573
98 | 2615670.6174 | 1255641.433 | 2615688.5243 | 1255652.657
99 | 2615637.1538 | 1255644.7138 | 2615603.8211 | 1255611.6314
100 | 2615614.9712 | 1255475.633 | 2615632.5486 | 1255491.6074
101 | 2615735.6641 | 1255419.2991 | 2615736.1912 | 1255419.7811 | 2615747.2834 | 1255431.9074 | 2615749.7765 | 1255434.6318
102 | 2615768.9587 | 1255455.6841 | 2615763.4593 | 1255449.5842 | 2615749.7765 | 1255434.6318
103 | 2615735.6641 | 1255419.2991 | 2615723.3857 | 1255408.0727 | 2615720.8898 | 1255407.0545
104 | 2615791.6138 | 1255480.8125 | 2615768.9587 | 1255455.6841
105 | 2615989.9759 | 1255140.4838 | 2615968.188 | 1255131.3637
106 | 2615968.188 | 1255131.3637 | 2615961.3898 | 1255146.1377
107 | 2615955.2908 | 1255159.3921 | 2615961.3898 | 1255146.1377
108 | 2615515.3559 | 1255544.0137 | 2615535.6081 | 1255565.7172 | 2615539.5769 | 1255571.068
109 | 2615491.3235 | 1255519.1706 | 2615514.2041 | 1255542.7793 | 2615515.3559 | 1255544.0137
110 | 2615591.3368 | 1255599.2409 | 2615539.5769 | 1255571.068
111 | 2615527.9073 | 1255470.7672 | 2615511.5619 | 1255497.5646 | 2615491.3235 | 1255519.1706
112 | 2615591.3368 | 1255599.2409 | 2615603.8211 | 1255611.6314
113 | 2615527.9073 | 1255470.7672 | 2615545.3497 | 1255492.2488
114 | 2615550.3779 | 1255498.4414 | 2615545.3497 | 1255492.2488
115 | 2615609.24 | 1255470.4245 | 2615614.3975 | 1255475.1116
116 | 2615614.3975 | 1255475.1116 | 2615614.9712 | 1255475.633
117 | 2615551.0801 | 1255499.3062 | 2615550.3779 | 1255498.4414
118 | 2615714.5732 | 1255668.8395 | 2615692.2789 | 1255655.0103 | 2615688.5243 | 1255652.657
119 | 2615901.1309 | 1255336.3868 | 2615901.1309 | 1255336.3868 | 2615898.587 | 1255328.786 | 2615898.701 | 1255328.436
120 | 2615913.9997 | 1255343.1278 | 2615906.5876 | 1255340.6153 | 2615901.1309 | 1255336.3868
121 | 2615898.701 | 1255328.436 | 2615906.0277 | 1255305.9515
122 | 2615913.9997 | 1255343.1278 | 2615931.5411 | 1255349.074
123 | 2615913.5729 | 1255280.9721 | 2615906.2067 | 1255305.402 | 2615906.0277 | 1255305.9515
124 | 2615948.8302 | 1255354.9346 | 2615931.5411 | 1255349.074
125 | 2615553.6101 | 1255502.4221 | 2615551.0801 | 1255499.3062

## bus_geodata
| x | y | coords
0 | 2615796.5074 | 1255213.7001
1 | 2615785.5345 | 1255229.7584
2 | 2615799.4243 | 1255209.4312
3 | 2615772.6085 | 1255252.5111
4 | 2615803.0855 | 1255206.5753
5 | 2615771.5344 | 1255254.622
6 | 2615824.8454 | 1255189.6011
7 | 2615761.9111 | 1255273.5344
8 | 2615848.5587 | 1255171.1032
9 | 2616016.8493 | 1255302.5209
10 | 2616019.6981 | 1255292.8783
11 | 2616014.5358 | 1255310.3517
12 | 2616025.7477 | 1255272.4011
13 | 2616026.2664 | 1255324.4221
14 | 2615988.5467 | 1255253.6868
15 | 2616031.3866 | 1255262.2207
16 | 2616001.5083 | 1255372.7914
17 | 2615981.7445 | 1255366.0919
18 | 2615999.7484 | 1255390.546
19 | 2615960.653 | 1255239.2471
20 | 2616047.9415 | 1255212.9458
21 | 2615960.3423 | 1255358.837
22 | 2616058.7687 | 1255399.6561
23 | 2615998.1561 | 1255406.6099
24 | 2615956.4723 | 1255237.0828
25 | 2615922.4003 | 1255219.2431
26 | 2615909.7287 | 1255212.5497
27 | 2615891.6483 | 1255203.0807
28 | 2615897.3917 | 1255235.9276
29 | 2615887.0033 | 1255249.4468
30 | 2615966.2326 | 1255521.4923
31 | 2615966.9044 | 1255519.1748
32 | 2615966.1317 | 1255521.8403
33 | 2615967.0375 | 1255518.7155
34 | 2615961.5855 | 1255537.5238
35 | 2615968.2759 | 1255514.4432
36 | 2615956.906 | 1255553.6671
37 | 2615976.4548 | 1255487.4317
38 | 2615953.8364 | 1255560.6928
39 | 2615933.5018 | 1255597.7473
40 | 2615929.4309 | 1255606.5256
41 | 2615916.1222 | 1255584.8371
42 | 2615562.2698 | 1255248.4934
43 | 2615561.3662 | 1255282.4296
44 | 2615653.7126 | 1255296.5592
45 | 2615662.7301 | 1255299.0649
46 | 2615726.682 | 1255340.5733
47 | 2615724.4215 | 1255344.8352
48 | 2615737.655 | 1255319.8852
49 | 2615762.058 | 1255327.7099
50 | 2615748.8706 | 1255299.1626
51 | 2615782.3216 | 1255334.5405
52 | 2615786.9181 | 1255336.0913
53 | 2615703.3594 | 1255403.261
54 | 2615987.4155 | 1255453.4356
55 | 2615994.2335 | 1255432.717
56 | 2615986.3809 | 1255456.5795
57 | 2615996.8617 | 1255419.6678
58 | 2615979.8175 | 1255476.5243
59 | 2615947.6613 | 1255452.2337
60 | 2615946.904 | 1255451.6616
61 | 2615812.5611 | 1255349.4622
62 | 2615813.6906 | 1255350.3444
63 | 2616065.7994 | 1255409.4422
64 | 2615882.8476 | 1255571.0161
65 | 2615881.3846 | 1255569.6772
66 | 2615897.1902 | 1255574.5124
67 | 2615870.0554 | 1255556.8916
68 | 2615862.903 | 1255548.8458
69 | 2615867.3104 | 1255154.3063
70 | 2615914.5316 | 1255638.6535
71 | 2615905.7119 | 1255657.6719
72 | 2615862.3946 | 1255388.3812
73 | 2615896.2097 | 1255413.7412
74 | 2615900.8315 | 1255417.1878
75 | 2615920.0957 | 1255431.5535
76 | 2615943.9356 | 1255449.4193
77 | 2615758.0074 | 1255646.3606
78 | 2615729.3686 | 1255672.1753
79 | 2615885.2359 | 1255134.1007
80 | 2615900.0923 | 1255104.5077
81 | 2615932.8965 | 1255117.4452
82 | 2615935.097 | 1255118.3131
83 | 2615964.3036 | 1255129.8317
84 | 2615661.733 | 1255582.9755
85 | 2615649.5501 | 1255607.5829
86 | 2615680.8238 | 1255537.602
87 | 2615644.7053 | 1255619.2019
88 | 2615667.2831 | 1255524.5088
89 | 2615788.5881 | 1255497.9374
90 | 2615799.1404 | 1255489.1608
91 | 2615640.6206 | 1255631.2917
92 | 2615644.8916 | 1255502.8573
93 | 2615670.6174 | 1255641.433
94 | 2615637.1538 | 1255644.7138
95 | 2615632.5486 | 1255491.6074
96 | 2615749.7765 | 1255434.6318
97 | 2615735.6641 | 1255419.2991
98 | 2615768.9587 | 1255455.6841
99 | 2615968.188 | 1255131.3637
100 | 2615989.9759 | 1255140.4838
101 | 2615961.3898 | 1255146.1377
102 | 2615515.3559 | 1255544.0137
103 | 2615539.5769 | 1255571.068
104 | 2615491.3235 | 1255519.1706
105 | 2615591.3368 | 1255599.2409
106 | 2615527.9073 | 1255470.7672
107 | 2615603.8211 | 1255611.6314
108 | 2615720.8898 | 1255407.0545
109 | 2615545.3497 | 1255492.2488
110 | 2615609.24 | 1255470.4245
111 | 2615614.3975 | 1255475.1116
112 | 2615550.3779 | 1255498.4414
113 | 2615714.5732 | 1255668.8395
114 | 2615791.6138 | 1255480.8125
115 | 2615901.1309 | 1255336.3868
116 | 2615898.701 | 1255328.436
117 | 2615913.9997 | 1255343.1278
118 | 2615906.0277 | 1255305.9515
119 | 2615931.5411 | 1255349.074
120 | 2615913.5729 | 1255280.9721
121 | 2615948.8302 | 1255354.9346
122 | 2615551.0801 | 1255499.3062
123 | 2615553.6101 | 1255502.4221
124 | 2615614.9712 | 1255475.633
125 | 2615688.5243 | 1255652.657
126 | 2615955.2908 | 1255159.3921
127 | 2615737.655 | 1255319.8852

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98251 | -0.3349 | 0.0037184 | 0.00093192
1 | 0.98334 | -0.31864 | 0.0020511 | 0.00051406
2 | 0.9823 | -0.33889 | 0.00053604 | 0.00013434
3 | 0.98452 | -0.29578 | 0.0013393 | 0.00033567
4 | 0.98212 | -0.34242 | 0.0022079 | 0.00055336
5 | 0.98463 | -0.29366 | 0.0021476 | 0.00053823
6 | 0.9811 | -0.36234 | 0.0018044 | 0.00045223
7 | 0.98565 | -0.27388 | 0.0016343 | 0.0004096
8 | 0.98004 | -0.3831 | 0 | 0
9 | 0.97743 | -0.43429 | 0.00049465 | 0.00012397
10 | 0.97745 | -0.43396 | 0.0018292 | 0.00045845
11 | 0.97742 | -0.43449 | 0 | 0
12 | 0.97752 | -0.43254 | 0 | 0
13 | 0.9774 | -0.43494 | 0.0013147 | 0.0003295
14 | 0.97773 | -0.42844 | 0.0013723 | 0.00034394
15 | 0.9775 | -0.43291 | 0 | 0
16 | 0.98924 | -0.20682 | 0 | 0
17 | 0.989 | -0.21149 | 0.00066473 | 0.0001666
18 | 0.98945 | -0.20283 | 0.0015758 | 0.00039494
19 | 0.97793 | -0.42457 | 0.0022107 | 0.00055405
20 | 0.97742 | -0.43458 | 0.0017542 | 0.00043963
21 | 0.98876 | -0.21627 | 0.0013803 | 0.00034593
22 | 0.98936 | -0.20465 | 0.00042824 | 0.00010733
23 | 0.98968 | -0.19828 | 0.00055458 | 0.00013899
24 | 0.97797 | -0.4238 | 0.0011221 | 0.00028121
25 | 0.97833 | -0.41672 | 0.0028266 | 0.00070841
26 | 0.9785 | -0.41334 | 0.00099003 | 0.00024813
27 | 0.97888 | -0.40582 | 0.0028025 | 0.00070236
28 | 0.97834 | -0.41639 | 0.0029056 | 0.00072822
29 | 0.97829 | -0.41749 | 0.0034338 | 0.0008606
30 | 0.98974 | -0.19719 | 0.0019613 | 0.00049154
31 | 0.98979 | -0.19621 | 0.002681 | 0.00067192
32 | 0.98973 | -0.19733 | 0.00090889 | 0.00022779
33 | 0.9898 | -0.196 | 0.0014972 | 0.00037523
34 | 0.98943 | -0.20312 | 0.00084912 | 0.00021281
35 | 0.98991 | -0.19386 | 0.0026028 | 0.00065232
36 | 0.98914 | -0.20883 | 0.0015894 | 0.00039833
37 | 0.99068 | -0.17902 | 0.0051314 | 0.001286
38 | 0.98902 | -0.21124 | 0.0018505 | 0.00046377
39 | 0.98841 | -0.22303 | 0 | 0
40 | 0.98837 | -0.22376 | 0.0019885 | 0.00049837
41 | 0.98818 | -0.22742 | 0.0023659 | 0.00059295
42 | 0.98625 | -0.26227 | 0.0018473 | 0.00046298
43 | 0.98631 | -0.26107 | 0 | 0
44 | 0.98647 | -0.25797 | 0.000712 | 0.00017844
45 | 0.98649 | -0.25754 | 0.0018094 | 0.00045349
46 | 0.98679 | -0.25157 | 0.0013924 | 0.00034897
47 | 0.98651 | -0.25699 | 0.0007191 | 0.00018022
48 | 0.98828 | -0.22291 | 0 | 0
49 | 0.99123 | -0.16635 | 0.0020508 | 0.00051398
50 | 0.98707 | -0.2463 | 0.002019 | 0.00050602
51 | 0.99373 | -0.11863 | 0.0018325 | 0.00045927
52 | 0.99431 | -0.10769 | 0.00098366 | 0.00024653
53 | 0.98291 | -0.32661 | 0 | 0
54 | 0.99051 | -0.18225 | 0.0020968 | 0.00052551
55 | 0.99011 | -0.18994 | 0.00089634 | 0.00022464
56 | 0.99058 | -0.18097 | 0.0021538 | 0.0005398
57 | 0.98988 | -0.19446 | 0.0025461 | 0.00063811
58 | 0.99104 | -0.17199 | 0 | 0
59 | 0.99321 | -0.13002 | 0.0022913 | 0.00057426
60 | 0.99327 | -0.129 | 0.0015496 | 0.00038837
61 | 0.99604 | -0.074714 | 0.0022271 | 0.00055817
62 | 0.99613 | -0.073063 | 0.0039978 | 0.0010019
63 | 0.98934 | -0.20493 | 0.0012822 | 0.00032134
64 | 0.98791 | -0.23277 | 0.0015585 | 0.0003906
65 | 0.9879 | -0.23297 | 0.0031868 | 0.00079869
66 | 0.98801 | -0.23089 | 0.001835 | 0.00045989
67 | 0.98786 | -0.23371 | 0.00093371 | 0.00023401
68 | 0.98785 | -0.23399 | 0.0014744 | 0.00036952
69 | 0.97969 | -0.38997 | 0.0029791 | 0.00074664
70 | 0.9883 | -0.22522 | 0.0015423 | 0.00038654
71 | 0.98828 | -0.2255 | 0.00075267 | 0.00018864
72 | 1 | 0 | -0.21218 | -0.053982
73 | 0.9972 | -0.053386 | 0.0011767 | 0.0002949
74 | 0.99683 | -0.060572 | 0.00094053 | 0.00023572
75 | 0.99528 | -0.090183 | 0.0040721 | 0.0010206
76 | 0.99348 | -0.12488 | 0.0034184 | 0.00085672
77 | 0.97338 | -0.51314 | 0.00052724 | 0.00013214
78 | 0.9734 | -0.51277 | 0 | 0
79 | 0.97939 | -0.39589 | 0.0017141 | 0.00042958
80 | 0.97907 | -0.40211 | 0 | 0
81 | 0.97874 | -0.40874 | 0.0013879 | 0.00034784
82 | 0.97872 | -0.40912 | 0.0026835 | 0.00067256
83 | 0.97853 | -0.4127 | 0.0025192 | 0.00063136
84 | 0.97474 | -0.48623 | 0.0026114 | 0.00065449
85 | 0.97417 | -0.49749 | 0.00051388 | 0.00012879
86 | 0.97589 | -0.4637 | 0 | 0
87 | 0.97392 | -0.50256 | 0.00028835 | 7.2266e-05
88 | 0.97633 | -0.4551 | 0.0021973 | 0.00055069
89 | 0.98198 | -0.34478 | 0.0016841 | 0.00042208
90 | 0.98201 | -0.34436 | 0 | 0
91 | 0.97366 | -0.50761 | 0 | 0
92 | 0.97712 | -0.43964 | 0.0059072 | 0.0014805
93 | 0.97354 | -0.50989 | 0.00064228 | 0.00016097
94 | 0.97343 | -0.51211 | 0 | 0
95 | 0.97763 | -0.42956 | 0.003501 | 0.00087743
96 | 0.98235 | -0.33764 | 0.0012075 | 0.00030263
97 | 0.98253 | -0.33415 | 0.0011609 | 0.00029094
98 | 0.98214 | -0.34179 | 0.0044367 | 0.0011119
99 | 0.97852 | -0.41298 | 0 | 0
100 | 0.9785 | -0.41327 | 0.0006703 | 0.00016799
101 | 0.97847 | -0.41389 | 0.00090869 | 0.00022774
102 | 0.97124 | -0.55545 | 0.0017291 | 0.00043335
103 | 0.9716 | -0.54822 | 0.0033958 | 0.00085107
104 | 0.97094 | -0.56121 | 0 | 0
105 | 0.97238 | -0.53283 | 0.0026925 | 0.00067479
106 | 0.97043 | -0.57139 | 0 | 0
107 | 0.97266 | -0.52737 | 0.0008008 | 0.0002007
108 | 0.98271 | -0.3305 | 0.0014225 | 0.00035651
109 | 0.9702 | -0.57601 | 0.0010891 | 0.00027294
110 | 0.97727 | -0.43662 | 0.0081616 | 0.0020455
111 | 0.97733 | -0.43558 | 0.0026797 | 0.0006716
112 | 0.97014 | -0.57718 | 0.0017468 | 0.00043778
113 | 0.97341 | -0.51262 | 0.0020646 | 0.00051744
114 | 0.98202 | -0.34402 | 0.0019503 | 0.00048879
115 | 0.98826 | -0.22589 | 0.0011876 | 0.00029765
116 | 0.98822 | -0.22673 | 0.0017937 | 0.00044956
117 | 0.98836 | -0.22409 | 0.00099252 | 0.00024875
118 | 0.98814 | -0.22835 | 0.0010022 | 0.00025117
119 | 0.98849 | -0.22151 | 0.0012634 | 0.00031663
120 | 0.98807 | -0.22968 | 0.0028423 | 0.00071234
121 | 0.98864 | -0.21855 | 0.0014175 | 0.00035525
122 | 0.97013 | -0.57731 | 0.001453 | 0.00036415
123 | 0.97011 | -0.57766 | 0.0047358 | 0.0011869
124 | 0.97733 | -0.43543 | 0.0027038 | 0.00067763
125 | 0.97348 | -0.51115 | 0.00066318 | 0.00016621
126 | 0.97844 | -0.41446 | 0.0021568 | 0.00054055
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.046492 | -0.011702 | 0.046528 | 0.011725 | 3.6179e-05 | 2.2908e-05 | 0.07043 | 0.07043 | 0.07043 | 0.98251 | -0.3349 | 0.98334 | -0.31864 | 19.349
1 | 0.042774 | 0.01077 | -0.042765 | -0.010765 | 8.1411e-06 | 5.1449e-06 | 0.064799 | 0.064799 | 0.064799 | 0.98251 | -0.3349 | 0.9823 | -0.33889 | 17.8019
2 | -0.048579 | -0.012239 | 0.048632 | 0.012273 | 5.3163e-05 | 3.3691e-05 | 0.073534 | 0.073534 | 0.073534 | 0.98334 | -0.31864 | 0.98452 | -0.29578 | 20.2017
3 | 0.042229 | 0.010631 | -0.042222 | -0.010626 | 7.1293e-06 | 4.504e-06 | 0.063987 | 0.063987 | 0.063987 | 0.9823 | -0.33889 | 0.98212 | -0.34242 | 17.5788
4 | -0.049972 | -0.012608 | 0.049977 | 0.012611 | 5.0706e-06 | 3.2151e-06 | 0.075558 | 0.075558 | 0.075558 | 0.98452 | -0.29578 | 0.98463 | -0.29366 | 20.7578
5 | 0.040014 | 0.010073 | -0.039976 | -0.010049 | 3.8058e-05 | 2.4008e-05 | 0.060642 | 0.060642 | 0.060642 | 0.98212 | -0.34242 | 0.9811 | -0.36234 | 16.6598
6 | -0.052124 | -0.01315 | 0.052174 | 0.013181 | 4.9416e-05 | 3.1356e-05 | 0.078804 | 0.078804 | 0.078804 | 0.98463 | -0.29366 | 0.98565 | -0.27388 | 21.6494
7 | 0.038172 | 0.0095964 | -0.038134 | -0.0095726 | 3.7815e-05 | 2.3822e-05 | 0.057905 | 0.057905 | 0.057905 | 0.9811 | -0.36234 | 0.98004 | -0.3831 | 15.908
8 | -0.053808 | -0.013591 | 0.053879 | 0.013636 | 7.1222e-05 | 4.5215e-05 | 0.081271 | 0.081271 | 0.081271 | 0.98565 | -0.27388 | 0.98707 | -0.2463 | 22.3272
9 | 0.015036 | 0.0037719 | -0.015031 | -0.0037691 | 4.9206e-06 | 2.8321e-06 | 0.02283 | 0.02283 | 0.02283 | 0.98004 | -0.3831 | 0.97969 | -0.38997 | 6.2721
10 | 0.023098 | 0.0058007 | -0.023073 | -0.0057854 | 2.5003e-05 | 1.532e-05 | 0.035075 | 0.035075 | 0.035075 | 0.98004 | -0.3831 | 0.97888 | -0.40582 | 9.636
11 | -0.0018094 | -0.00045316 | 0.0018095 | 0.00045305 | 2.8607e-08 | -1.0772e-07 | 0.0027545 | 0.0027545 | 0.0027545 | 0.97743 | -0.43429 | 0.97745 | -0.43396 | 0.75673
12 | 0.0013148 | 0.00032919 | -0.0013148 | -0.00032928 | 1.2266e-08 | -9.4492e-08 | 0.0020015 | 0.0020015 | 0.0020015 | 0.97743 | -0.43429 | 0.97742 | -0.43449 | 0.54986
13 | -0.0036387 | -0.0009115 | 0.0036389 | 0.00091139 | 2.4567e-07 | -1.1042e-07 | 0.0055392 | 0.0055391 | 0.0055392 | 0.97745 | -0.43396 | 0.97752 | -0.43254 | 1.5217
14 | 0.0013148 | 0.00032928 | -0.0013147 | -0.0003295 | 2.8537e-08 | -2.1981e-07 | 0.0020015 | 0.0020016 | 0.0020016 | 0.97742 | -0.43449 | 0.9774 | -0.43494 | 0.54989
15 | -0.0053933 | -0.0013503 | 0.0053943 | 0.0013505 | 1.0524e-06 | 1.5137e-07 | 0.0082093 | 0.0082091 | 0.0082093 | 0.97752 | -0.43254 | 0.97773 | -0.42844 | 2.2553
16 | 0.0017543 | 0.00043894 | -0.0017543 | -0.00043907 | 3.1099e-08 | -1.259e-07 | 0.0026702 | 0.0026703 | 0.0026703 | 0.97752 | -0.43254 | 0.9775 | -0.43291 | 0.73359
17 | -0.0067666 | -0.0016944 | 0.0067679 | 0.0016948 | 1.249e-06 | 4.0536e-07 | 0.010298 | 0.010298 | 0.010298 | 0.97773 | -0.42844 | 0.97793 | -0.42457 | 2.829
18 | 0.0017543 | 0.00043907 | -0.0017542 | -0.00043963 | 1.3909e-07 | -5.6295e-07 | 0.0026703 | 0.0026705 | 0.0026705 | 0.9775 | -0.43291 | 0.97742 | -0.43458 | 0.73366
19 | 0.012554 | 0.0031483 | -0.012552 | -0.0031467 | 2.7909e-06 | 1.5183e-06 | 0.018885 | 0.018885 | 0.018885 | 0.98924 | -0.20682 | 0.989 | -0.21149 | 5.1882
20 | -0.012554 | -0.0031483 | 0.012557 | 0.0031496 | 2.3861e-06 | 1.298e-06 | 0.018885 | 0.018885 | 0.018885 | 0.98924 | -0.20682 | 0.98945 | -0.20283 | 5.1881
21 | 0.011887 | 0.0029801 | -0.011884 | -0.0029787 | 2.7107e-06 | 1.4449e-06 | 0.017885 | 0.017885 | 0.017885 | 0.989 | -0.21149 | 0.98876 | -0.21627 | 4.9134
22 | 0.0017106 | 0.00042785 | -0.0017104 | -0.00042852 | 1.4818e-07 | -6.7212e-07 | 0.0025722 | 0.0025725 | 0.0025725 | 0.98945 | -0.20283 | 0.98936 | -0.20465 | 0.70672
23 | -0.015843 | -0.0039723 | 0.015847 | 0.0039743 | 3.4366e-06 | 1.9921e-06 | 0.023827 | 0.023827 | 0.023827 | 0.98945 | -0.20283 | 0.98968 | -0.19828 | 6.5458
24 | -0.0089786 | -0.0022489 | 0.0089789 | 0.002249 | 3.2948e-07 | 1.518e-07 | 0.013661 | 0.013661 | 0.013661 | 0.97793 | -0.42457 | 0.97797 | -0.4238 | 3.7531
25 | 0.010504 | 0.0026328 | -0.010503 | -0.0026322 | 1.1391e-06 | 5.7311e-07 | 0.015808 | 0.015808 | 0.015808 | 0.98876 | -0.21627 | 0.98864 | -0.21855 | 4.3428
26 | 0.0012822 | 0.0003212 | -0.0012822 | -0.00032134 | 1.7012e-08 | -1.4576e-07 | 0.0019284 | 0.0019284 | 0.0019284 | 0.98936 | -0.20465 | 0.98934 | -0.20493 | 0.52979
27 | -0.016401 | -0.0041133 | 0.016404 | 0.0041151 | 2.9925e-06 | 1.7465e-06 | 0.024661 | 0.02466 | 0.024661 | 0.98968 | -0.19828 | 0.98988 | -0.19446 | 6.7749
28 | -0.010101 | -0.0025303 | 0.010104 | 0.0025319 | 3.4065e-06 | 1.6974e-06 | 0.015369 | 0.015368 | 0.015369 | 0.97797 | -0.4238 | 0.97833 | -0.41672 | 4.2221
29 | -0.012931 | -0.0032404 | 0.012933 | 0.0032415 | 2.0788e-06 | 1.1504e-06 | 0.019668 | 0.019668 | 0.019668 | 0.97833 | -0.41672 | 0.9785 | -0.41334 | 5.4032
30 | -0.020264 | -0.0050786 | 0.020271 | 0.005083 | 7.2678e-06 | 4.3949e-06 | 0.030815 | 0.030815 | 0.030815 | 0.9785 | -0.41334 | 0.97888 | -0.40582 | 8.4657
31 | 0.0063406 | 0.001589 | -0.0063396 | -0.0015887 | 9.2158e-07 | 2.5783e-07 | 0.0096421 | 0.0096422 | 0.0096422 | 0.9785 | -0.41334 | 0.97834 | -0.41639 | 2.649
32 | 0.003434 | 0.00086049 | -0.0034338 | -0.0008606 | 1.7923e-07 | -1.0529e-07 | 0.0052229 | 0.005223 | 0.005223 | 0.97834 | -0.41639 | 0.97829 | -0.41749 | 1.4349
33 | -0.022824 | -0.0057275 | 0.022825 | 0.0057281 | 1.0656e-06 | 6.5095e-07 | 0.034317 | 0.034317 | 0.034317 | 0.98974 | -0.19719 | 0.98979 | -0.19621 | 9.4276
34 | 0.020862 | 0.0052359 | -0.020862 | -0.0052358 | 1.3367e-07 | 8.0894e-08 | 0.031368 | 0.031368 | 0.031368 | 0.98974 | -0.19719 | 0.98973 | -0.19733 | 8.6175
35 | -0.025506 | -0.0064 | 0.025506 | 0.0064002 | 2.6366e-07 | 1.626e-07 | 0.038347 | 0.038347 | 0.038347 | 0.98979 | -0.19621 | 0.9898 | -0.196 | 10.5349
36 | 0.019953 | 0.005008 | -0.019948 | -0.0050047 | 5.5116e-06 | 3.3176e-06 | 0.030001 | 0.030001 | 0.030001 | 0.98973 | -0.19733 | 0.98943 | -0.20312 | 8.2422
37 | -0.027003 | -0.0067754 | 0.027006 | 0.0067771 | 2.7493e-06 | 1.7024e-06 | 0.040598 | 0.040598 | 0.040598 | 0.9898 | -0.196 | 0.98991 | -0.19386 | 11.1532
38 | 0.019099 | 0.0047919 | -0.019093 | -0.0047888 | 5.2005e-06 | 3.1125e-06 | 0.028724 | 0.028725 | 0.028725 | 0.98943 | -0.20312 | 0.98914 | -0.20883 | 7.8914
39 | -0.029609 | -0.0074294 | 0.02963 | 0.0074425 | 2.0968e-05 | 1.3056e-05 | 0.04451 | 0.04451 | 0.04451 | 0.98991 | -0.19386 | 0.99068 | -0.17902 | 12.2281
40 | 0.017504 | 0.0043905 | -0.017502 | -0.0043893 | 2.0055e-06 | 1.1845e-06 | 0.026334 | 0.026334 | 0.026334 | 0.98914 | -0.20883 | 0.98902 | -0.21124 | 7.2345
41 | -0.034761 | -0.0087285 | 0.034773 | 0.0087358 | 1.1671e-05 | 7.3223e-06 | 0.052217 | 0.052217 | 0.052217 | 0.99068 | -0.17902 | 0.99104 | -0.17199 | 14.3455
42 | 0.015652 | 0.0039255 | -0.015643 | -0.0039204 | 8.7903e-06 | 5.0837e-06 | 0.023549 | 0.02355 | 0.02355 | 0.98902 | -0.21124 | 0.98841 | -0.22303 | 6.4697
43 | 0.0042838 | 0.0010729 | -0.0042837 | -0.0010729 | 1.5091e-07 | -2.7435e-08 | 0.0064489 | 0.0064489 | 0.0064489 | 0.98841 | -0.22303 | 0.98837 | -0.22376 | 1.7717
44 | 0.011359 | 0.0028475 | -0.011357 | -0.0028463 | 2.3768e-06 | 1.2434e-06 | 0.017101 | 0.017101 | 0.017101 | 0.98841 | -0.22303 | 0.98818 | -0.22742 | 4.698
45 | 0.0022952 | 0.00057457 | -0.002295 | -0.00057492 | 1.5855e-07 | -3.5236e-07 | 0.0034552 | 0.0034553 | 0.0034553 | 0.98837 | -0.22376 | 0.9883 | -0.22522 | 0.94927
46 | 0.0089907 | 0.0022533 | -0.0089892 | -0.0022527 | 1.4854e-06 | 6.7386e-07 | 0.013538 | 0.013538 | 0.013538 | 0.98818 | -0.22742 | 0.98801 | -0.23089 | 3.7193
47 | -0.0018473 | -0.00046298 | 0.0018474 | 0.00046259 | 1.0566e-07 | -3.9529e-07 | 0.0027872 | 0.002787 | 0.0027872 | 0.98625 | -0.26227 | 0.98631 | -0.26107 | 0.76571
48 | -0.0018474 | -0.00046259 | 0.0018477 | 0.00046157 | 2.7208e-07 | -1.0183e-06 | 0.002787 | 0.0027866 | 0.002787 | 0.98631 | -0.26107 | 0.98647 | -0.25797 | 0.76566
49 | -0.0025597 | -0.00064001 | 0.0025598 | 0.00063993 | 5.2308e-08 | -8.6009e-08 | 0.0038606 | 0.0038606 | 0.0038606 | 0.98647 | -0.25797 | 0.98649 | -0.25754 | 1.0606
50 | -0.0043692 | -0.0010934 | 0.0043704 | 0.0010932 | 1.2415e-06 | -1.7911e-07 | 0.0065899 | 0.0065896 | 0.0065899 | 0.98649 | -0.25754 | 0.98679 | -0.25157 | 1.8104
51 | 0.063313 | 0.0161 | -0.063296 | -0.016089 | 1.6518e-05 | 1.051e-05 | 0.095554 | 0.095554 | 0.095554 | 0.98679 | -0.25157 | 0.98651 | -0.25699 | 26.2512
52 | -0.069076 | -0.017542 | 0.069171 | 0.017603 | 9.5429e-05 | 6.0775e-05 | 0.10424 | 0.10424 | 0.10424 | 0.98679 | -0.25157 | 0.98828 | -0.22291 | 28.6383
53 | 0.062577 | 0.015909 | -0.062368 | -0.015776 | 0.00020911 | 0.00013304 | 0.09447 | 0.09447 | 0.09447 | 0.98651 | -0.25699 | 0.98291 | -0.32661 | 25.9533
54 | -0.12513 | -0.031785 | 0.12547 | 0.032003 | 0.00034168 | 0.00021834 | 0.18856 | 0.18856 | 0.18856 | 0.98828 | -0.22291 | 0.99123 | -0.16635 | 51.8016
55 | 0.055961 | 0.014182 | -0.055898 | -0.014142 | 6.2836e-05 | 3.9913e-05 | 0.084314 | 0.084315 | 0.084315 | 0.98828 | -0.22291 | 0.98707 | -0.2463 | 23.1633
56 | -0.12752 | -0.032517 | 0.12782 | 0.032705 | 0.00029449 | 0.0001882 | 0.19164 | 0.19164 | 0.19164 | 0.99123 | -0.16635 | 0.99373 | -0.11863 | 52.6473
57 | -0.12965 | -0.033164 | 0.12972 | 0.033208 | 6.8734e-05 | 4.3927e-05 | 0.19438 | 0.19438 | 0.19438 | 0.99373 | -0.11863 | 0.99431 | -0.10769 | 53.4012
58 | -0.1307 | -0.033455 | 0.13091 | 0.033588 | 0.00020906 | 0.00013304 | 0.19585 | 0.19585 | 0.19585 | 0.99431 | -0.10769 | 0.99604 | -0.074714 | 26.9028
59 | 0.01187 | 0.0029759 | -0.011867 | -0.0029747 | 2.1988e-06 | 1.1771e-06 | 0.01797 | 0.01797 | 0.01797 | 0.98291 | -0.32661 | 0.98271 | -0.3305 | 4.9367
60 | 0.050498 | 0.0128 | -0.05025 | -0.012642 | 0.00024848 | 0.0001576 | 0.0765 | 0.076501 | 0.076501 | 0.98291 | -0.32661 | 0.97763 | -0.42956 | 21.0167
61 | 0.019858 | 0.0049846 | -0.019851 | -0.0049803 | 7.2806e-06 | 4.3789e-06 | 0.029835 | 0.029835 | 0.029835 | 0.99051 | -0.18225 | 0.99011 | -0.18994 | 8.1964
62 | -0.021955 | -0.0055101 | 0.021956 | 0.005511 | 1.3504e-06 | 8.2163e-07 | 0.032985 | 0.032985 | 0.032985 | 0.99051 | -0.18225 | 0.99058 | -0.18097 | 9.0617
63 | 0.018954 | 0.0047556 | -0.01895 | -0.0047532 | 4.0753e-06 | 2.436e-06 | 0.028488 | 0.028488 | 0.028488 | 0.99011 | -0.18994 | 0.98988 | -0.19446 | 7.8263
64 | -0.02411 | -0.0060508 | 0.02412 | 0.0060571 | 1.033e-05 | 6.3406e-06 | 0.03622 | 0.03622 | 0.03622 | 0.99058 | -0.18097 | 0.99104 | -0.17199 | 9.9506
65 | -0.058893 | -0.014793 | 0.059011 | 0.014868 | 0.0001182 | 7.5125e-05 | 0.088437 | 0.088437 | 0.088437 | 0.99104 | -0.17199 | 0.99321 | -0.13002 | 24.296
66 | -0.061302 | -0.015442 | 0.061305 | 0.015444 | 3.0039e-06 | 1.9102e-06 | 0.09187 | 0.09187 | 0.09187 | 0.99321 | -0.13002 | 0.99327 | -0.129 | 25.239
67 | -0.062855 | -0.015833 | 0.062867 | 0.01584 | 1.2377e-05 | 7.8732e-06 | 0.094192 | 0.094192 | 0.094192 | 0.99327 | -0.129 | 0.99348 | -0.12488 | 25.8768
68 | -0.13314 | -0.034146 | 0.13315 | 0.034153 | 1.0661e-05 | 6.7856e-06 | 0.19918 | 0.19918 | 0.19918 | 0.99604 | -0.074714 | 0.99613 | -0.073063 | 27.3598
69 | -0.13715 | -0.035155 | 0.13764 | 0.035465 | 0.00048766 | 0.00031049 | 0.20515 | 0.20515 | 0.20515 | 0.99613 | -0.073063 | 1 | 0 | 28.1801
70 | 0.0055951 | 0.0014019 | -0.005595 | -0.0014019 | 5.2818e-08 | 8.4109e-09 | 0.0084274 | 0.0084274 | 0.0084274 | 0.98791 | -0.23277 | 0.9879 | -0.23297 | 2.3152
71 | -0.0071536 | -0.0017925 | 0.0071542 | 0.0017928 | 6.4271e-07 | 2.2229e-07 | 0.010775 | 0.010775 | 0.010775 | 0.98791 | -0.23277 | 0.98801 | -0.23089 | 2.9601
72 | 0.0024082 | 0.00060324 | -0.0024081 | -0.00060341 | 8.4442e-08 | -1.6507e-07 | 0.0036273 | 0.0036273 | 0.0036273 | 0.9879 | -0.23297 | 0.98786 | -0.23371 | 0.99652
73 | 0.0014744 | 0.0003694 | -0.0014744 | -0.00036952 | 1.996e-08 | -1.2538e-07 | 0.0022209 | 0.0022209 | 0.0022209 | 0.98786 | -0.23371 | 0.98785 | -0.23399 | 0.61015
74 | 0.012052 | 0.0030224 | -0.012048 | -0.0030206 | 3.4007e-06 | 1.8358e-06 | 0.018306 | 0.018306 | 0.018306 | 0.97969 | -0.38997 | 0.97939 | -0.39589 | 5.029
75 | 0.00075268 | 0.00018838 | -0.00075267 | -0.00018864 | 1.0096e-08 | -2.6217e-07 | 0.0011332 | 0.0011333 | 0.0011333 | 0.9883 | -0.22522 | 0.98828 | -0.2255 | 0.31134
76 | 0.072897 | 0.018517 | -0.07271 | -0.018398 | 0.0001868 | 0.000119 | 0.10856 | 0.10856 | 0.10856 | 1 | 0 | 0.9972 | -0.053386 | 29.8239
77 | 0.071533 | 0.018103 | -0.071509 | -0.018087 | 2.4662e-05 | 1.5709e-05 | 0.1068 | 0.1068 | 0.1068 | 0.9972 | -0.053386 | 0.99683 | -0.060572 | 29.3416
78 | 0.070568 | 0.017852 | -0.070468 | -0.017788 | 0.00010011 | 6.3757e-05 | 0.1054 | 0.1054 | 0.1054 | 0.99683 | -0.060572 | 0.99528 | -0.090183 | 28.9559
79 | 0.066396 | 0.016767 | -0.066286 | -0.016697 | 0.00011018 | 7.0132e-05 | 0.099311 | 0.099312 | 0.099312 | 0.99528 | -0.090183 | 0.99348 | -0.12488 | 27.2834
80 | -0.00052724 | -0.00013214 | 0.00052725 | 0.00013166 | 9.4543e-09 | -4.7645e-07 | 0.000806 | 0.00080583 | 0.000806 | 0.97338 | -0.51314 | 0.9734 | -0.51277 | 0.22143
81 | -0.00052725 | -0.00013166 | 0.00052726 | 0.00013147 | 3.7858e-09 | -1.9085e-07 | 0.00080583 | 0.00080576 | 0.00080583 | 0.9734 | -0.51277 | 0.97341 | -0.51262 | 0.22138
82 | 0.010334 | 0.002591 | -0.010331 | -0.0025895 | 3.0617e-06 | 1.5429e-06 | 0.015701 | 0.015702 | 0.015702 | 0.97939 | -0.39589 | 0.97907 | -0.40211 | 4.3136
83 | 0.010331 | 0.0025895 | -0.010328 | -0.0025878 | 3.2602e-06 | 1.6432e-06 | 0.015702 | 0.015702 | 0.015702 | 0.97907 | -0.40211 | 0.97874 | -0.40874 | 4.3137
84 | 0.00894 | 0.00224 | -0.0089398 | -0.0022399 | 1.6387e-07 | 7.5148e-08 | 0.013592 | 0.013592 | 0.013592 | 0.97874 | -0.40874 | 0.97872 | -0.40912 | 3.734
85 | 0.0062563 | 0.0015674 | -0.0062552 | -0.0015671 | 1.0652e-06 | 2.8725e-07 | 0.0095117 | 0.0095118 | 0.0095118 | 0.97872 | -0.40912 | 0.97853 | -0.4127 | 2.6131
86 | 0.0037361 | 0.00093571 | -0.003736 | -0.00093573 | 5.0537e-08 | -2.011e-08 | 0.0056811 | 0.0056811 | 0.0056811 | 0.97853 | -0.4127 | 0.97852 | -0.41298 | 1.5607
87 | 0.02241 | 0.0056368 | -0.022398 | -0.0056294 | 1.2056e-05 | 7.374e-06 | 0.034218 | 0.034218 | 0.034218 | 0.97474 | -0.48623 | 0.97417 | -0.49749 | 9.4006
88 | -0.025022 | -0.0062913 | 0.025049 | 0.0063079 | 2.6946e-05 | 1.6631e-05 | 0.038205 | 0.038204 | 0.038205 | 0.97474 | -0.48623 | 0.97589 | -0.4637 | 10.4958
89 | 0.021884 | 0.0055006 | -0.021879 | -0.0054974 | 5.2886e-06 | 3.2277e-06 | 0.033433 | 0.033433 | 0.033433 | 0.97417 | -0.49749 | 0.97392 | -0.50256 | 9.185
90 | -0.025049 | -0.0063079 | 0.025059 | 0.0063143 | 1.031e-05 | 6.3627e-06 | 0.038204 | 0.038204 | 0.038204 | 0.97589 | -0.4637 | 0.97633 | -0.4551 | 10.4957
91 | 0.021591 | 0.0054251 | -0.021585 | -0.005422 | 5.2091e-06 | 3.1751e-06 | 0.032993 | 0.032993 | 0.032993 | 0.97392 | -0.50256 | 0.97366 | -0.50761 | 9.064
92 | -0.027256 | -0.006865 | 0.027276 | 0.0068775 | 2.0168e-05 | 1.2518e-05 | 0.041553 | 0.041553 | 0.041553 | 0.97633 | -0.4551 | 0.97712 | -0.43964 | 11.4157
93 | -0.0016841 | -0.00042208 | 0.0016842 | 0.00042193 | 3.3519e-08 | -1.5219e-07 | 0.002552 | 0.0025519 | 0.002552 | 0.98198 | -0.34478 | 0.98201 | -0.34436 | 0.70109
94 | -0.0016842 | -0.00042193 | 0.0016842 | 0.0004218 | 2.745e-08 | -1.2464e-07 | 0.0025519 | 0.0025519 | 0.0025519 | 0.98201 | -0.34436 | 0.98202 | -0.34402 | 0.70108
95 | 0.0038981 | 0.00097556 | -0.0038977 | -0.00097569 | 4.2184e-07 | -1.2424e-07 | 0.0059569 | 0.005957 | 0.005957 | 0.97366 | -0.50761 | 0.97354 | -0.50989 | 1.6365
96 | 0.017687 | 0.0044464 | -0.017684 | -0.0044441 | 3.7994e-06 | 2.2592e-06 | 0.027036 | 0.027036 | 0.027036 | 0.97366 | -0.50761 | 0.97343 | -0.51211 | 7.4275
97 | -0.033184 | -0.008358 | 0.0332 | 0.008368 | 1.6003e-05 | 1.0032e-05 | 0.050549 | 0.050549 | 0.050549 | 0.97712 | -0.43964 | 0.97763 | -0.42956 | 13.8871
98 | 0.0032554 | 0.00081472 | -0.0032552 | -0.00081485 | 1.9618e-07 | -1.3721e-07 | 0.0049753 | 0.0049754 | 0.0049754 | 0.97354 | -0.50989 | 0.97348 | -0.51115 | 1.3669
99 | 0.017684 | 0.0044441 | -0.017671 | -0.0044365 | 1.2873e-05 | 7.6553e-06 | 0.027036 | 0.027036 | 0.027036 | 0.97343 | -0.51211 | 0.97266 | -0.52737 | 7.4276
100 | 0.013549 | 0.0033971 | -0.013546 | -0.0033949 | 3.7884e-06 | 2.1268e-06 | 0.020623 | 0.020624 | 0.020624 | 0.97763 | -0.42956 | 0.97733 | -0.43543 | 5.6658
101 | -0.0092807 | -0.0023256 | 0.0092822 | 0.0023264 | 1.5445e-06 | 7.2458e-07 | 0.014058 | 0.014058 | 0.014058 | 0.98235 | -0.33764 | 0.98253 | -0.33415 | 3.862
102 | 0.0080732 | 0.002023 | -0.0080716 | -0.0020224 | 1.5972e-06 | 6.617e-07 | 0.012229 | 0.012229 | 0.012229 | 0.98235 | -0.33764 | 0.98214 | -0.34179 | 3.3596
103 | -0.010443 | -0.0026173 | 0.010445 | 0.0026182 | 1.8135e-06 | 9.1572e-07 | 0.015816 | 0.015816 | 0.015816 | 0.98253 | -0.33415 | 0.98271 | -0.3305 | 4.345
104 | 0.0036349 | 0.00091041 | -0.0036345 | -0.00091059 | 3.8477e-07 | -1.8185e-07 | 0.0055069 | 0.005507 | 0.005507 | 0.98214 | -0.34179 | 0.98202 | -0.34402 | 1.5129
105 | 0.00067031 | 0.0001677 | -0.0006703 | -0.00016799 | 9.1788e-09 | -2.9008e-07 | 0.0010192 | 0.0010193 | 0.0010193 | 0.97852 | -0.41298 | 0.9785 | -0.41327 | 0.28003
106 | 0.0030657 | 0.00076803 | -0.0030656 | -0.00076815 | 1.3254e-07 | -1.1945e-07 | 0.0046619 | 0.0046619 | 0.0046619 | 0.97852 | -0.41298 | 0.97847 | -0.41389 | 1.2808
107 | 0.0021569 | 0.00054041 | -0.0021568 | -0.00054055 | 5.8866e-08 | -1.4558e-07 | 0.00328 | 0.0032801 | 0.0032801 | 0.97847 | -0.41389 | 0.97844 | -0.41446 | 0.90113
108 | -0.010763 | -0.0026995 | 0.010767 | 0.0027014 | 3.7066e-06 | 1.9222e-06 | 0.016491 | 0.016491 | 0.016491 | 0.97124 | -0.55545 | 0.9716 | -0.54822 | 4.5304
109 | 0.009034 | 0.0022661 | -0.0090315 | -0.002265 | 2.4834e-06 | 1.1618e-06 | 0.013842 | 0.013842 | 0.013842 | 0.97124 | -0.55545 | 0.97094 | -0.56121 | 3.8027
110 | -0.014163 | -0.0035525 | 0.014173 | 0.0035584 | 1.0398e-05 | 5.9241e-06 | 0.021691 | 0.021691 | 0.021691 | 0.9716 | -0.54822 | 0.97238 | -0.53283 | 5.9592
111 | 0.0090315 | 0.002265 | -0.0090272 | -0.0022629 | 4.3779e-06 | 2.0486e-06 | 0.013842 | 0.013842 | 0.013842 | 0.97094 | -0.56121 | 0.97043 | -0.57139 | 3.8028
112 | -0.016866 | -0.0042332 | 0.01687 | 0.0042358 | 4.3943e-06 | 2.5941e-06 | 0.025811 | 0.025811 | 0.025811 | 0.97238 | -0.53283 | 0.97266 | -0.52737 | 7.091
113 | 0.0090272 | 0.0022629 | -0.0090252 | -0.002262 | 1.9882e-06 | 9.3067e-07 | 0.013842 | 0.013842 | 0.013842 | 0.97043 | -0.57139 | 0.9702 | -0.57601 | 3.8028
114 | 0.0079361 | 0.001989 | -0.0079357 | -0.0019889 | 4.4319e-07 | 1.8514e-07 | 0.012172 | 0.012172 | 0.012172 | 0.9702 | -0.57601 | 0.97014 | -0.57718 | 3.3439
115 | -0.0081616 | -0.0020455 | 0.0081621 | 0.0020457 | 4.036e-07 | 1.7098e-07 | 0.012427 | 0.012427 | 0.012427 | 0.97727 | -0.43662 | 0.97733 | -0.43558 | 3.414
116 | -0.010842 | -0.0027173 | 0.010842 | 0.0027173 | 7.9219e-08 | 4.0985e-08 | 0.016507 | 0.016507 | 0.016507 | 0.97733 | -0.43558 | 0.97733 | -0.43543 | 4.5349
117 | 0.0061889 | 0.0015511 | -0.0061889 | -0.0015511 | 3.7643e-08 | 1.0337e-08 | 0.0094927 | 0.0094927 | 0.0094927 | 0.97014 | -0.57718 | 0.97013 | -0.57731 | 2.6079
118 | -0.0025919 | -0.00064891 | 0.002592 | 0.00064865 | 1.805e-07 | -2.6571e-07 | 0.0039619 | 0.0039617 | 0.0039619 | 0.97341 | -0.51262 | 0.97348 | -0.51115 | 1.0884
119 | 0.0056389 | 0.0014128 | -0.0056387 | -0.0014127 | 2.2662e-07 | 3.7622e-08 | 0.0084902 | 0.0084903 | 0.0084903 | 0.98826 | -0.22589 | 0.98822 | -0.22673 | 2.3325
120 | -0.0068265 | -0.0017104 | 0.0068271 | 0.0017106 | 5.8355e-07 | 1.8472e-07 | 0.010278 | 0.010278 | 0.010278 | 0.98826 | -0.22589 | 0.98836 | -0.22409 | 2.8238
121 | 0.0038449 | 0.00096318 | -0.0038446 | -0.00096329 | 2.9723e-07 | -1.1273e-07 | 0.0057893 | 0.0057895 | 0.0057895 | 0.98822 | -0.22673 | 0.98814 | -0.22835 | 1.5905
122 | -0.0078196 | -0.0019594 | 0.0078206 | 0.0019597 | 9.6264e-07 | 3.7869e-07 | 0.011773 | 0.011773 | 0.011773 | 0.98836 | -0.22409 | 0.98849 | -0.22151 | 3.2343
123 | 0.0028424 | 0.00071212 | -0.0028423 | -0.00071234 | 1.7928e-07 | -2.195e-07 | 0.0042803 | 0.0042804 | 0.0042804 | 0.98814 | -0.22835 | 0.98807 | -0.22968 | 1.1759
124 | -0.009084 | -0.0022764 | 0.0090852 | 0.0022769 | 1.2801e-06 | 5.8519e-07 | 0.013674 | 0.013674 | 0.013674 | 0.98849 | -0.22151 | 0.98864 | -0.21855 | 3.7567
125 | 0.0047359 | 0.0011869 | -0.0047358 | -0.0011869 | 7.9421e-08 | 1.272e-09 | 0.007264 | 0.0072641 | 0.0072641 | 0.97013 | -0.57731 | 0.97011 | -0.57766 | 1.9956

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.21396 | 0.054428

## res_load
| p_mw | q_mvar
0 | 0.0037184 | 0.00093192
1 | 0.0020511 | 0.00051406
2 | 0.00053604 | 0.00013434
3 | 0.0013393 | 0.00033567
4 | 0.0022079 | 0.00055336
5 | 0.0021476 | 0.00053823
6 | 0.0018044 | 0.00045223
7 | 0.0016343 | 0.0004096
8 | 0.00049465 | 0.00012397
9 | 0.0018292 | 0.00045845
10 | 0.0013147 | 0.0003295
11 | 0.0013723 | 0.00034394
12 | 0.00066473 | 0.0001666
13 | 0.0015758 | 0.00039494
14 | 0.0022107 | 0.00055405
15 | 0.0017542 | 0.00043963
16 | 0.0013803 | 0.00034593
17 | 0.00042824 | 0.00010733
18 | 0.00055458 | 0.00013899
19 | 0.0011221 | 0.00028121
20 | 0.0028266 | 0.00070841
21 | 0.00099003 | 0.00024813
22 | 0.0028025 | 0.00070236
23 | 0.0029056 | 0.00072822
24 | 0.0034338 | 0.0008606
25 | 0.0019613 | 0.00049154
26 | 0.002681 | 0.00067192
27 | 0.00090889 | 0.00022779
28 | 0.0014972 | 0.00037523
29 | 0.00084912 | 0.00021281
30 | 0.0026028 | 0.00065232
31 | 0.0015894 | 0.00039833
32 | 0.0051314 | 0.001286
33 | 0.0018505 | 0.00046377
34 | 0.0019885 | 0.00049837
35 | 0.0023659 | 0.00059295
36 | 0.0018473 | 0.00046298
37 | 0.000712 | 0.00017844
38 | 0.0018094 | 0.00045349
39 | 0.0013924 | 0.00034897
40 | 0.0007191 | 0.00018022
41 | 0.0020508 | 0.00051398
42 | 0.002019 | 0.00050602
43 | 0.0018325 | 0.00045927
44 | 0.00098366 | 0.00024653
45 | 0.0020968 | 0.00052551
46 | 0.00089634 | 0.00022464
47 | 0.0021538 | 0.0005398
48 | 0.0025461 | 0.00063811
49 | 0.0022913 | 0.00057426
50 | 0.0015496 | 0.00038837
51 | 0.0022271 | 0.00055817
52 | 0.0039978 | 0.0010019
53 | 0.0012822 | 0.00032134
54 | 0.0015585 | 0.0003906
55 | 0.0031868 | 0.00079869
56 | 0.001835 | 0.00045989
57 | 0.00093371 | 0.00023401
58 | 0.0014744 | 0.00036952
59 | 0.0029791 | 0.00074664
60 | 0.0015423 | 0.00038654
61 | 0.00075267 | 0.00018864
62 | 0.0017785 | 0.00044573
63 | 0.0011767 | 0.0002949
64 | 0.00094053 | 0.00023572
65 | 0.0040721 | 0.0010206
66 | 0.0034184 | 0.00085672
67 | 0.00052724 | 0.00013214
68 | 0.0017141 | 0.00042958
69 | 0.0013879 | 0.00034784
70 | 0.0026835 | 0.00067256
71 | 0.0025192 | 0.00063136
72 | 0.0026114 | 0.00065449
73 | 0.00051388 | 0.00012879
74 | 0.00028835 | 7.2266e-05
75 | 0.0021973 | 0.00055069
76 | 0.0016841 | 0.00042208
77 | 0.0059072 | 0.0014805
78 | 0.00064228 | 0.00016097
79 | 0.003501 | 0.00087743
80 | 0.0012075 | 0.00030263
81 | 0.0011609 | 0.00029094
82 | 0.0044367 | 0.0011119
83 | 0.0006703 | 0.00016799
84 | 0.00090869 | 0.00022774
85 | 0.0017291 | 0.00043335
86 | 0.0033958 | 0.00085107
87 | 0.0026925 | 0.00067479
88 | 0.0008008 | 0.0002007
89 | 0.0014225 | 0.00035651
90 | 0.0010891 | 0.00027294
91 | 0.0081616 | 0.0020455
92 | 0.0026797 | 0.0006716
93 | 0.0017468 | 0.00043778
94 | 0.0020646 | 0.00051744
95 | 0.0019503 | 0.00048879
96 | 0.0011876 | 0.00029765
97 | 0.0017937 | 0.00044956
98 | 0.00099252 | 0.00024875
99 | 0.0010022 | 0.00025117
100 | 0.0012634 | 0.00031663
101 | 0.0028423 | 0.00071234
102 | 0.0014175 | 0.00035525
103 | 0.001453 | 0.00036415
104 | 0.0047358 | 0.0011869
105 | 0.0027038 | 0.00067763
106 | 0.00066318 | 0.00016621
107 | 0.0021568 | 0.00054055

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1