## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2479-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2479-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2479-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2479-2_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2479-2_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2479-2_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2479-2_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2479-2_0_4_node_115 | 0.4 | n |  | TRUE
8 | bus_LV_2479-2_0_4_node_77 | 0.4 | n |  | TRUE
9 | bus_LV_2479-2_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2479-2_0_4_node_75 | 0.4 | n |  | TRUE
11 | bus_LV_2479-2_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2479-2_0_4_node_104 | 0.4 | n |  | TRUE
13 | bus_LV_2479-2_0_4_node_105 | 0.4 | n |  | TRUE
14 | bus_LV_2479-2_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2479-2_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2479-2_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2479-2_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2479-2_0_4_node_72 | 0.4 | n |  | TRUE
19 | bus_LV_2479-2_0_4_node_114 | 0.4 | n |  | TRUE
20 | bus_LV_2479-2_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_2479-2_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_2479-2_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_2479-2_0_4_node_45 | 0.4 | n |  | TRUE
24 | bus_LV_2479-2_0_4_node_46 | 0.4 | n |  | TRUE
25 | bus_LV_2479-2_0_4_node_47 | 0.4 | n |  | TRUE
26 | bus_LV_2479-2_0_4_node_44 | 0.4 | n |  | TRUE
27 | bus_LV_2479-2_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_2479-2_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_2479-2_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_2479-2_0_4_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_2479-2_0_4_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2479-2_0_4_node_81 | 0.4 | n |  | TRUE
33 | bus_LV_2479-2_0_4_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_2479-2_0_4_node_108 | 0.4 | n |  | TRUE
35 | bus_LV_2479-2_0_4_node_66 | 0.4 | n |  | TRUE
36 | bus_LV_2479-2_0_4_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_2479-2_0_4_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_2479-2_0_4_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_2479-2_0_4_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_2479-2_0_4_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_2479-2_0_4_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_2479-2_0_4_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_2479-2_0_4_node_119 | 0.4 | n |  | TRUE
44 | bus_LV_2479-2_0_4_node_131 | 0.4 | n |  | TRUE
45 | bus_LV_2479-2_0_4_node_140 | 0.4 | n |  | TRUE
46 | bus_LV_2479-2_0_4_node_120 | 0.4 | n |  | TRUE
47 | bus_LV_2479-2_0_4_node_130 | 0.4 | n |  | TRUE
48 | bus_LV_2479-2_0_4_node_141 | 0.4 | n |  | TRUE
49 | bus_LV_2479-2_0_4_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_2479-2_0_4_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_2479-2_0_4_node_30 | 0.4 | n |  | TRUE
52 | bus_LV_2479-2_0_4_node_31 | 0.4 | n |  | TRUE
53 | bus_LV_2479-2_0_4_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_2479-2_0_4_node_88 | 0.4 | n |  | TRUE
55 | bus_LV_2479-2_0_4_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_2479-2_0_4_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_2479-2_0_4_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_2479-2_0_4_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_2479-2_0_4_node_65 | 0.4 | n |  | TRUE
60 | bus_LV_2479-2_0_4_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_2479-2_0_4_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_2479-2_0_4_node_41 | 0.4 | n |  | TRUE
63 | bus_LV_2479-2_0_4_node_42 | 0.4 | n |  | TRUE
64 | bus_LV_2479-2_0_4_node_43 | 0.4 | n |  | TRUE
65 | bus_LV_2479-2_0_4_node_99 | 0.4 | n |  | TRUE
66 | bus_LV_2479-2_0_4_node_94 | 0.4 | n |  | TRUE
67 | bus_LV_2479-2_0_4_node_93 | 0.4 | n |  | TRUE
68 | bus_LV_2479-2_0_4_node_100 | 0.4 | n |  | TRUE
69 | bus_LV_2479-2_0_4_node_106 | 0.4 | n |  | TRUE
70 | bus_LV_2479-2_0_4_node_69 | 0.4 | n |  | TRUE
71 | bus_LV_2479-2_0_4_node_132 | 0.4 | n |  | TRUE
72 | bus_LV_2479-2_0_4_node_129 | 0.4 | n |  | TRUE
73 | bus_LV_2479-2_0_4_node_59 | 0.4 | n |  | TRUE
74 | bus_LV_2479-2_0_4_node_113 | 0.4 | n |  | TRUE
75 | bus_LV_2479-2_0_4_node_60 | 0.4 | n |  | TRUE
76 | bus_LV_2479-2_0_4_node_48 | 0.4 | n |  | TRUE
77 | bus_LV_2479-2_0_4_node_49 | 0.4 | n |  | TRUE
78 | bus_LV_2479-2_0_4_node_50 | 0.4 | n |  | TRUE
79 | bus_LV_2479-2_0_4_node_51 | 0.4 | n |  | TRUE
80 | bus_LV_2479-2_0_4_node_52 | 0.4 | n |  | TRUE
81 | bus_LV_2479-2_0_4_node_80 | 0.4 | n |  | TRUE
82 | bus_LV_2479-2_0_4_node_83 | 0.4 | n |  | TRUE
83 | bus_LV_2479-2_0_4_node_84 | 0.4 | n |  | TRUE
84 | bus_LV_2479-2_0_4_node_95 | 0.4 | n |  | TRUE
85 | bus_LV_2479-2_0_4_node_122 | 0.4 | n |  | TRUE
86 | bus_LV_2479-2_0_4_node_53 | 0.4 | n |  | TRUE
87 | bus_LV_2479-2_0_4_node_54 | 0.4 | n |  | TRUE
88 | bus_LV_2479-2_0_4_node_55 | 0.4 | n |  | TRUE
89 | bus_LV_2479-2_0_4_node_56 | 0.4 | n |  | TRUE
90 | bus_LV_2479-2_0_4_node_57 | 0.4 | n |  | TRUE
91 | bus_LV_2479-2_0_4_node_58 | 0.4 | n |  | TRUE
92 | bus_LV_2479-2_0_4_node_70 | 0.4 | n |  | TRUE
93 | bus_LV_2479-2_0_4_node_91 | 0.4 | n |  | TRUE
94 | bus_LV_2479-2_0_4_node_71 | 0.4 | n |  | TRUE
95 | bus_LV_2479-2_0_4_node_89 | 0.4 | n |  | TRUE
96 | bus_LV_2479-2_0_4_node_61 | 0.4 | n |  | TRUE
97 | bus_LV_2479-2_0_4_node_62 | 0.4 | n |  | TRUE
98 | bus_LV_2479-2_0_4_node_63 | 0.4 | n |  | TRUE
99 | bus_LV_2479-2_0_4_node_135 | 0.4 | n |  | TRUE
100 | bus_LV_2479-2_0_4_node_136 | 0.4 | n |  | TRUE
101 | bus_LV_2479-2_0_4_node_133 | 0.4 | n |  | TRUE
102 | bus_LV_2479-2_0_4_node_82 | 0.4 | n |  | TRUE
103 | bus_LV_2479-2_0_4_node_107 | 0.4 | n |  | TRUE
104 | bus_LV_2479-2_0_4_node_67 | 0.4 | n |  | TRUE
105 | bus_LV_2479-2_0_4_node_68 | 0.4 | n |  | TRUE
106 | bus_LV_2479-2_0_4_node_78 | 0.4 | n |  | TRUE
107 | bus_LV_2479-2_0_4_node_79 | 0.4 | n |  | TRUE
108 | bus_LV_2479-2_0_4_node_112 | 0.4 | n |  | TRUE
109 | bus_LV_2479-2_0_4_node_73 | 0.4 | n |  | TRUE
110 | bus_LV_2479-2_0_4_node_74 | 0.4 | n |  | TRUE
111 | bus_LV_2479-2_0_4_node_76 | 0.4 | n |  | TRUE
112 | bus_LV_2479-2_0_4_node_97 | 0.4 | n |  | TRUE
113 | bus_LV_2479-2_0_4_node_98 | 0.4 | n |  | TRUE
114 | bus_LV_2479-2_0_4_node_116 | 0.4 | n |  | TRUE
115 | bus_LV_2479-2_0_4_node_117 | 0.4 | n |  | TRUE
116 | bus_LV_2479-2_0_4_node_96 | 0.4 | n |  | TRUE
117 | bus_LV_2479-2_0_4_node_121 | 0.4 | n |  | TRUE
118 | bus_LV_2479-2_0_4_node_85 | 0.4 | n |  | TRUE
119 | bus_LV_2479-2_0_4_node_86 | 0.4 | n |  | TRUE
120 | bus_LV_2479-2_0_4_node_127 | 0.4 | n |  | TRUE
121 | bus_LV_2479-2_0_4_node_87 | 0.4 | n |  | TRUE
122 | bus_LV_2479-2_0_4_node_126 | 0.4 | n |  | TRUE
123 | bus_LV_2479-2_0_4_node_90 | 0.4 | n |  | TRUE
124 | bus_LV_2479-2_0_4_node_92 | 0.4 | n |  | TRUE
125 | bus_LV_2479-2_0_4_node_139 | 0.4 | n |  | TRUE
126 | bus_LV_2479-2_0_4_node_102 | 0.4 | n |  | TRUE
127 | bus_LV_2479-2_0_4_node_137 | 0.4 | n |  | TRUE
128 | bus_LV_2479-2_0_4_node_138 | 0.4 | n |  | TRUE
129 | bus_LV_2479-2_0_4_node_101 | 0.4 | n |  | TRUE
130 | bus_LV_2479-2_0_4_node_118 | 0.4 | n |  | TRUE
131 | bus_LV_2479-2_0_4_node_110 | 0.4 | n |  | TRUE
132 | bus_LV_2479-2_0_4_node_111 | 0.4 | n |  | TRUE
133 | bus_LV_2479-2_0_4_node_124 | 0.4 | n |  | TRUE
134 | bus_LV_2479-2_0_4_node_123 | 0.4 | n |  | TRUE
135 | bus_LV_2479-2_0_4_node_134 | 0.4 | n |  | TRUE
136 | bus_MV_288_0_node_31 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2479-2_0_4_load_0 | 0 | 0.00086371 | 0.00021647 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2479-2_0_4_load_1 | 1 | 0.0012617 | 0.00031622 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2479-2_0_4_load_3 | 3 | 0.0011631 | 0.00029151 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2479-2_0_4_load_4 | 4 | 0.0015045 | 0.00037706 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2479-2_0_4_load_5 | 5 | 0.0012988 | 0.00032552 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2479-2_0_4_load_6 | 6 | 0.0027812 | 0.00069702 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2479-2_0_4_load_115 | 7 | 0.001109 | 0.00027794 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2479-2_0_4_load_77 | 8 | 0.0010691 | 0.00026793 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2479-2_0_4_load_7 | 9 | 0.00088817 | 0.0002226 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2479-2_0_4_load_75 | 10 | 0.00097296 | 0.00024385 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2479-2_0_4_load_8 | 11 | 0.0023097 | 0.00057886 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2479-2_0_4_load_104 | 12 | 0.0020009 | 0.00050148 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2479-2_0_4_load_105 | 13 | 0.0015189 | 0.00038067 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2479-2_0_4_load_9 | 14 | 0.0012591 | 0.00031557 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2479-2_0_4_load_10 | 15 | 0.0012351 | 0.00030955 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2479-2_0_4_load_11 | 16 | 0.0010039 | 0.00025161 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2479-2_0_4_load_12 | 17 | 0.0010177 | 0.00025506 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2479-2_0_4_load_72 | 18 | 0.001734 | 0.00043459 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2479-2_0_4_load_114 | 19 | 0.0015798 | 0.00039594 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2479-2_0_4_load_13 | 20 | 0.0016869 | 0.00042277 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2479-2_0_4_load_14 | 21 | 0.001547 | 0.00038772 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2479-2_0_4_load_16 | 22 | 0.001548 | 0.00038798 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2479-2_0_4_load_47 | 25 | 0.0011149 | 0.00027943 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2479-2_0_4_load_44 | 26 | 0.0010502 | 0.00026319 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2479-2_0_4_load_17 | 27 | 0.0020913 | 0.00052414 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2479-2_0_4_load_18 | 28 | 0.00088572 | 0.00022198 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2479-2_0_4_load_19 | 29 | 0.0019137 | 0.00047963 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2479-2_0_4_load_20 | 30 | 0.0048697 | 0.0012205 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2479-2_0_4_load_21 | 31 | 0.0046049 | 0.0011541 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2479-2_0_4_load_81 | 32 | 0.0031495 | 0.00078933 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2479-2_0_4_load_108 | 34 | 0.0042379 | 0.0010621 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2479-2_0_4_load_34 | 36 | 0.0052926 | 0.0013264 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2479-2_0_4_load_22 | 37 | 0.0024842 | 0.0006226 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2479-2_0_4_load_23 | 38 | 0.00076394 | 0.00019146 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2479-2_0_4_load_25 | 40 | 0.0010721 | 0.0002687 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2479-2_0_4_load_119 | 43 | 0.001545 | 0.00038721 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2479-2_0_4_load_131 | 44 | 0.0024503 | 0.00061411 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2479-2_0_4_load_140 | 45 | 0.0059634 | 0.0014946 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2479-2_0_4_load_120 | 46 | 0.0021885 | 0.00054849 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2479-2_0_4_load_130 | 47 | 0.0032552 | 0.00081583 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2479-2_0_4_load_141 | 48 | 0.0031544 | 0.00079057 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2479-2_0_4_load_28 | 49 | 0.0019285 | 0.00048333 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2479-2_0_4_load_29 | 50 | 0.0021639 | 0.00054233 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2479-2_0_4_load_30 | 51 | 0.00072456 | 0.00018159 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2479-2_0_4_load_31 | 52 | 0.0028623 | 0.00071735 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2479-2_0_4_load_32 | 53 | 0.0015508 | 0.00038867 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2479-2_0_4_load_88 | 54 | 0.0047036 | 0.0011788 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2479-2_0_4_load_35 | 55 | 0.0049334 | 0.0012364 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2479-2_0_4_load_36 | 56 | 0.0049627 | 0.0012438 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2479-2_0_4_load_37 | 57 | 0.010128 | 0.0025384 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2479-2_0_4_load_38 | 58 | 0.0017131 | 0.00042933 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2479-2_0_4_load_65 | 59 | 0.0043466 | 0.0010894 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2479-2_0_4_load_39 | 60 | 0.0023717 | 0.0005944 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2479-2_0_4_load_40 | 61 | 0.00189 | 0.00047368 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2479-2_0_4_load_41 | 62 | 0.0022263 | 0.00055796 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2479-2_0_4_load_42 | 63 | 0.0035762 | 0.00089627 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2479-2_0_4_load_99 | 65 | 0.0018904 | 0.00047377 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2479-2_0_4_load_94 | 66 | 0.00195 | 0.00048872 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2479-2_0_4_load_93 | 67 | 0.002245 | 0.00056265 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2479-2_0_4_load_100 | 68 | 0.0018892 | 0.00047348 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2479-2_0_4_load_106 | 69 | 0.0021468 | 0.00053805 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2479-2_0_4_load_132 | 71 | 0.0020644 | 0.0005174 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2479-2_0_4_load_129 | 72 | 0.0011276 | 0.0002826 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2479-2_0_4_load_59 | 73 | 0.003042 | 0.0007624 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2479-2_0_4_load_113 | 74 | 0.0018999 | 0.00047615 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2479-2_0_4_load_60 | 75 | 0.00039575 | 9.9184e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2479-2_0_4_load_48 | 76 | 0.002348 | 0.00058847 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2479-2_0_4_load_49 | 77 | 0.0019366 | 0.00048535 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2479-2_0_4_load_50 | 78 | 0.0039018 | 0.00097789 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2479-2_0_4_load_51 | 79 | 0.0019281 | 0.00048323 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2479-2_0_4_load_80 | 81 | 0.002058 | 0.00051579 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2479-2_0_4_load_83 | 82 | 0.0011791 | 0.00029552 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2479-2_0_4_load_84 | 83 | 0.0015302 | 0.00038351 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2479-2_0_4_load_122 | 85 | 0.0011781 | 0.00029527 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2479-2_0_4_load_53 | 86 | 0.0018858 | 0.00047263 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2479-2_0_4_load_54 | 87 | 0.0028302 | 0.0007093 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2479-2_0_4_load_57 | 90 | 0.0037441 | 0.00093837 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2479-2_0_4_load_58 | 91 | 0.0018379 | 0.00046062 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2479-2_0_4_load_70 | 92 | 0.002056 | 0.00051529 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2479-2_0_4_load_71 | 94 | 0.0021037 | 0.00052725 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2479-2_0_4_load_89 | 95 | 0.0010725 | 0.0002688 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2479-2_0_4_load_61 | 96 | 0.015111 | 0.0037873 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2479-2_0_4_load_62 | 97 | 0.0025429 | 0.00063731 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2479-2_0_4_load_136 | 100 | 0.0024954 | 0.0006254 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2479-2_0_4_load_133 | 101 | 0.00041 | 0.00010276 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2479-2_0_4_load_82 | 102 | 0.0069842 | 0.0017504 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2479-2_0_4_load_107 | 103 | 0.0049055 | 0.0012294 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2479-2_0_4_load_67 | 104 | 0.0027263 | 0.00068327 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2479-2_0_4_load_68 | 105 | 0.0014011 | 0.00035114 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2479-2_0_4_load_78 | 106 | 0.0017296 | 0.00043348 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2479-2_0_4_load_79 | 107 | 0.0020844 | 0.00052239 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2479-2_0_4_load_112 | 108 | 0.0015774 | 0.00039533 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2479-2_0_4_load_73 | 109 | 0.0014877 | 0.00037285 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2479-2_0_4_load_74 | 110 | 0.0010194 | 0.00025548 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2479-2_0_4_load_76 | 111 | 0.0010164 | 0.00025475 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2479-2_0_4_load_98 | 113 | 0.0019779 | 0.00049572 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2479-2_0_4_load_116 | 114 | 0.0024348 | 0.00061021 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2479-2_0_4_load_117 | 115 | 0.0026885 | 0.00067381 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2479-2_0_4_load_96 | 116 | 0.0026601 | 0.00066668 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2479-2_0_4_load_121 | 117 | 0.0032472 | 0.00081382 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2479-2_0_4_load_85 | 118 | 0.0058241 | 0.0014596 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2479-2_0_4_load_87 | 121 | 0.0014673 | 0.00036775 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2479-2_0_4_load_126 | 122 | 0.0071658 | 0.0017959 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2479-2_0_4_load_90 | 123 | 0.0023817 | 0.0005969 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2479-2_0_4_load_92 | 124 | 0.0026087 | 0.0006538 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2479-2_0_4_load_139 | 125 | 0.0011315 | 0.00028359 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2479-2_0_4_load_102 | 126 | 0.0022124 | 0.00055447 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2479-2_0_4_load_137 | 127 | 0.0023338 | 0.00058491 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2479-2_0_4_load_138 | 128 | 0.0018965 | 0.00047531 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2479-2_0_4_load_101 | 129 | 0.0060239 | 0.0015097 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2479-2_0_4_load_118 | 130 | 0.0026608 | 0.00066686 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2479-2_0_4_load_110 | 131 | 0.0017495 | 0.00043846 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2479-2_0_4_load_111 | 132 | 0.0017786 | 0.00044576 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2479-2_0_4_load_124 | 133 | 0.0027926 | 0.0006999 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2479-2_0_4_load_123 | 134 | 0.0020801 | 0.00052133 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2479-2_0_4_load_134 | 135 | 0.0010164 | 0.00025474 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 129 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2479-2_0_4_line_0 |  | 0 | 1 | 0.020435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2479-2_0_4_line_1 |  | 0 | 2 | 0.010444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2479-2_0_4_line_2 |  | 1 | 3 | 0.00068966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2479-2_0_4_line_3 |  | 2 | 4 | 0.01742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2479-2_0_4_line_4 |  | 2 | 5 | 0.01508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2479-2_0_4_line_5 |  | 3 | 6 | 0.022532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2479-2_0_4_line_6 |  | 4 | 7 | 0.001957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2479-2_0_4_line_7 |  | 5 | 8 | 0.012247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2479-2_0_4_line_8 |  | 6 | 9 | 0.011037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2479-2_0_4_line_9 |  | 8 | 10 | 0.0040217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2479-2_0_4_line_10 |  | 9 | 11 | 0.017405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2479-2_0_4_line_11 |  | 10 | 109 | 0.006808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2479-2_0_4_line_12 |  | 11 | 12 | 0.029076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2479-2_0_4_line_13 |  | 12 | 13 | 0.021919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2479-2_0_4_line_14 |  | 13 | 89 | 0.0045803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2479-2_0_4_line_15 |  | 14 | 15 | 0.0053945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2479-2_0_4_line_16 |  | 14 | 16 | 0.022915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2479-2_0_4_line_17 |  | 16 | 17 | 0.025158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2479-2_0_4_line_18 |  | 17 | 18 | 0.003099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2479-2_0_4_line_19 |  | 18 | 19 | 0.014116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2479-2_0_4_line_20 |  | 19 | 108 | 0.022752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2479-2_0_4_line_21 |  | 20 | 21 | 0.018672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2479-2_0_4_line_22 |  | 21 | 22 | 0.027968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2479-2_0_4_line_23 |  | 22 | 23 | 0.043282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2479-2_0_4_line_24 |  | 23 | 24 | 0.04875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2479-2_0_4_line_25 |  | 23 | 25 | 0.016675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2479-2_0_4_line_26 |  | 23 | 26 | 0.03278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2479-2_0_4_line_27 |  | 24 | 71 | 0.019989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2479-2_0_4_line_28 |  | 24 | 72 | 0.016833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2479-2_0_4_line_29 |  | 25 | 73 | 0.03164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2479-2_0_4_line_30 |  | 27 | 28 | 0.022064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_2479-2_0_4_line_31 |  | 27 | 29 | 0.00084302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_2479-2_0_4_line_32 |  | 28 | 30 | 0.006487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_2479-2_0_4_line_33 |  | 29 | 31 | 0.019312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_2479-2_0_4_line_34 |  | 30 | 32 | 0.016721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2479-2_0_4_line_35 |  | 31 | 33 | 0.046553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_2479-2_0_4_line_36 |  | 32 | 34 | 0.076686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2479-2_0_4_line_37 |  | 32 | 35 | 0.01002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_2479-2_0_4_line_38 |  | 33 | 36 | 0.033963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_2479-2_0_4_line_39 |  | 34 | 103 | 0.021816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2479-2_0_4_line_40 |  | 35 | 102 | 0.02479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_2479-2_0_4_line_41 |  | 35 | 59 | 0.034068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2479-2_0_4_line_42 |  | 36 | 54 | 0.0054132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_2479-2_0_4_line_43 |  | 37 | 38 | 0.01365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_2479-2_0_4_line_44 |  | 37 | 39 | 0.049203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_2479-2_0_4_line_45 |  | 38 | 40 | 0.011079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_2479-2_0_4_line_46 |  | 39 | 41 | 0.036858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2479-2_0_4_line_47 |  | 39 | 42 | 0.041496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_2479-2_0_4_line_48 |  | 40 | 43 | 0.008261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_2479-2_0_4_line_49 |  | 41 | 44 | 0.016069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2479-2_0_4_line_50 |  | 42 | 45 | 0.026005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_2479-2_0_4_line_51 |  | 43 | 46 | 0.012344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_2479-2_0_4_line_52 |  | 44 | 47 | 0.020412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2479-2_0_4_line_53 |  | 45 | 48 | 0.026468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_2479-2_0_4_line_54 |  | 46 | 53 | 0.011893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_2479-2_0_4_line_55 |  | 47 | 72 | 0.010803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2479-2_0_4_line_56 |  | 48 | 97 | 0.11088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_2479-2_0_4_line_57 |  | 49 | 50 | 0.011495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_2479-2_0_4_line_58 |  | 49 | 51 | 0.015229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_2479-2_0_4_line_59 |  | 50 | 52 | 0.011524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_2479-2_0_4_line_60 |  | 51 | 53 | 0.0071528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_2479-2_0_4_line_61 |  | 52 | 54 | 0.021647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_2479-2_0_4_line_62 |  | 55 | 56 | 0.02457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2479-2_0_4_line_63 |  | 55 | 57 | 0.022313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2479-2_0_4_line_64 |  | 56 | 58 | 0.0086253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2479-2_0_4_line_65 |  | 58 | 59 | 0.013172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2479-2_0_4_line_66 |  | 60 | 61 | 0.009723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_2479-2_0_4_line_67 |  | 60 | 62 | 0.0065572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_2479-2_0_4_line_68 |  | 61 | 63 | 0.0010131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_2479-2_0_4_line_69 |  | 62 | 64 | 0.028328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_2479-2_0_4_line_70 |  | 63 | 65 | 0.003773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_2479-2_0_4_line_71 |  | 64 | 66 | 0.023874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2479-2_0_4_line_72 |  | 64 | 67 | 0.019273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_2479-2_0_4_line_73 |  | 65 | 68 | 0.00017118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_2479-2_0_4_line_74 |  | 66 | 69 | 0.0087721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2479-2_0_4_line_75 |  | 67 | 70 | 0.020083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_2479-2_0_4_line_76 |  | 68 | 129 | 0.027134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_2479-2_0_4_line_77 |  | 69 | 83 | 0.024459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2479-2_0_4_line_78 |  | 70 | 102 | 0.0020363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_2479-2_0_4_line_79 |  | 70 | 105 | 0.027218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2479-2_0_4_line_80 |  | 71 | 74 | 0.0088252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2479-2_0_4_line_81 |  | 73 | 75 | 0.004338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2479-2_0_4_line_82 |  | 74 | 132 | 0.028808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2479-2_0_4_line_83 |  | 75 | 96 | 0.029555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2479-2_0_4_line_84 |  | 76 | 77 | 0.017888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2479-2_0_4_line_85 |  | 76 | 78 | 0.016324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2479-2_0_4_line_86 |  | 77 | 79 | 0.023303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2479-2_0_4_line_87 |  | 78 | 80 | 0.036512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2479-2_0_4_line_88 |  | 79 | 81 | 0.002744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2479-2_0_4_line_89 |  | 80 | 82 | 0.014902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2479-2_0_4_line_90 |  | 80 | 83 | 0.0095861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2479-2_0_4_line_91 |  | 81 | 84 | 0.01215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2479-2_0_4_line_92 |  | 82 | 85 | 0.0067368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2479-2_0_4_line_93 |  | 84 | 116 | 0.00071194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2479-2_0_4_line_94 |  | 85 | 117 | 0.0031589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2479-2_0_4_line_95 |  | 86 | 87 | 0.010635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2479-2_0_4_line_96 |  | 86 | 88 | 0.027107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2479-2_0_4_line_97 |  | 87 | 89 | 0.016531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2479-2_0_4_line_98 |  | 88 | 90 | 0.018311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2479-2_0_4_line_99 |  | 88 | 91 | 0.015722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2479-2_0_4_line_100 |  | 90 | 92 | 0.021969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2479-2_0_4_line_101 |  | 91 | 93 | 0.0073613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2479-2_0_4_line_102 |  | 92 | 94 | 0.0075296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2479-2_0_4_line_103 |  | 93 | 95 | 0.053881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2479-2_0_4_line_104 |  | 94 | 106 | 0.015927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2479-2_0_4_line_105 |  | 95 | 123 | 0.046742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2479-2_0_4_line_106 |  | 97 | 98 | 0.047627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_2479-2_0_4_line_107 |  | 98 | 99 | 0.10952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
108 | LV_2479-2_0_4_line_108 |  | 99 | 100 | 0.055546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2479-2_0_4_line_109 |  | 99 | 101 | 0.030257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2479-2_0_4_line_110 |  | 100 | 121 | 0.071916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2479-2_0_4_line_111 |  | 101 | 135 | 0.0084148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2479-2_0_4_line_112 |  | 104 | 105 | 0.020339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2479-2_0_4_line_113 |  | 106 | 107 | 0.008762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2479-2_0_4_line_114 |  | 107 | 114 | 0.015788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2479-2_0_4_line_115 |  | 108 | 131 | 0.0026437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2479-2_0_4_line_116 |  | 109 | 110 | 0.0069034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2479-2_0_4_line_117 |  | 110 | 111 | 0.01405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2479-2_0_4_line_118 |  | 111 | 112 | 0.037166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2479-2_0_4_line_119 |  | 112 | 113 | 0.019971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2479-2_0_4_line_120 |  | 113 | 127 | 0.029594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2479-2_0_4_line_121 |  | 114 | 115 | 0.0020291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2479-2_0_4_line_122 |  | 115 | 133 | 0.020757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2479-2_0_4_line_123 |  | 116 | 126 | 0.020077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2479-2_0_4_line_124 |  | 117 | 134 | 0.023854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2479-2_0_4_line_125 |  | 118 | 119 | 0.017208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2479-2_0_4_line_126 |  | 118 | 120 | 0.31612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2479-2_0_4_line_127 |  | 119 | 121 | 0.025985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2479-2_0_4_line_128 |  | 120 | 122 | 0.02286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2479-2_0_4_line_129 |  | 123 | 124 | 0.054322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2479-2_0_4_line_130 |  | 124 | 125 | 0.020072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2479-2_0_4_line_131 |  | 127 | 128 | 0.02711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2479-2_0_4_line_132 |  | 129 | 130 | 0.037874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2479-2_0_4_line_133 |  | 131 | 132 | 0.018205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2479-2_0_4_line_134 |  | 133 | 134 | 0.0024193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2479-2_0_4_trafo_101 | 0.63 MVA 20/0.4 kV | 136 | 129 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2601105.0884 | 1259226.5365 | 2601120.1342 | 1259212.709
1 | 2601097.3985 | 1259233.6037 | 2601105.0884 | 1259226.5365
2 | 2601120.1342 | 1259212.709 | 2601120.642 | 1259212.2423
3 | 2601097.3985 | 1259233.6037 | 2601087.1747 | 1259219.4989
4 | 2601097.3985 | 1259233.6037 | 2601086.2944 | 1259243.8063
5 | 2601137.2318 | 1259196.9958 | 2601120.642 | 1259212.2423
6 | 2601087.1747 | 1259219.4989 | 2601086.0262 | 1259217.9143
7 | 2601077.2765 | 1259252.0922 | 2601086.2944 | 1259243.8063
8 | 2601137.2318 | 1259196.9958 | 2601145.358 | 1259189.5277
9 | 2601077.2765 | 1259252.0922 | 2601074.3151 | 1259254.8132
10 | 2601158.0228 | 1259177.5954 | 2601155.3983 | 1259180.3004 | 2601145.358 | 1259189.5277
11 | 2601074.3151 | 1259254.8132 | 2601069.3019 | 1259259.4195
12 | 2601158.0228 | 1259177.5954 | 2601178.2699 | 1259156.7278
13 | 2601178.2699 | 1259156.7278 | 2601191.003 | 1259143.6045 | 2601193.1383 | 1259140.6639
14 | 2601195.3985 | 1259136.7007 | 2601194.1996 | 1259139.2022 | 2601193.1383 | 1259140.6639
15 | 2601268.6608 | 1258854.268 | 2601274.0009 | 1258853.5036
16 | 2601245.9822 | 1258857.5431 | 2601246.5409 | 1258857.4341 | 2601268.6608 | 1258854.268
17 | 2601245.9822 | 1258857.5431 | 2601235.2643 | 1258859.6333 | 2601226.1886 | 1258862.5002 | 2601221.8332 | 1258864.3206
18 | 2601218.974 | 1258865.5158 | 2601221.8332 | 1258864.3206
19 | 2601218.974 | 1258865.5158 | 2601212.4692 | 1258868.2347 | 2601206.4012 | 1258871.8552
20 | 2601206.4012 | 1258871.8552 | 2601197.6035 | 1258877.1045 | 2601187.3095 | 1258884.2083
21 | 2601174.1381 | 1258830.6491 | 2601161.6566 | 1258839.2946 | 2601158.7737 | 1258841.2588
22 | 2601158.7737 | 1258841.2588 | 2601135.6606 | 1258857.0066
23 | 2601100.2106 | 1258881.8344 | 2601122.5998 | 1258865.9054 | 2601135.6606 | 1258857.0066
24 | 2601100.2106 | 1258881.8344 | 2601120.9008 | 1258926.001
25 | 2601100.2106 | 1258881.8344 | 2601090.9008 | 1258887.9035 | 2601086.305 | 1258891.036
26 | 2601100.2106 | 1258881.8344 | 2601098.8022 | 1258875.5966 | 2601087.9372 | 1258851.5525
27 | 2601120.9008 | 1258926.001 | 2601137.8641 | 1258915.4268
28 | 2601120.9008 | 1258926.001 | 2601128.1682 | 1258941.184
29 | 2601060.1605 | 1258908.8562 | 2601086.305 | 1258891.036
30 | 2601360.3747 | 1258947.9959 | 2601367.3148 | 1258968.94
31 | 2601360.3747 | 1258947.9959 | 2601360.1095 | 1258947.1957
32 | 2601369.3552 | 1258975.0978 | 2601367.3148 | 1258968.94
33 | 2601353.8145 | 1258928.9397 | 2601357.4604 | 1258939.201 | 2601360.1095 | 1258947.1957
34 | 2601375.6075 | 1258990.6052 | 2601369.5198 | 1258975.5947 | 2601369.3552 | 1258975.0978
35 | 2601340.053 | 1258885.1609 | 2601339.6597 | 1258891.7319 | 2601341.1731 | 1258899.3373 | 2601350.5227 | 1258919.6752 | 2601353.8145 | 1258928.9397
36 | 2601375.6075 | 1258990.6052 | 2601444.6567 | 1258957.2438
37 | 2601379.3734 | 1258999.891 | 2601375.6075 | 1258990.6052
38 | 2601340.053 | 1258885.1609 | 2601331.0227 | 1258887.0603 | 2601312.7801 | 1258903.7644
39 | 2601456.0127 | 1258975.8715 | 2601444.6567 | 1258957.2438 | 2601444.6567 | 1258957.2438
40 | 2601379.3734 | 1258999.891 | 2601357.9596 | 1259012.3802
41 | 2601379.3734 | 1258999.891 | 2601393.2358 | 1259028.1353 | 2601394.6119 | 1259030.3473
42 | 2601308.7878 | 1258907.4201 | 2601312.7801 | 1258903.7644
43 | 2601212.0633 | 1258983.0925 | 2601223.9561 | 1258976.3938
44 | 2601171.7025 | 1259010.1001 | 2601175.1028 | 1259004.8972 | 2601178.5027 | 1259001.9959 | 2601212.0633 | 1258983.0925
45 | 2601223.9561 | 1258976.3938 | 2601233.6093 | 1258970.9565
46 | 2601171.7025 | 1259010.1001 | 2601165.0023 | 1259007.7973 | 2601160.3598 | 1259005.1057 | 2601155.8008 | 1258998.9007 | 2601148.5828 | 1258983.8337
47 | 2601171.7025 | 1259010.1001 | 2601165.0023 | 1259007.7973 | 2601160.3598 | 1259005.1057 | 2601156.0701 | 1259010.0749 | 2601136.8101 | 1259021.6681
48 | 2601240.8071 | 1258966.9023 | 2601233.6093 | 1258970.9565
49 | 2601148.5828 | 1258983.8337 | 2601141.6451 | 1258969.3397
50 | 2601117.6503 | 1259021.5758 | 2601122.6536 | 1259029.8711 | 2601136.8101 | 1259021.6681
51 | 2601240.8071 | 1258966.9023 | 2601251.5625 | 1258960.8442
52 | 2601141.6451 | 1258969.3397 | 2601132.8321 | 1258950.9278
53 | 2601117.6503 | 1259021.5758 | 2601118.8591 | 1259048.016
54 | 2601261.7713 | 1258954.768 | 2601259.8022 | 1258956.2031 | 2601251.5625 | 1258960.8442
55 | 2601128.1682 | 1258941.184 | 2601132.8321 | 1258950.9278
56 | 2601118.8591 | 1259048.016 | 2601008.2467 | 1259055.6576
57 | 2601278.8518 | 1258940.38 | 2601280.2999 | 1258938.9957 | 2601286.1756 | 1258931.5414
58 | 2601267.5519 | 1258950.5552 | 2601270.3108 | 1258948.5445 | 2601278.8518 | 1258940.38
59 | 2601293.3097 | 1258922.4907 | 2601286.1756 | 1258931.5414
60 | 2601267.5519 | 1258950.5552 | 2601261.7713 | 1258954.768
61 | 2601308.7878 | 1258907.4201 | 2601295.8537 | 1258919.2634 | 2601293.3097 | 1258922.4907
62 | 2601406.1257 | 1259048.8552 | 2601415.2969 | 1259063.5974 | 2601420.0781 | 1259068.991
63 | 2601437.7009 | 1259082.304 | 2601430.7977 | 1259078.5999 | 2601425.7862 | 1259075.1298 | 2601420.7977 | 1259069.8028 | 2601420.0781 | 1259068.991
64 | 2601401.5696 | 1259041.5314 | 2601406.1257 | 1259048.8552
65 | 2601401.5696 | 1259041.5314 | 2601394.6119 | 1259030.3473
66 | 2601288.0787 | 1259062.4493 | 2601295.8668 | 1259056.6285
67 | 2601301.1192 | 1259052.703 | 2601295.8668 | 1259056.6285
68 | 2601288.0787 | 1259062.4493 | 2601287.2672 | 1259063.0558
69 | 2601323.7025 | 1259035.603 | 2601316.5032 | 1259041.2052 | 2601301.1192 | 1259052.703
70 | 2601284.245 | 1259065.3145 | 2601287.2672 | 1259063.0558
71 | 2601323.7025 | 1259035.603 | 2601338.0312 | 1259054.6992
72 | 2601323.7025 | 1259035.603 | 2601339.6171 | 1259024.7329
73 | 2601284.1079 | 1259065.417 | 2601284.245 | 1259065.3145
74 | 2601343.2959 | 1259061.7157 | 2601338.0312 | 1259054.6992
75 | 2601356.2006 | 1259013.4061 | 2601339.6171 | 1259024.7329
76 | 2601284.1079 | 1259065.417 | 2601278.1024 | 1259069.9054 | 2601262.4585 | 1259081.7736
77 | 2601343.2959 | 1259061.7157 | 2601357.9756 | 1259081.2798
78 | 2601356.2006 | 1259013.4061 | 2601357.9596 | 1259012.3802
79 | 2601356.2006 | 1259013.4061 | 2601354.0004 | 1259010.4147 | 2601333.8708 | 1258998.28 | 2601333.8708 | 1258998.28
80 | 2601137.8641 | 1258915.4268 | 2601145.3534 | 1258910.7584
81 | 2601060.1605 | 1258908.8562 | 2601056.5759 | 1258911.2995
82 | 2601145.3534 | 1258910.7584 | 2601165.4974 | 1258898.2015 | 2601169.7928 | 1258895.5065
83 | 2601032.1284 | 1258927.9073 | 2601037.8008 | 1258924.0967 | 2601056.5759 | 1258911.2995
84 | 2601398.1345 | 1259128.9025 | 2601399.8531 | 1259130.5945 | 2601411.43 | 1259140.865
85 | 2601398.1345 | 1259128.9025 | 2601387.9696 | 1259118.8951 | 2601386.5791 | 1259117.3759
86 | 2601411.43 | 1259140.865 | 2601421.5031 | 1259149.8012 | 2601428.7897 | 1259156.4102
87 | 2601363.729 | 1259088.9474 | 2601372.1985 | 1259099.7009 | 2601379.0025 | 1259109.0976 | 2601386.5791 | 1259117.3759
88 | 2601430.8222 | 1259158.2537 | 2601428.7897 | 1259156.4102
89 | 2601363.729 | 1259088.9474 | 2601351.4712 | 1259097.4225
90 | 2601363.729 | 1259088.9474 | 2601357.9756 | 1259081.2798
91 | 2601439.822 | 1259166.4166 | 2601430.8222 | 1259158.2537
92 | 2601351.4712 | 1259097.4225 | 2601345.9299 | 1259101.2538
93 | 2601440.3555 | 1259166.888 | 2601439.822 | 1259166.4166
94 | 2601343.3315 | 1259103.0503 | 2601345.9299 | 1259101.2538
95 | 2601212.6099 | 1259157.6916 | 2601206.1385 | 1259149.2517
96 | 2601229.1039 | 1259179.2025 | 2601212.6099 | 1259157.6916
97 | 2601195.3985 | 1259136.7007 | 2601200.0028 | 1259141.6049 | 2601206.0989 | 1259149.2001 | 2601206.1385 | 1259149.2517
98 | 2601229.1039 | 1259179.2025 | 2601244.3869 | 1259169.1168
99 | 2601229.1039 | 1259179.2025 | 2601238.2749 | 1259191.972
100 | 2601244.3869 | 1259169.1168 | 2601252.6002 | 1259163.6967 | 2601262.7729 | 1259157.0923
101 | 2601242.569 | 1259197.9511 | 2601238.2749 | 1259191.972
102 | 2601269.0883 | 1259152.9922 | 2601262.7729 | 1259157.0923
103 | 2601242.569 | 1259197.9511 | 2601238.6257 | 1259205.0551 | 2601205.4567 | 1259236.5732
104 | 2601269.0883 | 1259152.9922 | 2601274.001 | 1259149.8028 | 2601282.6139 | 1259144.5856
105 | 2601171.5726 | 1259268.7707 | 2601205.4567 | 1259236.5732
106 | 2600970.1772 | 1259057.7981 | 2600995.4443 | 1259044.1595 | 2600998.8285 | 1259043.8598 | 2601000.954 | 1259044.5606 | 2601008.2467 | 1259055.6576
107 | 2600861.6953 | 1259042.7614 | 2600970.1772 | 1259057.7981
108 | 2600861.6953 | 1259042.7614 | 2600842.3981 | 1259055.801 | 2600815.6878 | 1259073.885
109 | 2600861.6953 | 1259042.7614 | 2600844.2309 | 1259018.0533
110 | 2600815.6878 | 1259073.885 | 2600778.002 | 1259099.4 | 2600756.5028 | 1259114.7297
111 | 2600839.3739 | 1259011.1817 | 2600844.2309 | 1259018.0533
112 | 2601315.8889 | 1259006.887 | 2601329.6649 | 1258998.5015 | 2601333.8708 | 1258998.28
113 | 2601290.1082 | 1259140.0461 | 2601282.6139 | 1259144.5856
114 | 2601290.1082 | 1259140.0461 | 2601299.1028 | 1259134.5977 | 2601303.366 | 1259131.4962
115 | 2601185.1337 | 1258885.7099 | 2601187.3095 | 1258884.2083
116 | 2601064.2185 | 1259264.0902 | 2601069.3019 | 1259259.4195
117 | 2601064.2185 | 1259264.0902 | 2601053.8725 | 1259273.5964
118 | 2601024.897 | 1259296.7007 | 2601026.299 | 1259296.0004 | 2601032.103 | 1259292.2989 | 2601037.5982 | 1259287.9969 | 2601044.503 | 1259282.2052 | 2601053.8725 | 1259273.5964
119 | 2601024.897 | 1259296.7007 | 2601028.6042 | 1259302.8054 | 2601032.5978 | 1259308.6878 | 2601037.0698 | 1259312.2527
120 | 2601060.0458 | 1259330.9052 | 2601037.2852 | 1259312.4244 | 2601037.0698 | 1259312.2527
121 | 2601305.0068 | 1259130.3025 | 2601303.366 | 1259131.4962
122 | 2601321.7916 | 1259118.0914 | 2601305.0068 | 1259130.3025
123 | 2601440.3555 | 1259166.888 | 2601455.4007 | 1259180.1815
124 | 2601343.3315 | 1259103.0503 | 2601325.9016 | 1259115.1013 | 2601323.748 | 1259116.6681
125 | 2600735.3455 | 1259129.8156 | 2600730.5976 | 1259124.4448 | 2600724.2464 | 1259116.6694
126 | 2600724.2464 | 1259116.6694 | 2600436.0152 | 1258986.8379
127 | 2600735.3455 | 1259129.8156 | 2600756.5028 | 1259114.7297
128 | 2600436.0152 | 1258986.8379 | 2600424.9276 | 1258966.8471
129 | 2601128.7889 | 1259278.2903 | 2601139.2906 | 1259268.5568 | 2601141.3107 | 1259267.7011 | 2601143.4362 | 1259267.4457 | 2601145.0263 | 1259268.0909 | 2601154.9358 | 1259277.5212 | 2601157.2797 | 1259278.1554 | 2601159.9628 | 1259278.2338 | 2601162.7366 | 1259277.1669 | 2601171.5726 | 1259268.7707
130 | 2601114.0677 | 1259291.9347 | 2601128.7889 | 1259278.2903
131 | 2601060.0458 | 1259330.9052 | 2601081.0916 | 1259347.9938
132 | 2601232.3072 | 1259104.6936 | 2601249.5017 | 1259091.6031 | 2601262.4585 | 1259081.7736
133 | 2601185.1337 | 1258885.7099 | 2601182.3984 | 1258887.5975 | 2601169.7928 | 1258895.5065
134 | 2601321.7916 | 1259118.0914 | 2601323.748 | 1259116.6681

## bus_geodata
| x | y | coords
0 | 2601105.0884 | 1259226.5365
1 | 2601120.1342 | 1259212.709
2 | 2601097.3985 | 1259233.6037
3 | 2601120.642 | 1259212.2423
4 | 2601087.1747 | 1259219.4989
5 | 2601086.2944 | 1259243.8063
6 | 2601137.2318 | 1259196.9958
7 | 2601086.0262 | 1259217.9143
8 | 2601077.2765 | 1259252.0922
9 | 2601145.358 | 1259189.5277
10 | 2601074.3151 | 1259254.8132
11 | 2601158.0228 | 1259177.5954
12 | 2601178.2699 | 1259156.7278
13 | 2601193.1383 | 1259140.6639
14 | 2601268.6608 | 1258854.268
15 | 2601274.0009 | 1258853.5036
16 | 2601245.9822 | 1258857.5431
17 | 2601221.8332 | 1258864.3206
18 | 2601218.974 | 1258865.5158
19 | 2601206.4012 | 1258871.8552
20 | 2601174.1381 | 1258830.6491
21 | 2601158.7737 | 1258841.2588
22 | 2601135.6606 | 1258857.0066
23 | 2601100.2106 | 1258881.8344
24 | 2601120.9008 | 1258926.001
25 | 2601086.305 | 1258891.036
26 | 2601087.9372 | 1258851.5525
27 | 2601360.3747 | 1258947.9959
28 | 2601367.3148 | 1258968.94
29 | 2601360.1095 | 1258947.1957
30 | 2601369.3552 | 1258975.0978
31 | 2601353.8145 | 1258928.9397
32 | 2601375.6075 | 1258990.6052
33 | 2601340.053 | 1258885.1609
34 | 2601444.6567 | 1258957.2438
35 | 2601379.3734 | 1258999.891
36 | 2601312.7801 | 1258903.7644
37 | 2601212.0633 | 1258983.0925
38 | 2601223.9561 | 1258976.3938
39 | 2601171.7025 | 1259010.1001
40 | 2601233.6093 | 1258970.9565
41 | 2601148.5828 | 1258983.8337
42 | 2601136.8101 | 1259021.6681
43 | 2601240.8071 | 1258966.9023
44 | 2601141.6451 | 1258969.3397
45 | 2601117.6503 | 1259021.5758
46 | 2601251.5625 | 1258960.8442
47 | 2601132.8321 | 1258950.9278
48 | 2601118.8591 | 1259048.016
49 | 2601278.8518 | 1258940.38
50 | 2601286.1756 | 1258931.5414
51 | 2601267.5519 | 1258950.5552
52 | 2601293.3097 | 1258922.4907
53 | 2601261.7713 | 1258954.768
54 | 2601308.7878 | 1258907.4201
55 | 2601420.0781 | 1259068.991
56 | 2601406.1257 | 1259048.8552
57 | 2601437.7009 | 1259082.304
58 | 2601401.5696 | 1259041.5314
59 | 2601394.6119 | 1259030.3473
60 | 2601295.8668 | 1259056.6285
61 | 2601288.0787 | 1259062.4493
62 | 2601301.1192 | 1259052.703
63 | 2601287.2672 | 1259063.0558
64 | 2601323.7025 | 1259035.603
65 | 2601284.245 | 1259065.3145
66 | 2601338.0312 | 1259054.6992
67 | 2601339.6172 | 1259024.7329
68 | 2601284.1079 | 1259065.417
69 | 2601343.2959 | 1259061.7157
70 | 2601356.2006 | 1259013.4061
71 | 2601137.8641 | 1258915.4268
72 | 2601128.1682 | 1258941.184
73 | 2601060.1605 | 1258908.8562
74 | 2601145.3534 | 1258910.7584
75 | 2601056.5759 | 1258911.2995
76 | 2601398.1345 | 1259128.9025
77 | 2601411.43 | 1259140.865
78 | 2601386.5791 | 1259117.3759
79 | 2601428.7897 | 1259156.4102
80 | 2601363.729 | 1259088.9474
81 | 2601430.8222 | 1259158.2537
82 | 2601351.4712 | 1259097.4225
83 | 2601357.9756 | 1259081.2798
84 | 2601439.822 | 1259166.4166
85 | 2601345.9299 | 1259101.2538
86 | 2601212.6099 | 1259157.6916
87 | 2601206.1385 | 1259149.2517
88 | 2601229.1039 | 1259179.2025
89 | 2601195.3985 | 1259136.7007
90 | 2601244.3869 | 1259169.1168
91 | 2601238.2749 | 1259191.972
92 | 2601262.7729 | 1259157.0923
93 | 2601242.569 | 1259197.9511
94 | 2601269.0883 | 1259152.9922
95 | 2601205.4567 | 1259236.5732
96 | 2601032.1284 | 1258927.9073
97 | 2601008.2467 | 1259055.6576
98 | 2600970.1772 | 1259057.7981
99 | 2600861.6953 | 1259042.7614
100 | 2600815.6878 | 1259073.885
101 | 2600844.2309 | 1259018.0533
102 | 2601357.9596 | 1259012.3802
103 | 2601456.0127 | 1258975.8715
104 | 2601315.8889 | 1259006.887
105 | 2601333.8708 | 1258998.28
106 | 2601282.6139 | 1259144.5856
107 | 2601290.1082 | 1259140.0461
108 | 2601187.3095 | 1258884.2083
109 | 2601069.3019 | 1259259.4195
110 | 2601064.2185 | 1259264.0902
111 | 2601053.8725 | 1259273.5964
112 | 2601024.897 | 1259296.7007
113 | 2601037.0698 | 1259312.2527
114 | 2601303.366 | 1259131.4962
115 | 2601305.0068 | 1259130.3025
116 | 2601440.3555 | 1259166.888
117 | 2601343.3315 | 1259103.0503
118 | 2600724.2464 | 1259116.6694
119 | 2600735.3455 | 1259129.8156
120 | 2600436.0152 | 1258986.8379
121 | 2600756.5028 | 1259114.7297
122 | 2600424.9276 | 1258966.8471
123 | 2601171.5726 | 1259268.7707
124 | 2601128.7889 | 1259278.2903
125 | 2601114.0677 | 1259291.9347
126 | 2601455.4007 | 1259180.1815
127 | 2601060.0458 | 1259330.9052
128 | 2601081.0916 | 1259347.9938
129 | 2601262.4585 | 1259081.7736
130 | 2601232.3072 | 1259104.6936
131 | 2601185.1337 | 1258885.7099
132 | 2601169.7928 | 1258895.5065
133 | 2601321.7916 | 1259118.0914
134 | 2601323.748 | 1259116.6681
135 | 2600839.3739 | 1259011.1817
136 | 2601323.7025 | 1259035.603

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9755 | -0.47269 | 0.00086371 | 0.00021647
1 | 0.97581 | -0.4665 | 0.0012617 | 0.00031622
2 | 0.97535 | -0.4757 | 0 | 0
3 | 0.97582 | -0.46627 | 0.0011631 | 0.00029151
4 | 0.9753 | -0.47653 | 0.0015045 | 0.00037706
5 | 0.97516 | -0.47931 | 0.0012988 | 0.00032552
6 | 0.97622 | -0.45845 | 0.0027812 | 0.00069702
7 | 0.9753 | -0.47657 | 0.001109 | 0.00027794
8 | 0.97503 | -0.48195 | 0.0010691 | 0.00026793
9 | 0.97645 | -0.45406 | 0.00088817 | 0.0002226
10 | 0.97499 | -0.48274 | 0.00097296 | 0.00024385
11 | 0.97681 | -0.44685 | 0.0023097 | 0.00057886
12 | 0.97749 | -0.4336 | 0.0020009 | 0.00050148
13 | 0.97804 | -0.42283 | 0.0015189 | 0.00038067
14 | 0.97418 | -0.49828 | 0.0012591 | 0.00031557
15 | 0.97417 | -0.4984 | 0.0012351 | 0.00030955
16 | 0.97423 | -0.49723 | 0.0010039 | 0.00025161
17 | 0.97431 | -0.49561 | 0.0010177 | 0.00025506
18 | 0.97433 | -0.49535 | 0.001734 | 0.00043459
19 | 0.97441 | -0.49373 | 0.0015798 | 0.00039594
20 | 0.97411 | -0.49969 | 0.0016869 | 0.00042277
21 | 0.97414 | -0.49911 | 0.001547 | 0.00038772
22 | 0.97422 | -0.49745 | 0.001548 | 0.00038798
23 | 0.97441 | -0.49365 | 0 | 0
24 | 0.97557 | -0.47085 | 0 | 0
25 | 0.97411 | -0.49967 | 0.0011149 | 0.00027943
26 | 0.97438 | -0.49428 | 0.0010502 | 0.00026319
27 | 0.98813 | -0.2264 | 0.0020913 | 0.00052414
28 | 0.98892 | -0.21129 | 0.00088572 | 0.00022198
29 | 0.9881 | -0.22697 | 0.0019137 | 0.00047963
30 | 0.98915 | -0.20681 | 0.0048697 | 0.0012205
31 | 0.98744 | -0.23976 | 0.0046049 | 0.0011541
32 | 0.98978 | -0.1948 | 0.0031495 | 0.00078933
33 | 0.9859 | -0.26939 | 0 | 0
34 | 0.98913 | -0.20729 | 0.0042379 | 0.0010621
35 | 0.99019 | -0.18688 | 0 | 0
36 | 0.98478 | -0.29106 | 0.0052926 | 0.0013264
37 | 0.9812 | -0.36075 | 0.0024842 | 0.0006226
38 | 0.98154 | -0.35401 | 0.00076394 | 0.00019146
39 | 0.97999 | -0.38434 | 0 | 0
40 | 0.98183 | -0.3485 | 0.0010721 | 0.0002687
41 | 0.9783 | -0.41733 | 0 | 0
42 | 0.9796 | -0.39189 | 0 | 0
43 | 0.98204 | -0.34433 | 0.001545 | 0.00038721
44 | 0.97756 | -0.43175 | 0.0024503 | 0.00061411
45 | 0.97936 | -0.39663 | 0.0059634 | 0.0014946
46 | 0.98237 | -0.338 | 0.0021885 | 0.00054849
47 | 0.97667 | -0.44919 | 0.0032552 | 0.00081583
48 | 0.97916 | -0.4005 | 0.0031544 | 0.00079057
49 | 0.98331 | -0.3197 | 0.0019285 | 0.00048333
50 | 0.98363 | -0.31338 | 0.0021639 | 0.00054233
51 | 0.98288 | -0.32791 | 0.00072456 | 0.00018159
52 | 0.98397 | -0.30689 | 0.0028623 | 0.00071735
53 | 0.98269 | -0.33174 | 0.0015508 | 0.00038867
54 | 0.98461 | -0.29435 | 0.0047036 | 0.0011788
55 | 0.98861 | -0.21747 | 0.0049334 | 0.0012364
56 | 0.98895 | -0.21087 | 0.0049627 | 0.0012438
57 | 0.98841 | -0.2215 | 0.010128 | 0.0025384
58 | 0.98911 | -0.2078 | 0.0017131 | 0.00042933
59 | 0.98937 | -0.2027 | 0.0043466 | 0.0010894
60 | 0.99644 | -0.067331 | 0.0023717 | 0.0005944
61 | 0.99725 | -0.052005 | 0.00189 | 0.00047368
62 | 0.9959 | -0.07759 | 0.0022263 | 0.00055796
63 | 0.99734 | -0.050398 | 0.0035762 | 0.00089627
64 | 0.99359 | -0.12167 | 0 | 0
65 | 0.99766 | -0.044338 | 0.0018904 | 0.00047377
66 | 0.99156 | -0.16063 | 0.00195 | 0.00048872
67 | 0.99257 | -0.14128 | 0.002245 | 0.00056265
68 | 0.99767 | -0.044062 | 0.0018892 | 0.00047348
69 | 0.99082 | -0.17468 | 0.0021468 | 0.00053805
70 | 0.99151 | -0.1615 | 0 | 0
71 | 0.97526 | -0.47704 | 0.0020644 | 0.0005174
72 | 0.97623 | -0.45779 | 0.0011276 | 0.0002826
73 | 0.97356 | -0.51046 | 0.003042 | 0.0007624
74 | 0.97513 | -0.47944 | 0.0018999 | 0.00047615
75 | 0.9735 | -0.5117 | 0.00039575 | 9.9184e-05
76 | 0.98729 | -0.2428 | 0.002348 | 0.00058847
77 | 0.98712 | -0.24625 | 0.0019366 | 0.00048535
78 | 0.98749 | -0.23896 | 0.0039018 | 0.00097789
79 | 0.98693 | -0.24995 | 0.0019281 | 0.00048323
80 | 0.98806 | -0.22784 | 0 | 0
81 | 0.98691 | -0.25029 | 0.002058 | 0.00051579
82 | 0.9871 | -0.24637 | 0.0011791 | 0.00029552
83 | 0.98883 | -0.21303 | 0.0015302 | 0.00038351
84 | 0.98685 | -0.25135 | 0 | 0
85 | 0.98667 | -0.25461 | 0.0011781 | 0.00029527
86 | 0.9789 | -0.40582 | 0.0018858 | 0.00047263
87 | 0.97859 | -0.41188 | 0.0028302 | 0.0007093
88 | 0.97974 | -0.38946 | 0 | 0
89 | 0.97816 | -0.42045 | 0 | 0
90 | 0.98046 | -0.37543 | 0.0037441 | 0.00093837
91 | 0.97961 | -0.39204 | 0.0018379 | 0.00046062
92 | 0.98139 | -0.35713 | 0.002056 | 0.00051529
93 | 0.97956 | -0.393 | 0 | 0
94 | 0.98173 | -0.35058 | 0.0021037 | 0.00052725
95 | 0.9792 | -0.40005 | 0.0010725 | 0.0002688
96 | 0.97308 | -0.51991 | 0.015111 | 0.0037873
97 | 0.97844 | -0.41459 | 0.0025429 | 0.00063731
98 | 0.97817 | -0.41991 | 0 | 0
99 | 0.97723 | -0.43828 | 0 | 0
100 | 0.97636 | -0.4555 | 0.0024954 | 0.0006254
101 | 0.97719 | -0.43907 | 0.00041 | 0.00010276
102 | 0.99141 | -0.1635 | 0.0069842 | 0.0017504
103 | 0.98904 | -0.2092 | 0.0049055 | 0.0012294
104 | 0.99136 | -0.16447 | 0.0027263 | 0.00068327
105 | 0.99141 | -0.16349 | 0.0014011 | 0.00035114
106 | 0.98247 | -0.33615 | 0.0017296 | 0.00043348
107 | 0.98289 | -0.32795 | 0.0020844 | 0.00052239
108 | 0.97458 | -0.49046 | 0.0015774 | 0.00039533
109 | 0.97493 | -0.48396 | 0.0014877 | 0.00037285
110 | 0.97487 | -0.485 | 0.0010194 | 0.00025548
111 | 0.97478 | -0.48687 | 0.0010164 | 0.00025475
112 | 0.97457 | -0.4911 | 0 | 0
113 | 0.97445 | -0.49338 | 0.0019779 | 0.00049572
114 | 0.98368 | -0.31259 | 0.0024348 | 0.00061021
115 | 0.98379 | -0.31053 | 0.0026885 | 0.00067381
116 | 0.98685 | -0.25141 | 0.0026601 | 0.00066668
117 | 0.98648 | -0.25841 | 0.0032472 | 0.00081382
118 | 0.97487 | -0.48484 | 0.0058241 | 0.0014596
119 | 0.97508 | -0.48073 | 0 | 0
120 | 0.97276 | -0.5265 | 0 | 0
121 | 0.97539 | -0.47454 | 0.0014673 | 0.00036775
122 | 0.9726 | -0.52952 | 0.0071658 | 0.0017959
123 | 0.97894 | -0.40526 | 0.0023817 | 0.0005969
124 | 0.97875 | -0.40896 | 0.0026087 | 0.0006538
125 | 0.97873 | -0.40937 | 0.0011315 | 0.00028359
126 | 0.98681 | -0.2522 | 0.0022124 | 0.00055447
127 | 0.97433 | -0.49568 | 0.0023338 | 0.00058491
128 | 0.97429 | -0.49662 | 0.0018965 | 0.00047531
129 | 1 | 0 | -0.28757 | -0.073375
130 | 0.99991 | -0.001757 | 0.0026608 | 0.00066686
131 | 0.9746 | -0.49001 | 0.0017495 | 0.00043846
132 | 0.97479 | -0.48628 | 0.0017786 | 0.00044576
133 | 0.98493 | -0.28847 | 0.0027926 | 0.0006999
134 | 0.98506 | -0.28578 | 0.0020801 | 0.00052133
135 | 0.97719 | -0.43922 | 0.0010164 | 0.00025474
136 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.01656 | -0.004152 | 0.016565 | 0.0041549 | 4.8901e-06 | 2.8745e-06 | 0.025262 | 0.025262 | 0.025262 | 0.9755 | -0.47269 | 0.97581 | -0.4665 | 6.94
1 | 0.015697 | 0.0039356 | -0.015694 | -0.0039342 | 2.2455e-06 | 1.3067e-06 | 0.023944 | 0.023944 | 0.023944 | 0.9755 | -0.47269 | 0.97535 | -0.4757 | 6.5781
2 | -0.017827 | -0.0044711 | 0.017827 | 0.0044712 | 1.9114e-07 | 1.1371e-07 | 0.027186 | 0.027186 | 0.027186 | 0.97581 | -0.4665 | 0.97582 | -0.46627 | 7.4686
3 | 0.0026136 | 0.00065483 | -0.0026135 | -0.00065498 | 1.0386e-07 | -1.5093e-07 | 0.0039873 | 0.0039874 | 0.0039874 | 0.97535 | -0.4757 | 0.9753 | -0.47653 | 1.0954
4 | 0.013081 | 0.0032794 | -0.013079 | -0.0032782 | 2.2522e-06 | 1.2533e-06 | 0.019957 | 0.019957 | 0.019957 | 0.97535 | -0.4757 | 0.97516 | -0.47931 | 5.4827
5 | -0.01899 | -0.0047627 | 0.018997 | 0.004767 | 7.0859e-06 | 4.2534e-06 | 0.028959 | 0.028959 | 0.028959 | 0.97582 | -0.46627 | 0.97622 | -0.45845 | 7.9558
6 | 0.001109 | 0.00027792 | -0.001109 | -0.00027794 | 2.1009e-09 | -2.3077e-08 | 0.001692 | 0.001692 | 0.001692 | 0.9753 | -0.47653 | 0.9753 | -0.47657 | 0.46483
7 | 0.01178 | 0.0029527 | -0.011778 | -0.0029519 | 1.4838e-06 | 7.9689e-07 | 0.017975 | 0.017975 | 0.017975 | 0.97516 | -0.47931 | 0.97503 | -0.48195 | 4.9382
8 | -0.021779 | -0.005464 | 0.021783 | 0.0054668 | 4.5614e-06 | 2.7813e-06 | 0.033198 | 0.033198 | 0.033198 | 0.97622 | -0.45845 | 0.97645 | -0.45406 | 9.1204
9 | 0.010709 | 0.0026839 | -0.010709 | -0.0026837 | 4.0285e-07 | 2.0766e-07 | 0.016344 | 0.016344 | 0.016344 | 0.97503 | -0.48195 | 0.97499 | -0.48274 | 4.49
10 | -0.022671 | -0.0056894 | 0.022679 | 0.0056942 | 7.7921e-06 | 4.7691e-06 | 0.034552 | 0.034552 | 0.034552 | 0.97645 | -0.45406 | 0.97681 | -0.44685 | 9.4922
11 | 0.0097359 | 0.0024399 | -0.0097353 | -0.0024396 | 5.6366e-07 | 2.7584e-07 | 0.014859 | 0.014859 | 0.014859 | 0.97499 | -0.48274 | 0.97493 | -0.48396 | 4.0821
12 | -0.024989 | -0.006273 | 0.025005 | 0.0062828 | 1.5803e-05 | 9.7494e-06 | 0.03807 | 0.03807 | 0.03807 | 0.97681 | -0.44685 | 0.97749 | -0.4336 | 10.4588
13 | -0.027006 | -0.0067842 | 0.027019 | 0.0067929 | 1.3896e-05 | 8.6183e-06 | 0.041116 | 0.041116 | 0.041116 | 0.97749 | -0.4336 | 0.97804 | -0.42283 | 11.2956
14 | -0.028538 | -0.0071735 | 0.028542 | 0.0071756 | 3.2392e-06 | 2.0156e-06 | 0.043427 | 0.043427 | 0.043427 | 0.97804 | -0.42283 | 0.97816 | -0.42045 | 11.9304
15 | 0.0012351 | 0.00030949 | -0.0012351 | -0.00030955 | 7.2001e-09 | -6.2556e-08 | 0.0018866 | 0.0018866 | 0.0018866 | 0.97418 | -0.49828 | 0.97417 | -0.4984 | 0.5183
16 | -0.0024942 | -0.00062505 | 0.0024944 | 0.00062485 | 1.2472e-07 | -2.0549e-07 | 0.0038098 | 0.0038097 | 0.0038098 | 0.97418 | -0.49828 | 0.97423 | -0.49723 | 1.0467
17 | -0.0034983 | -0.00087645 | 0.0034986 | 0.00087631 | 2.6933e-07 | -1.4092e-07 | 0.0053431 | 0.005343 | 0.0053431 | 0.97423 | -0.49723 | 0.97431 | -0.49561 | 1.4679
18 | -0.0045162 | -0.0011314 | 0.0045163 | 0.0011314 | 5.5284e-08 | -3.2135e-09 | 0.0068972 | 0.0068972 | 0.0068972 | 0.97431 | -0.49561 | 0.97433 | -0.49535 | 1.8948
19 | -0.0062503 | -0.001566 | 0.0062508 | 0.0015661 | 4.8233e-07 | 1.3287e-07 | 0.0095455 | 0.0095454 | 0.0095455 | 0.97433 | -0.49535 | 0.97441 | -0.49373 | 2.6224
20 | -0.0078307 | -0.001962 | 0.0078319 | 0.0019625 | 1.22e-06 | 4.9734e-07 | 0.011958 | 0.011958 | 0.011958 | 0.97441 | -0.49373 | 0.97458 | -0.49046 | 3.2852
21 | -0.0016869 | -0.00042277 | 0.0016869 | 0.00042257 | 4.649e-08 | -2.0269e-07 | 0.0025768 | 0.0025767 | 0.0025768 | 0.97411 | -0.49969 | 0.97414 | -0.49911 | 0.70791
22 | -0.0032339 | -0.00081028 | 0.0032342 | 0.0008101 | 2.5592e-07 | -1.8443e-07 | 0.0049398 | 0.0049397 | 0.0049398 | 0.97414 | -0.49911 | 0.97422 | -0.49745 | 1.3571
23 | -0.0047822 | -0.0011981 | 0.0047831 | 0.0011981 | 8.6589e-07 | 1.5141e-08 | 0.0073042 | 0.007304 | 0.0073042 | 0.97422 | -0.49745 | 0.97441 | -0.49365 | 2.0066
24 | -0.025519 | -0.0064023 | 0.025547 | 0.0064194 | 2.7767e-05 | 1.7163e-05 | 0.038973 | 0.038973 | 0.038973 | 0.97441 | -0.49365 | 0.97557 | -0.47085 | 10.7068
25 | 0.019686 | 0.0049414 | -0.01968 | -0.0049379 | 5.6524e-06 | 3.4099e-06 | 0.030065 | 0.030065 | 0.030065 | 0.97441 | -0.49365 | 0.97411 | -0.49967 | 8.2597
26 | 0.0010502 | 0.0002628 | -0.0010502 | -0.00026319 | 3.1612e-08 | -3.8808e-07 | 0.0016036 | 0.0016037 | 0.0016037 | 0.97441 | -0.49365 | 0.97438 | -0.49428 | 0.44058
27 | 0.016915 | 0.004243 | -0.01691 | -0.0042401 | 4.99e-06 | 2.9441e-06 | 0.025801 | 0.025801 | 0.025801 | 0.97557 | -0.47085 | 0.97526 | -0.47704 | 7.0882
28 | -0.042462 | -0.010662 | 0.042488 | 0.010679 | 2.6484e-05 | 1.6739e-05 | 0.064774 | 0.064773 | 0.064774 | 0.97557 | -0.47085 | 0.97623 | -0.45779 | 17.7949
29 | 0.018566 | 0.0046585 | -0.018556 | -0.0046528 | 9.5444e-06 | 5.7148e-06 | 0.028362 | 0.028362 | 0.028362 | 0.97411 | -0.49967 | 0.97356 | -0.51046 | 7.7918
30 | -0.11626 | -0.029527 | 0.11634 | 0.02958 | 8.4663e-05 | 5.3336e-05 | 0.17521 | 0.17521 | 0.17521 | 0.98813 | -0.2264 | 0.98892 | -0.21129 | 16.0445
31 | 0.11416 | 0.029003 | -0.11416 | -0.029001 | 3.1196e-06 | 1.9641e-06 | 0.17206 | 0.17206 | 0.17206 | 0.98813 | -0.2264 | 0.9881 | -0.22697 | 15.7561
32 | -0.11723 | -0.029802 | 0.11725 | 0.029818 | 2.5272e-05 | 1.5924e-05 | 0.17654 | 0.17654 | 0.17654 | 0.98892 | -0.21129 | 0.98915 | -0.20681 | 16.1666
33 | 0.11225 | 0.028521 | -0.11218 | -0.028478 | 6.9089e-05 | 4.3475e-05 | 0.16918 | 0.16918 | 0.16918 | 0.9881 | -0.22697 | 0.98744 | -0.23976 | 15.4923
34 | -0.12212 | -0.031039 | 0.12219 | 0.031083 | 7.0661e-05 | 4.4579e-05 | 0.18386 | 0.18386 | 0.18386 | 0.98915 | -0.20681 | 0.98978 | -0.1948 | 16.8374
35 | 0.10757 | 0.027324 | -0.10742 | -0.027227 | 0.00015316 | 9.6241e-05 | 0.16224 | 0.16224 | 0.16224 | 0.98744 | -0.23976 | 0.9859 | -0.26939 | 14.8568
36 | 0.0091492 | 0.002294 | -0.0091438 | -0.0022915 | 5.4412e-06 | 2.4974e-06 | 0.013755 | 0.013756 | 0.013756 | 0.98978 | -0.1948 | 0.98913 | -0.20729 | 3.779
37 | -0.13449 | -0.034167 | 0.13454 | 0.034199 | 5.1288e-05 | 3.2438e-05 | 0.20235 | 0.20235 | 0.20235 | 0.98978 | -0.1948 | 0.99019 | -0.18688 | 18.5306
38 | 0.10742 | 0.027227 | -0.10731 | -0.027157 | 0.00011174 | 7.0217e-05 | 0.16224 | 0.16224 | 0.16224 | 0.9859 | -0.26939 | 0.98478 | -0.29106 | 14.8569
39 | 0.0049059 | 0.0012294 | -0.0049055 | -0.0012294 | 4.4562e-07 | 5.1941e-09 | 0.0073803 | 0.0073804 | 0.0073804 | 0.98913 | -0.20729 | 0.98904 | -0.2092 | 2.0276
40 | -0.16066 | -0.040757 | 0.16084 | 0.040872 | 0.00018089 | 0.00011481 | 0.24161 | 0.24161 | 0.24161 | 0.99019 | -0.18688 | 0.99141 | -0.1635 | 22.1253
41 | 0.026119 | 0.0065581 | -0.026099 | -0.006546 | 1.9686e-05 | 1.2161e-05 | 0.039254 | 0.039255 | 0.039255 | 0.99019 | -0.18688 | 0.98937 | -0.2027 | 10.7842
42 | 0.10202 | 0.025831 | -0.102 | -0.025821 | 1.6098e-05 | 1.0096e-05 | 0.15424 | 0.15424 | 0.15424 | 0.98478 | -0.29106 | 0.98461 | -0.29435 | 14.1246
43 | -0.082211 | -0.020755 | 0.082237 | 0.020771 | 2.6544e-05 | 1.6471e-05 | 0.12473 | 0.12473 | 0.12473 | 0.9812 | -0.36075 | 0.98154 | -0.35401 | 11.4221
44 | 0.079726 | 0.020132 | -0.079636 | -0.020076 | 8.9991e-05 | 5.5732e-05 | 0.12096 | 0.12096 | 0.12096 | 0.9812 | -0.36075 | 0.97999 | -0.38434 | 11.0771
45 | -0.083001 | -0.020963 | 0.083023 | 0.020976 | 2.1947e-05 | 1.3626e-05 | 0.12589 | 0.12589 | 0.12589 | 0.98154 | -0.35401 | 0.98183 | -0.3485 | 11.5281
46 | 0.049491 | 0.012499 | -0.049412 | -0.012449 | 7.8123e-05 | 4.9535e-05 | 0.075181 | 0.075181 | 0.075181 | 0.97999 | -0.38434 | 0.9783 | -0.41733 | 20.6542
47 | 0.030146 | 0.0075774 | -0.030135 | -0.007572 | 1.0872e-05 | 5.39e-06 | 0.045781 | 0.045782 | 0.045782 | 0.97999 | -0.38434 | 0.9796 | -0.39189 | 4.1925
48 | -0.084095 | -0.021245 | 0.084112 | 0.021255 | 1.679e-05 | 1.0432e-05 | 0.12751 | 0.12751 | 0.12751 | 0.98183 | -0.3485 | 0.98204 | -0.34433 | 11.6769
49 | 0.049412 | 0.012449 | -0.049378 | -0.012428 | 3.4059e-05 | 2.1596e-05 | 0.075181 | 0.075181 | 0.075181 | 0.9783 | -0.41733 | 0.97756 | -0.43175 | 20.6542
50 | 0.030135 | 0.007572 | -0.030128 | -0.0075686 | 6.8133e-06 | 3.3786e-06 | 0.045782 | 0.045782 | 0.045782 | 0.9796 | -0.39189 | 0.97936 | -0.39663 | 4.1925
51 | -0.085657 | -0.021643 | 0.085683 | 0.021659 | 2.6018e-05 | 1.6183e-05 | 0.12985 | 0.12985 | 0.12985 | 0.98204 | -0.34433 | 0.98237 | -0.338 | 11.8913
52 | 0.046928 | 0.011814 | -0.046889 | -0.011789 | 3.9079e-05 | 2.4755e-05 | 0.071452 | 0.071452 | 0.071452 | 0.97756 | -0.43175 | 0.97667 | -0.44919 | 19.6296
53 | 0.024165 | 0.006074 | -0.02416 | -0.0060722 | 4.4614e-06 | 1.8564e-06 | 0.036722 | 0.036722 | 0.036722 | 0.97936 | -0.39663 | 0.97916 | -0.4005 | 3.3628
54 | -0.087871 | -0.022207 | 0.087898 | 0.022224 | 2.6364e-05 | 1.6421e-05 | 0.13317 | 0.13317 | 0.13317 | 0.98237 | -0.338 | 0.98269 | -0.33174 | 12.1948
55 | 0.043634 | 0.010973 | -0.043616 | -0.010962 | 1.791e-05 | 1.1327e-05 | 0.066492 | 0.066492 | 0.066492 | 0.97667 | -0.44919 | 0.97623 | -0.45779 | 18.2671
56 | 0.021006 | 0.0052816 | -0.020992 | -0.0052768 | 1.4129e-05 | 4.8619e-06 | 0.031928 | 0.03193 | 0.03193 | 0.97916 | -0.4005 | 0.97844 | -0.41459 | 2.924
57 | -0.092154 | -0.02331 | 0.092182 | 0.023327 | 2.7974e-05 | 1.7466e-05 | 0.13953 | 0.13953 | 0.13953 | 0.98331 | -0.3197 | 0.98363 | -0.31338 | 12.7775
58 | 0.090225 | 0.022826 | -0.090189 | -0.022804 | 3.5528e-05 | 2.2159e-05 | 0.13661 | 0.13661 | 0.13661 | 0.98331 | -0.3197 | 0.98288 | -0.32791 | 12.5103
59 | -0.094345 | -0.023869 | 0.094375 | 0.023888 | 2.9377e-05 | 1.8362e-05 | 0.1428 | 0.1428 | 0.1428 | 0.98363 | -0.31338 | 0.98397 | -0.30689 | 13.0773
60 | 0.089465 | 0.022623 | -0.089449 | -0.022612 | 1.642e-05 | 1.0237e-05 | 0.13552 | 0.13552 | 0.13552 | 0.98288 | -0.32791 | 0.98269 | -0.33174 | 12.4098
61 | -0.097237 | -0.024605 | 0.097296 | 0.024642 | 5.8576e-05 | 3.6663e-05 | 0.14713 | 0.14713 | 0.14713 | 0.98397 | -0.30689 | 0.98461 | -0.29435 | 13.4736
62 | -0.015064 | -0.0037758 | 0.015068 | 0.0037785 | 4.7366e-06 | 2.7163e-06 | 0.022673 | 0.022673 | 0.022673 | 0.98861 | -0.21747 | 0.98895 | -0.21087 | 6.229
63 | 0.01013 | 0.0025394 | -0.010128 | -0.0025384 | 1.9454e-06 | 9.5902e-07 | 0.015248 | 0.015248 | 0.015248 | 0.98861 | -0.21747 | 0.98841 | -0.2215 | 4.189
64 | -0.020031 | -0.0050223 | 0.020034 | 0.0050241 | 2.9383e-06 | 1.7698e-06 | 0.03014 | 0.03014 | 0.03014 | 0.98895 | -0.21087 | 0.98911 | -0.2078 | 8.2803
65 | -0.021747 | -0.0054534 | 0.021752 | 0.0054566 | 5.2873e-06 | 3.2147e-06 | 0.032717 | 0.032717 | 0.032717 | 0.98911 | -0.2078 | 0.98937 | -0.2027 | 8.9883
66 | -0.2731 | -0.069807 | 0.2733 | 0.069937 | 0.00020263 | 0.0001293 | 0.40831 | 0.40831 | 0.40831 | 0.99644 | -0.067331 | 0.99725 | -0.052005 | 37.3914
67 | 0.27073 | 0.069213 | -0.2706 | -0.069127 | 0.00013429 | 8.5692e-05 | 0.40477 | 0.40477 | 0.40477 | 0.99644 | -0.067331 | 0.9959 | -0.07759 | 37.0671
68 | -0.27519 | -0.07041 | 0.27522 | 0.070424 | 2.1406e-05 | 1.366e-05 | 0.41113 | 0.41113 | 0.41113 | 0.99725 | -0.052005 | 0.99734 | -0.050398 | 37.6497
69 | 0.26837 | 0.068569 | -0.2678 | -0.068205 | 0.00057067 | 0.00036412 | 0.40145 | 0.40145 | 0.40145 | 0.9959 | -0.07759 | 0.99359 | -0.12167 | 36.7625
70 | -0.27879 | -0.07132 | 0.27887 | 0.071373 | 8.1803e-05 | 5.2206e-05 | 0.41647 | 0.41647 | 0.41647 | 0.99734 | -0.050398 | 0.99766 | -0.044338 | 38.1383
71 | 0.093253 | 0.023765 | -0.093078 | -0.023653 | 0.00017497 | 0.00011167 | 0.1398 | 0.1398 | 0.1398 | 0.99359 | -0.12167 | 0.99156 | -0.16063 | 38.4057
72 | 0.17455 | 0.044441 | -0.17438 | -0.044336 | 0.00016493 | 0.00010481 | 0.26165 | 0.26165 | 0.26165 | 0.99359 | -0.12167 | 0.99257 | -0.14128 | 23.9607
73 | -0.28076 | -0.071846 | 0.28077 | 0.071849 | 3.7617e-06 | 2.4008e-06 | 0.41929 | 0.41929 | 0.41929 | 0.99766 | -0.044338 | 0.99767 | -0.044062 | 38.3965
74 | 0.091128 | 0.023164 | -0.091066 | -0.023125 | 6.1624e-05 | 3.9327e-05 | 0.13687 | 0.13687 | 0.13687 | 0.99156 | -0.16063 | 0.99082 | -0.17468 | 37.6018
75 | 0.17214 | 0.043773 | -0.17197 | -0.043667 | 0.00016747 | 0.0001064 | 0.25829 | 0.25829 | 0.25829 | 0.99257 | -0.14128 | 0.99151 | -0.1615 | 23.6525
76 | -0.28266 | -0.072322 | 0.28326 | 0.072708 | 0.00060432 | 0.0003857 | 0.42211 | 0.42211 | 0.42211 | 0.99767 | -0.044062 | 1 | 0 | 38.6545
77 | 0.088919 | 0.022587 | -0.088755 | -0.022482 | 0.00016383 | 0.00010454 | 0.13365 | 0.13365 | 0.13365 | 0.99082 | -0.17468 | 0.98883 | -0.21303 | 36.7161
78 | 0.16784 | 0.042633 | -0.16782 | -0.042622 | 1.6176e-05 | 1.0274e-05 | 0.25209 | 0.25209 | 0.25209 | 0.99151 | -0.1615 | 0.99141 | -0.1635 | 23.0852
79 | 0.0041279 | 0.0010341 | -0.0041275 | -0.0010342 | 3.9169e-07 | -1.0032e-07 | 0.0061948 | 0.0061949 | 0.0061949 | 0.99151 | -0.1615 | 0.99141 | -0.16349 | 1.7019
80 | 0.014845 | 0.0037227 | -0.014844 | -0.0037217 | 1.698e-06 | 9.7662e-07 | 0.022651 | 0.022651 | 0.022651 | 0.97526 | -0.47704 | 0.97513 | -0.47944 | 6.2229
81 | 0.015514 | 0.0038904 | -0.015513 | -0.0038899 | 9.1472e-07 | 5.3148e-07 | 0.023713 | 0.023713 | 0.023713 | 0.97356 | -0.51046 | 0.9735 | -0.5117 | 6.5145
82 | 0.012944 | 0.0032456 | -0.01294 | -0.0032432 | 4.2148e-06 | 2.3382e-06 | 0.019752 | 0.019752 | 0.019752 | 0.97513 | -0.47944 | 0.97479 | -0.48628 | 5.4265
83 | 0.015117 | 0.0037907 | -0.015111 | -0.0037873 | 5.9182e-06 | 3.4203e-06 | 0.023108 | 0.023108 | 0.023108 | 0.9735 | -0.5117 | 0.97308 | -0.51991 | 6.3484
84 | 0.010799 | 0.002707 | -0.010797 | -0.002706 | 1.777e-06 | 9.0856e-07 | 0.016276 | 0.016276 | 0.016276 | 0.98729 | -0.2428 | 0.98712 | -0.24625 | 4.4714
85 | -0.013147 | -0.0032954 | 0.013149 | 0.0032968 | 2.4034e-06 | 1.3294e-06 | 0.019815 | 0.019815 | 0.019815 | 0.98729 | -0.2428 | 0.98749 | -0.23896 | 5.4436
86 | 0.0088606 | 0.0022207 | -0.008859 | -0.00222 | 1.559e-06 | 6.9994e-07 | 0.013357 | 0.013357 | 0.013357 | 0.98712 | -0.24625 | 0.98693 | -0.24995 | 3.6695
87 | -0.017051 | -0.0042746 | 0.01706 | 0.00428 | 9.0393e-06 | 5.3178e-06 | 0.025694 | 0.025694 | 0.025694 | 0.98749 | -0.23896 | 0.98806 | -0.22784 | 7.0589
88 | 0.0069309 | 0.0017368 | -0.0069308 | -0.0017367 | 1.1237e-07 | 3.6852e-08 | 0.01045 | 0.01045 | 0.01045 | 0.98693 | -0.24995 | 0.98691 | -0.25029 | 2.8708
89 | 0.070103 | 0.017779 | -0.070041 | -0.01774 | 6.2377e-05 | 3.9731e-05 | 0.10565 | 0.10565 | 0.10565 | 0.98806 | -0.22784 | 0.9871 | -0.24637 | 29.0247
90 | -0.087163 | -0.022059 | 0.087225 | 0.022099 | 6.2015e-05 | 3.9566e-05 | 0.13134 | 0.13134 | 0.13134 | 0.98806 | -0.22784 | 0.98883 | -0.21303 | 36.0835
91 | 0.0048728 | 0.001221 | -0.0048726 | -0.001221 | 2.4594e-07 | 2.1529e-09 | 0.0073469 | 0.0073469 | 0.0073469 | 0.98691 | -0.25029 | 0.98685 | -0.25135 | 2.0184
92 | 0.068862 | 0.017444 | -0.068834 | -0.017427 | 2.7258e-05 | 1.7359e-05 | 0.10387 | 0.10387 | 0.10387 | 0.9871 | -0.24637 | 0.98667 | -0.25461 | 28.5364
93 | 0.0048726 | 0.001221 | -0.0048725 | -0.0012209 | 1.4411e-08 | 1.268e-10 | 0.0073469 | 0.0073469 | 0.0073469 | 0.98685 | -0.25135 | 0.98685 | -0.25141 | 2.0184
94 | 0.067656 | 0.017131 | -0.067644 | -0.017124 | 1.2348e-05 | 7.8622e-06 | 0.1021 | 0.1021 | 0.1021 | 0.98667 | -0.25461 | 0.98648 | -0.25841 | 28.0483
95 | 0.031392 | 0.0078978 | -0.031383 | -0.0078921 | 9.0859e-06 | 5.6813e-06 | 0.04773 | 0.04773 | 0.04773 | 0.9789 | -0.40582 | 0.97859 | -0.41188 | 13.1127
96 | -0.033278 | -0.0083704 | 0.033304 | 0.0083868 | 2.6022e-05 | 1.6313e-05 | 0.050597 | 0.050596 | 0.050597 | 0.9789 | -0.40582 | 0.97974 | -0.38946 | 13.9002
97 | 0.028553 | 0.0071828 | -0.028542 | -0.0071756 | 1.1691e-05 | 7.2745e-06 | 0.043427 | 0.043427 | 0.043427 | 0.97859 | -0.41188 | 0.97816 | -0.42045 | 11.9304
98 | -0.042343 | -0.010652 | 0.042371 | 0.01067 | 2.8411e-05 | 1.7952e-05 | 0.064324 | 0.064324 | 0.064324 | 0.97974 | -0.38946 | 0.98046 | -0.37543 | 17.6714
99 | 0.0090384 | 0.0022651 | -0.0090373 | -0.0022646 | 1.111e-06 | 5.1306e-07 | 0.013727 | 0.013727 | 0.013727 | 0.97974 | -0.38946 | 0.97961 | -0.39204 | 3.7713
100 | -0.046115 | -0.011608 | 0.046156 | 0.011634 | 4.0375e-05 | 2.5563e-05 | 0.070006 | 0.070006 | 0.070006 | 0.98046 | -0.37543 | 0.98139 | -0.35713 | 19.2324
101 | 0.0071994 | 0.001804 | -0.007199 | -0.0018038 | 3.3012e-07 | 1.1861e-07 | 0.010936 | 0.010936 | 0.010936 | 0.97961 | -0.39204 | 0.97956 | -0.393 | 3.0043
102 | -0.048212 | -0.012149 | 0.048227 | 0.012159 | 1.5098e-05 | 9.5675e-06 | 0.073123 | 0.073123 | 0.073123 | 0.98139 | -0.35713 | 0.98173 | -0.35058 | 20.0888
103 | 0.007199 | 0.0018038 | -0.0071966 | -0.001803 | 2.4164e-06 | 8.6845e-07 | 0.010936 | 0.010936 | 0.010936 | 0.97956 | -0.393 | 0.9792 | -0.40005 | 3.0044
104 | -0.05033 | -0.012686 | 0.050365 | 0.012708 | 3.4782e-05 | 2.2059e-05 | 0.076312 | 0.076312 | 0.076312 | 0.98173 | -0.35058 | 0.98247 | -0.33615 | 20.9648
105 | 0.0061241 | 0.0015342 | -0.0061226 | -0.0015338 | 1.518e-06 | 3.8372e-07 | 0.0093061 | 0.0093063 | 0.0093063 | 0.9792 | -0.40005 | 0.97894 | -0.40526 | 2.5567
106 | 0.018449 | 0.0046394 | -0.018444 | -0.0046382 | 4.6884e-06 | 1.2065e-06 | 0.028062 | 0.028063 | 0.028063 | 0.97844 | -0.41459 | 0.97817 | -0.41991 | 2.5699
107 | 0.018444 | 0.0046382 | -0.018428 | -0.0046306 | 1.6172e-05 | 7.6035e-06 | 0.028063 | 0.028064 | 0.028064 | 0.97817 | -0.41991 | 0.97723 | -0.43828 | 3.855
108 | 0.017001 | 0.0042736 | -0.016987 | -0.0042653 | 1.3965e-05 | 8.242e-06 | 0.025892 | 0.025892 | 0.025892 | 0.97723 | -0.43828 | 0.97636 | -0.4555 | 7.1133
109 | 0.0014265 | 0.00035705 | -0.0014264 | -0.00035739 | 5.3526e-08 | -3.4481e-07 | 0.0021719 | 0.002172 | 0.002172 | 0.97723 | -0.43828 | 0.97719 | -0.43907 | 0.59671
110 | 0.014492 | 0.0036399 | -0.014479 | -0.0036324 | 1.3159e-05 | 7.5233e-06 | 0.022089 | 0.02209 | 0.02209 | 0.97636 | -0.4555 | 0.97539 | -0.47454 | 6.0686
111 | 0.0010164 | 0.00025464 | -0.0010164 | -0.00025474 | 7.559e-09 | -1.0058e-07 | 0.0015477 | 0.0015478 | 0.0015478 | 0.97719 | -0.43907 | 0.97719 | -0.43922 | 0.42521
112 | -0.0027263 | -0.00068327 | 0.0027264 | 0.00068309 | 1.2772e-07 | -1.8052e-07 | 0.0040921 | 0.004092 | 0.0040921 | 0.99136 | -0.16447 | 0.99141 | -0.16349 | 1.1242
113 | -0.052095 | -0.013141 | 0.052115 | 0.013154 | 2.0471e-05 | 1.299e-05 | 0.078932 | 0.078932 | 0.078932 | 0.98247 | -0.33615 | 0.98289 | -0.32795 | 21.6845
114 | -0.0542 | -0.013677 | 0.05424 | 0.013702 | 3.9894e-05 | 2.5332e-05 | 0.082087 | 0.082087 | 0.082087 | 0.98289 | -0.32795 | 0.98368 | -0.31259 | 22.5514
115 | -0.0094092 | -0.0023579 | 0.0094095 | 0.002358 | 2.0461e-07 | 9.8007e-08 | 0.014366 | 0.014366 | 0.014366 | 0.97458 | -0.49046 | 0.9746 | -0.49001 | 3.9468
116 | 0.0082476 | 0.0020667 | -0.0082472 | -0.0020666 | 4.1022e-07 | 1.7646e-07 | 0.012588 | 0.012588 | 0.012588 | 0.97493 | -0.48396 | 0.97487 | -0.485 | 3.4583
117 | 0.0072278 | 0.0018111 | -0.0072272 | -0.0018108 | 6.4127e-07 | 2.3525e-07 | 0.011032 | 0.011032 | 0.011032 | 0.97487 | -0.485 | 0.97478 | -0.48687 | 3.0308
118 | 0.0062107 | 0.0015561 | -0.0062095 | -0.0015558 | 1.2527e-06 | 3.3854e-07 | 0.0094806 | 0.0094808 | 0.0094808 | 0.97478 | -0.48687 | 0.97457 | -0.4911 | 2.6046
119 | 0.0062095 | 0.0015558 | -0.0062088 | -0.0015556 | 6.7317e-07 | 1.8201e-07 | 0.0094808 | 0.0094809 | 0.0094809 | 0.97457 | -0.4911 | 0.97445 | -0.49338 | 2.6046
120 | 0.0042309 | 0.0010599 | -0.0042304 | -0.0010599 | 4.6321e-07 | -7.2169e-08 | 0.0064605 | 0.0064606 | 0.0064606 | 0.97445 | -0.49338 | 0.97433 | -0.49568 | 1.7749
121 | -0.056674 | -0.014312 | 0.05668 | 0.014316 | 5.5977e-06 | 3.5568e-06 | 0.08577 | 0.08577 | 0.08577 | 0.98368 | -0.31259 | 0.98379 | -0.31053 | 23.5632
122 | -0.059369 | -0.01499 | 0.059431 | 0.01503 | 6.282e-05 | 3.9941e-05 | 0.089837 | 0.089836 | 0.089837 | 0.98379 | -0.31053 | 0.98493 | -0.28847 | 24.6804
123 | 0.0022125 | 0.00055427 | -0.0022124 | -0.00055447 | 8.3787e-08 | -2.0288e-07 | 0.003336 | 0.0033361 | 0.0033361 | 0.98685 | -0.25141 | 0.98681 | -0.2522 | 0.9165
124 | 0.064397 | 0.01631 | -0.064312 | -0.016256 | 8.4508e-05 | 5.3781e-05 | 0.097198 | 0.097198 | 0.097198 | 0.98648 | -0.25841 | 0.98506 | -0.28578 | 26.7027
125 | -0.013005 | -0.0032611 | 0.013008 | 0.0032625 | 2.543e-06 | 1.4129e-06 | 0.019851 | 0.019851 | 0.019851 | 0.97487 | -0.48484 | 0.97508 | -0.48073 | 5.4537
126 | 0.0071811 | 0.0018015 | -0.0071668 | -0.0017963 | 1.4246e-05 | 5.1845e-06 | 0.010962 | 0.010963 | 0.010963 | 0.97487 | -0.48484 | 0.97276 | -0.5265 | 3.0118
127 | -0.013008 | -0.0032625 | 0.013011 | 0.0032647 | 3.84e-06 | 2.1333e-06 | 0.019851 | 0.019851 | 0.019851 | 0.97508 | -0.48073 | 0.97539 | -0.47454 | 5.4536
128 | 0.0071668 | 0.0017963 | -0.0071658 | -0.0017959 | 1.0303e-06 | 3.7566e-07 | 0.010963 | 0.010963 | 0.010963 | 0.97276 | -0.5265 | 0.9726 | -0.52952 | 3.0119
129 | 0.0037409 | 0.00093689 | -0.0037402 | -0.00093715 | 6.5865e-07 | -2.613e-07 | 0.0056861 | 0.0056863 | 0.0056863 | 0.97894 | -0.40526 | 0.97875 | -0.40896 | 1.5622
130 | 0.0011315 | 0.00028335 | -0.0011315 | -0.00028359 | 2.2275e-08 | -2.3799e-07 | 0.0017202 | 0.0017203 | 0.0017203 | 0.97875 | -0.40896 | 0.97873 | -0.40937 | 0.47262
131 | 0.0018966 | 0.00047502 | -0.0018965 | -0.00047531 | 8.5287e-08 | -2.8304e-07 | 0.0028964 | 0.0028965 | 0.0028965 | 0.97433 | -0.49568 | 0.97429 | -0.49662 | 0.79574
132 | 0.002661 | 0.0006665 | -0.0026608 | -0.00066686 | 2.2267e-07 | -3.5432e-07 | 0.0039595 | 0.0039597 | 0.0039597 | 1 | 0 | 0.99991 | -0.001757 | 1.0878
133 | -0.011159 | -0.0027964 | 0.011161 | 0.0027975 | 1.9816e-06 | 1.0413e-06 | 0.017037 | 0.017037 | 0.017037 | 0.9746 | -0.49001 | 0.97479 | -0.48628 | 4.6806
134 | -0.062224 | -0.01573 | 0.062232 | 0.015735 | 8.0258e-06 | 5.1057e-06 | 0.094056 | 0.094056 | 0.094056 | 0.98493 | -0.28847 | 0.98506 | -0.28578 | 25.8394

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.2936 | 0.074884

## res_load
| p_mw | q_mvar
0 | 0.00086371 | 0.00021647
1 | 0.0012617 | 0.00031622
2 | 0.0011631 | 0.00029151
3 | 0.0015045 | 0.00037706
4 | 0.0012988 | 0.00032552
5 | 0.0027812 | 0.00069702
6 | 0.001109 | 0.00027794
7 | 0.0010691 | 0.00026793
8 | 0.00088817 | 0.0002226
9 | 0.00097296 | 0.00024385
10 | 0.0023097 | 0.00057886
11 | 0.0020009 | 0.00050148
12 | 0.0015189 | 0.00038067
13 | 0.0012591 | 0.00031557
14 | 0.0012351 | 0.00030955
15 | 0.0010039 | 0.00025161
16 | 0.0010177 | 0.00025506
17 | 0.001734 | 0.00043459
18 | 0.0015798 | 0.00039594
19 | 0.0016869 | 0.00042277
20 | 0.001547 | 0.00038772
21 | 0.001548 | 0.00038798
22 | 0.0011149 | 0.00027943
23 | 0.0010502 | 0.00026319
24 | 0.0020913 | 0.00052414
25 | 0.00088572 | 0.00022198
26 | 0.0019137 | 0.00047963
27 | 0.0048697 | 0.0012205
28 | 0.0046049 | 0.0011541
29 | 0.0031495 | 0.00078933
30 | 0.0042379 | 0.0010621
31 | 0.0052926 | 0.0013264
32 | 0.0024842 | 0.0006226
33 | 0.00076394 | 0.00019146
34 | 0.0010721 | 0.0002687
35 | 0.001545 | 0.00038721
36 | 0.0024503 | 0.00061411
37 | 0.0059634 | 0.0014946
38 | 0.0021885 | 0.00054849
39 | 0.0032552 | 0.00081583
40 | 0.0031544 | 0.00079057
41 | 0.0019285 | 0.00048333
42 | 0.0021639 | 0.00054233
43 | 0.00072456 | 0.00018159
44 | 0.0028623 | 0.00071735
45 | 0.0015508 | 0.00038867
46 | 0.0047036 | 0.0011788
47 | 0.0049334 | 0.0012364
48 | 0.0049627 | 0.0012438
49 | 0.010128 | 0.0025384
50 | 0.0017131 | 0.00042933
51 | 0.0043466 | 0.0010894
52 | 0.0023717 | 0.0005944
53 | 0.00189 | 0.00047368
54 | 0.0022263 | 0.00055796
55 | 0.0035762 | 0.00089627
56 | 0.0018904 | 0.00047377
57 | 0.00195 | 0.00048872
58 | 0.002245 | 0.00056265
59 | 0.0018892 | 0.00047348
60 | 0.0021468 | 0.00053805
61 | 0.0020644 | 0.0005174
62 | 0.0011276 | 0.0002826
63 | 0.003042 | 0.0007624
64 | 0.0018999 | 0.00047615
65 | 0.00039575 | 9.9184e-05
66 | 0.002348 | 0.00058847
67 | 0.0019366 | 0.00048535
68 | 0.0039018 | 0.00097789
69 | 0.0019281 | 0.00048323
70 | 0.002058 | 0.00051579
71 | 0.0011791 | 0.00029552
72 | 0.0015302 | 0.00038351
73 | 0.0011781 | 0.00029527
74 | 0.0018858 | 0.00047263
75 | 0.0028302 | 0.0007093
76 | 0.0037441 | 0.00093837
77 | 0.0018379 | 0.00046062
78 | 0.002056 | 0.00051529
79 | 0.0021037 | 0.00052725
80 | 0.0010725 | 0.0002688
81 | 0.015111 | 0.0037873
82 | 0.0025429 | 0.00063731
83 | 0.0024954 | 0.0006254
84 | 0.00041 | 0.00010276
85 | 0.0069842 | 0.0017504
86 | 0.0049055 | 0.0012294
87 | 0.0027263 | 0.00068327
88 | 0.0014011 | 0.00035114
89 | 0.0017296 | 0.00043348
90 | 0.0020844 | 0.00052239
91 | 0.0015774 | 0.00039533
92 | 0.0014877 | 0.00037285
93 | 0.0010194 | 0.00025548
94 | 0.0010164 | 0.00025475
95 | 0.0019779 | 0.00049572
96 | 0.0024348 | 0.00061021
97 | 0.0026885 | 0.00067381
98 | 0.0026601 | 0.00066668
99 | 0.0032472 | 0.00081382
100 | 0.0058241 | 0.0014596
101 | 0.0014673 | 0.00036775
102 | 0.0071658 | 0.0017959
103 | 0.0023817 | 0.0005969
104 | 0.0026087 | 0.0006538
105 | 0.0011315 | 0.00028359
106 | 0.0022124 | 0.00055447
107 | 0.0023338 | 0.00058491
108 | 0.0018965 | 0.00047531
109 | 0.0060239 | 0.0015097
110 | 0.0026608 | 0.00066686
111 | 0.0017495 | 0.00043846
112 | 0.0017786 | 0.00044576
113 | 0.0027926 | 0.0006999
114 | 0.0020801 | 0.00052133
115 | 0.0010164 | 0.00025474

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1