## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2611-2_1_3_node_5 | 0.4 | n |  | TRUE
1 | bus_LV_2611-2_1_3_node_6 | 0.4 | n |  | TRUE
2 | bus_LV_2611-2_1_3_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_2611-2_1_3_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_2611-2_1_3_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_2611-2_1_3_node_29 | 0.4 | n |  | TRUE
6 | bus_LV_2611-2_1_3_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_2611-2_1_3_node_154 | 0.4 | n |  | TRUE
8 | bus_LV_2611-2_1_3_node_26 | 0.4 | n |  | TRUE
9 | bus_LV_2611-2_1_3_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_2611-2_1_3_node_125 | 0.4 | n |  | TRUE
11 | bus_LV_2611-2_1_3_node_169 | 0.4 | n |  | TRUE
12 | bus_LV_2611-2_1_3_node_212 | 0.4 | n |  | TRUE
13 | bus_LV_2611-2_1_3_node_25 | 0.4 | n |  | TRUE
14 | bus_LV_2611-2_1_3_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_2611-2_1_3_node_137 | 0.4 | n |  | TRUE
16 | bus_LV_2611-2_1_3_node_139 | 0.4 | n |  | TRUE
17 | bus_LV_2611-2_1_3_node_135 | 0.4 | n |  | TRUE
18 | bus_LV_2611-2_1_3_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_2611-2_1_3_node_32 | 0.4 | n |  | TRUE
20 | bus_LV_2611-2_1_3_node_33 | 0.4 | n |  | TRUE
21 | bus_LV_2611-2_1_3_node_34 | 0.4 | n |  | TRUE
22 | bus_LV_2611-2_1_3_node_35 | 0.4 | n |  | TRUE
23 | bus_LV_2611-2_1_3_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_2611-2_1_3_node_83 | 0.4 | n |  | TRUE
25 | bus_LV_2611-2_1_3_node_101 | 0.4 | n |  | TRUE
26 | bus_LV_2611-2_1_3_node_85 | 0.4 | n |  | TRUE
27 | bus_LV_2611-2_1_3_node_81 | 0.4 | n |  | TRUE
28 | bus_LV_2611-2_1_3_node_129 | 0.4 | n |  | TRUE
29 | bus_LV_2611-2_1_3_node_91 | 0.4 | n |  | TRUE
30 | bus_LV_2611-2_1_3_node_103 | 0.4 | n |  | TRUE
31 | bus_LV_2611-2_1_3_node_49 | 0.4 | n |  | TRUE
32 | bus_LV_2611-2_1_3_node_50 | 0.4 | n |  | TRUE
33 | bus_LV_2611-2_1_3_node_214 | 0.4 | n |  | TRUE
34 | bus_LV_2611-2_1_3_node_51 | 0.4 | n |  | TRUE
35 | bus_LV_2611-2_1_3_node_82 | 0.4 | n |  | TRUE
36 | bus_LV_2611-2_1_3_node_84 | 0.4 | n |  | TRUE
37 | bus_LV_2611-2_1_3_node_76 | 0.4 | n |  | TRUE
38 | bus_LV_2611-2_1_3_node_77 | 0.4 | n |  | TRUE
39 | bus_LV_2611-2_1_3_node_78 | 0.4 | n |  | TRUE
40 | bus_LV_2611-2_1_3_node_79 | 0.4 | n |  | TRUE
41 | bus_LV_2611-2_1_3_node_80 | 0.4 | n |  | TRUE
42 | bus_LV_2611-2_1_3_node_144 | 0.4 | n |  | TRUE
43 | bus_LV_2611-2_1_3_node_88 | 0.4 | n |  | TRUE
44 | bus_LV_2611-2_1_3_node_145 | 0.4 | n |  | TRUE
45 | bus_LV_2611-2_1_3_node_130 | 0.4 | n |  | TRUE
46 | bus_LV_2611-2_1_3_node_207 | 0.4 | n |  | TRUE
47 | bus_LV_2611-2_1_3_node_197 | 0.4 | n |  | TRUE
48 | bus_LV_2611-2_1_3_node_178 | 0.4 | n |  | TRUE
49 | bus_LV_2611-2_1_3_node_87 | 0.4 | n |  | TRUE
50 | bus_LV_2611-2_1_3_node_89 | 0.4 | n |  | TRUE
51 | bus_LV_2611-2_1_3_node_90 | 0.4 | n |  | TRUE
52 | bus_LV_2611-2_1_3_node_167 | 0.4 | n |  | TRUE
53 | bus_LV_2611-2_1_3_node_199 | 0.4 | n |  | TRUE
54 | bus_LV_2611-2_1_3_node_95 | 0.4 | n |  | TRUE
55 | bus_LV_2611-2_1_3_node_96 | 0.4 | n |  | TRUE
56 | bus_LV_2611-2_1_3_node_97 | 0.4 | n |  | TRUE
57 | bus_LV_2611-2_1_3_node_98 | 0.4 | n |  | TRUE
58 | bus_LV_2611-2_1_3_node_99 | 0.4 | n |  | TRUE
59 | bus_LV_2611-2_1_3_node_171 | 0.4 | n |  | TRUE
60 | bus_LV_2611-2_1_3_node_182 | 0.4 | n |  | TRUE
61 | bus_LV_2611-2_1_3_node_194 | 0.4 | n |  | TRUE
62 | bus_LV_2611-2_1_3_node_181 | 0.4 | n |  | TRUE
63 | bus_LV_2611-2_1_3_node_193 | 0.4 | n |  | TRUE
64 | bus_LV_2611-2_1_3_node_116 | 0.4 | n |  | TRUE
65 | bus_LV_2611-2_1_3_node_117 | 0.4 | n |  | TRUE
66 | bus_LV_2611-2_1_3_node_104 | 0.4 | n |  | TRUE
67 | bus_LV_2611-2_1_3_node_105 | 0.4 | n |  | TRUE
68 | bus_LV_2611-2_1_3_node_106 | 0.4 | n |  | TRUE
69 | bus_LV_2611-2_1_3_node_107 | 0.4 | n |  | TRUE
70 | bus_LV_2611-2_1_3_node_109 | 0.4 | n |  | TRUE
71 | bus_LV_2611-2_1_3_node_108 | 0.4 | n |  | TRUE
72 | bus_LV_2611-2_1_3_node_110 | 0.4 | n |  | TRUE
73 | bus_LV_2611-2_1_3_node_111 | 0.4 | n |  | TRUE
74 | bus_LV_2611-2_1_3_node_112 | 0.4 | n |  | TRUE
75 | bus_LV_2611-2_1_3_node_113 | 0.4 | n |  | TRUE
76 | bus_LV_2611-2_1_3_node_114 | 0.4 | n |  | TRUE
77 | bus_LV_2611-2_1_3_node_115 | 0.4 | n |  | TRUE
78 | bus_LV_2611-2_1_3_node_119 | 0.4 | n |  | TRUE
79 | bus_LV_2611-2_1_3_node_126 | 0.4 | n |  | TRUE
80 | bus_LV_2611-2_1_3_node_121 | 0.4 | n |  | TRUE
81 | bus_LV_2611-2_1_3_node_151 | 0.4 | n |  | TRUE
82 | bus_LV_2611-2_1_3_node_128 | 0.4 | n |  | TRUE
83 | bus_LV_2611-2_1_3_node_118 | 0.4 | n |  | TRUE
84 | bus_LV_2611-2_1_3_node_205 | 0.4 | n |  | TRUE
85 | bus_LV_2611-2_1_3_node_127 | 0.4 | n |  | TRUE
86 | bus_LV_2611-2_1_3_node_213 | 0.4 | n |  | TRUE
87 | bus_LV_2611-2_1_3_node_198 | 0.4 | n |  | TRUE
88 | bus_LV_2611-2_1_3_node_131 | 0.4 | n |  | TRUE
89 | bus_LV_2611-2_1_3_node_132 | 0.4 | n |  | TRUE
90 | bus_LV_2611-2_1_3_node_133 | 0.4 | n |  | TRUE
91 | bus_LV_2611-2_1_3_node_134 | 0.4 | n |  | TRUE
92 | bus_LV_2611-2_1_3_node_160 | 0.4 | n |  | TRUE
93 | bus_LV_2611-2_1_3_node_177 | 0.4 | n |  | TRUE
94 | bus_LV_2611-2_1_3_node_161 | 0.4 | n |  | TRUE
95 | bus_LV_2611-2_1_3_node_136 | 0.4 | n |  | TRUE
96 | bus_LV_2611-2_1_3_node_138 | 0.4 | n |  | TRUE
97 | bus_LV_2611-2_1_3_node_168 | 0.4 | n |  | TRUE
98 | bus_LV_2611-2_1_3_node_170 | 0.4 | n |  | TRUE
99 | bus_LV_2611-2_1_3_node_180 | 0.4 | n |  | TRUE
100 | bus_LV_2611-2_1_3_node_179 | 0.4 | n |  | TRUE
101 | bus_LV_2611-2_1_3_node_172 | 0.4 | n |  | TRUE
102 | bus_LV_2611-2_1_3_node_173 | 0.4 | n |  | TRUE
103 | bus_LV_2611-2_1_3_node_174 | 0.4 | n |  | TRUE
104 | bus_LV_2611-2_1_3_node_175 | 0.4 | n |  | TRUE
105 | bus_LV_2611-2_1_3_node_176 | 0.4 | n |  | TRUE
106 | bus_LV_2611-2_1_3_node_185 | 0.4 | n |  | TRUE
107 | bus_LV_2611-2_1_3_node_186 | 0.4 | n |  | TRUE
108 | bus_LV_2611-2_1_3_node_187 | 0.4 | n |  | TRUE
109 | bus_LV_2611-2_1_3_node_188 | 0.4 | n |  | TRUE
110 | bus_LV_2611-2_1_3_node_189 | 0.4 | n |  | TRUE
111 | bus_MV_293_0_node_7 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2611-2_1_3_load_5 | 0 | 0.0024027 | 0.00060217 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2611-2_1_3_load_6 | 1 | 0.0019077 | 0.00047811 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2611-2_1_3_load_7 | 2 | 0.00086063 | 0.0002157 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2611-2_1_3_load_8 | 3 | 0.0016669 | 0.00041776 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2611-2_1_3_load_9 | 4 | 0.0017588 | 0.0004408 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2611-2_1_3_load_154 | 7 | 0.0018583 | 0.00046573 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2611-2_1_3_load_212 | 12 | 0.00090073 | 0.00022575 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2611-2_1_3_load_25 | 13 | 0.0030216 | 0.00075728 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2611-2_1_3_load_30 | 14 | 0.0016999 | 0.00042603 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2611-2_1_3_load_139 | 16 | 0.0019494 | 0.00048856 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2611-2_1_3_load_135 | 17 | 0.0015684 | 0.00039309 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2611-2_1_3_load_31 | 18 | 0.0044032 | 0.0011036 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2611-2_1_3_load_32 | 19 | 0.0022006 | 0.00055151 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2611-2_1_3_load_33 | 20 | 0.0011921 | 0.00029877 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2611-2_1_3_load_34 | 21 | 0.00061855 | 0.00015502 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2611-2_1_3_load_36 | 23 | 0.00082167 | 0.00020593 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2611-2_1_3_load_101 | 25 | 0.00080717 | 0.0002023 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2611-2_1_3_load_85 | 26 | 0.0027434 | 0.00068757 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2611-2_1_3_load_81 | 27 | 0.0009747 | 0.00024428 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2611-2_1_3_load_129 | 28 | 0.0008975 | 0.00022493 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2611-2_1_3_load_103 | 30 | 0.00078147 | 0.00019586 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2611-2_1_3_load_49 | 31 | 0.00059585 | 0.00014933 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2611-2_1_3_load_50 | 32 | 0.0019826 | 0.00049689 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2611-2_1_3_load_214 | 33 | 0.00099656 | 0.00024976 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2611-2_1_3_load_84 | 36 | 0.0027915 | 0.00069963 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2611-2_1_3_load_76 | 37 | 0.0013611 | 0.00034113 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2611-2_1_3_load_77 | 38 | 0.0020522 | 0.00051432 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2611-2_1_3_load_78 | 39 | 0.0012374 | 0.00031013 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2611-2_1_3_load_79 | 40 | 0.00096627 | 0.00024217 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2611-2_1_3_load_144 | 42 | 0.0038893 | 0.00097474 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2611-2_1_3_load_88 | 43 | 0.0017955 | 0.00045 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2611-2_1_3_load_145 | 44 | 0.0017945 | 0.00044974 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2611-2_1_3_load_130 | 45 | 0.0016133 | 0.00040432 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2611-2_1_3_load_207 | 46 | 0.0024158 | 0.00060545 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2611-2_1_3_load_197 | 47 | 0.0015243 | 0.00038202 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2611-2_1_3_load_178 | 48 | 0.0019616 | 0.00049161 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2611-2_1_3_load_87 | 49 | 0.0021005 | 0.00052643 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2611-2_1_3_load_89 | 50 | 0.0010476 | 0.00026255 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2611-2_1_3_load_90 | 51 | 0.0010034 | 0.00025146 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2611-2_1_3_load_167 | 52 | 0.0015783 | 0.00039557 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2611-2_1_3_load_199 | 53 | 0.0016011 | 0.00040128 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2611-2_1_3_load_95 | 54 | 0.0026 | 0.00065162 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2611-2_1_3_load_96 | 55 | 0.00217 | 0.00054386 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2611-2_1_3_load_98 | 57 | 0.0012081 | 0.00030279 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2611-2_1_3_load_171 | 59 | 0.0023523 | 0.00058954 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2611-2_1_3_load_182 | 60 | 0.0013771 | 0.00034512 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2611-2_1_3_load_194 | 61 | 0.0014868 | 0.00037263 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2611-2_1_3_load_181 | 62 | 0.002037 | 0.00051052 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2611-2_1_3_load_193 | 63 | 0.0019256 | 0.00048259 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2611-2_1_3_load_116 | 64 | 0.00054409 | 0.00013636 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2611-2_1_3_load_104 | 66 | 0.001545 | 0.00038722 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2611-2_1_3_load_105 | 67 | 0.001065 | 0.00026692 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2611-2_1_3_load_106 | 68 | 0.0010208 | 0.00025583 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2611-2_1_3_load_107 | 69 | 0.0010553 | 0.00026448 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2611-2_1_3_load_109 | 70 | 0.00093761 | 0.00023499 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2611-2_1_3_load_108 | 71 | 0.001229 | 0.00030802 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2611-2_1_3_load_110 | 72 | 0.0018653 | 0.00046749 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2611-2_1_3_load_111 | 73 | 0.0017213 | 0.0004314 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2611-2_1_3_load_112 | 74 | 0.0017326 | 0.00043423 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2611-2_1_3_load_113 | 75 | 0.0035128 | 0.00088038 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2611-2_1_3_load_114 | 76 | 0.00059936 | 0.00015021 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2611-2_1_3_load_119 | 78 | 0.00089749 | 0.00022493 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2611-2_1_3_load_126 | 79 | 0.00055227 | 0.00013841 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2611-2_1_3_load_128 | 82 | 0.00046705 | 0.00011705 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2611-2_1_3_load_118 | 83 | 0.0035206 | 0.00088235 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2611-2_1_3_load_205 | 84 | 0.0013909 | 0.00034859 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2611-2_1_3_load_127 | 85 | 0.00051482 | 0.00012903 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2611-2_1_3_load_213 | 86 | 0.0017092 | 0.00042837 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2611-2_1_3_load_198 | 87 | 0.0014038 | 0.00035184 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2611-2_1_3_load_131 | 88 | 0.0017056 | 0.00042746 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2611-2_1_3_load_133 | 90 | 0.0014402 | 0.00036095 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2611-2_1_3_load_134 | 91 | 0.001098 | 0.00027519 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2611-2_1_3_load_160 | 92 | 0.0016934 | 0.00042442 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2611-2_1_3_load_177 | 93 | 0.0023019 | 0.0005769 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2611-2_1_3_load_161 | 94 | 0.0016209 | 0.00040624 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2611-2_1_3_load_136 | 95 | 0.0028408 | 0.00071197 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2611-2_1_3_load_138 | 96 | 0.0011074 | 0.00027753 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2611-2_1_3_load_168 | 97 | 0.003268 | 0.00081903 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2611-2_1_3_load_170 | 98 | 0.0012526 | 0.00031394 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2611-2_1_3_load_180 | 99 | 0.0020021 | 0.00050178 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2611-2_1_3_load_179 | 100 | 0.0020952 | 0.00052512 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2611-2_1_3_load_172 | 101 | 0.0020394 | 0.00051112 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2611-2_1_3_load_173 | 102 | 0.0013532 | 0.00033914 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2611-2_1_3_load_174 | 103 | 0.0022821 | 0.00057195 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2611-2_1_3_load_175 | 104 | 0.0016122 | 0.00040406 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2611-2_1_3_load_176 | 105 | 0.0027065 | 0.0006783 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2611-2_1_3_load_185 | 106 | 0.0019699 | 0.0004937 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2611-2_1_3_load_186 | 107 | 0.0026913 | 0.00067449 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2611-2_1_3_load_187 | 108 | 0.0019526 | 0.00048938 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2611-2_1_3_load_188 | 109 | 0.0010027 | 0.0002513 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2611-2_1_3_load_189 | 110 | 0.0028477 | 0.0007137 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 87 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2611-2_1_3_line_0 |  | 0 | 1 | 0.020438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2611-2_1_3_line_1 |  | 0 | 2 | 0.036945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2611-2_1_3_line_2 |  | 1 | 3 | 0.019325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2611-2_1_3_line_3 |  | 2 | 4 | 0.034537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2611-2_1_3_line_4 |  | 3 | 5 | 0.017033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2611-2_1_3_line_5 |  | 4 | 6 | 0.0062985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2611-2_1_3_line_6 |  | 5 | 7 | 0.017881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2611-2_1_3_line_7 |  | 5 | 8 | 0.01797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2611-2_1_3_line_8 |  | 6 | 9 | 0.009473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2611-2_1_3_line_9 |  | 8 | 14 | 0.0030058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2611-2_1_3_line_10 |  | 8 | 13 | 0.01574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2611-2_1_3_line_11 |  | 9 | 10 | 0.009916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2611-2_1_3_line_12 |  | 10 | 11 | 0.03114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2611-2_1_3_line_13 |  | 10 | 12 | 0.0079184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2611-2_1_3_line_14 |  | 11 | 52 | 0.075066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2611-2_1_3_line_15 |  | 11 | 51 | 0.038412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2611-2_1_3_line_16 |  | 12 | 86 | 0.057447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2611-2_1_3_line_17 |  | 14 | 15 | 0.011195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2611-2_1_3_line_18 |  | 15 | 16 | 0.011028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_2611-2_1_3_line_19 |  | 15 | 17 | 0.01619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_2611-2_1_3_line_20 |  | 16 | 94 | 0.020245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_2611-2_1_3_line_21 |  | 17 | 95 | 0.012536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_2611-2_1_3_line_22 |  | 18 | 19 | 0.06287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2611-2_1_3_line_23 |  | 18 | 20 | 0.032494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_2611-2_1_3_line_24 |  | 19 | 21 | 0.059461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2611-2_1_3_line_25 |  | 20 | 22 | 0.011556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_2611-2_1_3_line_26 |  | 21 | 23 | 0.043634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2611-2_1_3_line_27 |  | 22 | 24 | 0.002937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_2611-2_1_3_line_28 |  | 23 | 25 | 0.0137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2611-2_1_3_line_29 |  | 24 | 26 | 0.052364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_2611-2_1_3_line_30 |  | 24 | 27 | 0.19263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2611-2_1_3_line_31 |  | 25 | 30 | 0.014361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2611-2_1_3_line_32 |  | 26 | 47 | 0.033114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_2611-2_1_3_line_33 |  | 27 | 35 | 0.008671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2611-2_1_3_line_34 |  | 28 | 29 | 0.035277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2611-2_1_3_line_35 |  | 29 | 45 | 0.044306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_2611-2_1_3_line_36 |  | 29 | 41 | 0.00544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_2611-2_1_3_line_37 |  | 30 | 66 | 0.0027367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2611-2_1_3_line_38 |  | 31 | 32 | 0.028718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2611-2_1_3_line_39 |  | 31 | 33 | 0.2307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2611-2_1_3_line_40 |  | 32 | 34 | 0.042395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2611-2_1_3_line_41 |  | 34 | 35 | 0.017912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2611-2_1_3_line_42 |  | 35 | 36 | 0.035221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2611-2_1_3_line_43 |  | 36 | 46 | 0.020083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2611-2_1_3_line_44 |  | 37 | 38 | 0.029605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_2611-2_1_3_line_45 |  | 37 | 39 | 0.018879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_2611-2_1_3_line_46 |  | 38 | 40 | 0.018108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_2611-2_1_3_line_47 |  | 39 | 41 | 0.0080031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_2611-2_1_3_line_48 |  | 40 | 42 | 0.0172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_2611-2_1_3_line_49 |  | 41 | 43 | 0.0039607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2611-2_1_3_line_50 |  | 42 | 44 | 0.0035883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_2611-2_1_3_line_51 |  | 44 | 96 | 0.020961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_2611-2_1_3_line_52 |  | 45 | 53 | 0.02609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_2611-2_1_3_line_53 |  | 47 | 48 | 0.023005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_2611-2_1_3_line_54 |  | 48 | 93 | 0.025335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_2611-2_1_3_line_55 |  | 49 | 50 | 0.030128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2611-2_1_3_line_56 |  | 50 | 51 | 0.016825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2611-2_1_3_line_57 |  | 52 | 97 | 0.038287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2611-2_1_3_line_58 |  | 53 | 87 | 0.021713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_2611-2_1_3_line_59 |  | 54 | 55 | 0.046255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2611-2_1_3_line_60 |  | 54 | 56 | 0.10884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2611-2_1_3_line_61 |  | 55 | 57 | 0.067273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2611-2_1_3_line_62 |  | 56 | 58 | 0.014509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2611-2_1_3_line_63 |  | 57 | 59 | 0.10129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2611-2_1_3_line_64 |  | 58 | 60 | 0.015968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2611-2_1_3_line_65 |  | 58 | 61 | 0.036542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2611-2_1_3_line_66 |  | 60 | 62 | 0.017268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2611-2_1_3_line_67 |  | 61 | 63 | 0.038826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2611-2_1_3_line_68 |  | 62 | 104 | 0.011641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2611-2_1_3_line_69 |  | 63 | 109 | 0.033278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2611-2_1_3_line_70 |  | 64 | 65 | 0.012773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2611-2_1_3_line_71 |  | 65 | 83 | 0.10489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2611-2_1_3_line_72 |  | 66 | 67 | 0.031388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2611-2_1_3_line_73 |  | 67 | 68 | 0.002559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2611-2_1_3_line_74 |  | 68 | 69 | 0.026053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2611-2_1_3_line_75 |  | 69 | 70 | 0.016531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2611-2_1_3_line_76 |  | 70 | 71 | 0.0073589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2611-2_1_3_line_77 |  | 71 | 72 | 0.0073207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2611-2_1_3_line_78 |  | 72 | 73 | 0.016979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2611-2_1_3_line_79 |  | 73 | 74 | 0.017248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2611-2_1_3_line_80 |  | 74 | 75 | 0.0113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2611-2_1_3_line_81 |  | 75 | 76 | 0.042666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2611-2_1_3_line_82 |  | 76 | 77 | 0.0024641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2611-2_1_3_line_83 |  | 77 | 78 | 0.0081374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2611-2_1_3_line_84 |  | 78 | 79 | 0.014871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2611-2_1_3_line_85 |  | 79 | 85 | 0.028353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2611-2_1_3_line_86 |  | 80 | 81 | 0.1148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2611-2_1_3_line_87 |  | 80 | 82 | 0.06873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2611-2_1_3_line_88 |  | 81 | 84 | 0.11513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2611-2_1_3_line_89 |  | 81 | 83 | 0.048336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2611-2_1_3_line_90 |  | 82 | 85 | 0.013426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2611-2_1_3_line_91 |  | 87 | 110 | 0.028123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2611-2_1_3_line_92 |  | 88 | 89 | 0.067735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2611-2_1_3_line_93 |  | 89 | 90 | 0.017302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
94 | LV_2611-2_1_3_line_94 |  | 89 | 91 | 0.032212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
95 | LV_2611-2_1_3_line_95 |  | 90 | 92 | 0.036046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_2611-2_1_3_line_96 |  | 91 | 93 | 0.028118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
97 | LV_2611-2_1_3_line_97 |  | 92 | 94 | 0.0083276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
98 | LV_2611-2_1_3_line_98 |  | 95 | 96 | 0.0069637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
99 | LV_2611-2_1_3_line_99 |  | 97 | 98 | 0.036491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2611-2_1_3_line_100 |  | 98 | 99 | 0.03695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2611-2_1_3_line_101 |  | 99 | 100 | 0.0046724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2611-2_1_3_line_102 |  | 100 | 105 | 0.062723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2611-2_1_3_line_103 |  | 101 | 102 | 0.0002505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2611-2_1_3_line_104 |  | 101 | 103 | 0.02954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2611-2_1_3_line_105 |  | 102 | 104 | 0.029798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2611-2_1_3_line_106 |  | 106 | 107 | 0.022775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2611-2_1_3_line_107 |  | 106 | 108 | 0.001922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2611-2_1_3_line_108 |  | 107 | 109 | 0.028943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2611-2_1_3_line_109 |  | 108 | 110 | 0.025533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2611-2_1_3_trafo_198 | 0.63 MVA 20/0.4 kV | 111 | 87 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26
0 | 2602710.7419 | 1249158.1394 | 2602711.3005 | 1249151.9032 | 2602712.3001 | 1249144.9992 | 2602713.4249 | 1249137.8863
1 | 2602706.394 | 1249193.1592 | 2602708.1421 | 1249191.3494 | 2602710.1971 | 1249188.126 | 2602711.9202 | 1249184.3911 | 2602712.2539 | 1249180.9223 | 2602712.5724 | 1249177.8205 | 2602711.1026 | 1249172.3051 | 2602710.8034 | 1249166.2011 | 2602710.6024 | 1249159.6968 | 2602710.7419 | 1249158.1394
2 | 2602717.3743 | 1249118.9757 | 2602714.1021 | 1249133.6038 | 2602713.4249 | 1249137.8863
3 | 2602673.6246 | 1249198.8135 | 2602676.4747 | 1249199.007 | 2602680.242 | 1249199.0198 | 2602684.0698 | 1249199.0103 | 2602688.1014 | 1249199.001 | 2602692.1029 | 1249199.0028 | 2602695.8928 | 1249199.2268 | 2602700.3631 | 1249197.3498 | 2602704.8036 | 1249194.8057 | 2602706.394 | 1249193.1592
4 | 2602720.2995 | 1249102.1975 | 2602719.497 | 1249107.2003 | 2602717.7031 | 1249117.5062 | 2602717.3743 | 1249118.9757
5 | 2602667.8594 | 1249201.1268 | 2602670.3062 | 1249199.6047 | 2602673.5077 | 1249198.8056 | 2602673.6246 | 1249198.8135
6 | 2602720.2995 | 1249102.1975 | 2602702.399 | 1249101.0999
7 | 2602723.403 | 1249084.4986 | 2602721.3973 | 1249095.5048 | 2602720.2995 | 1249102.1975
8 | 2602658.8386 | 1249198.2655 | 2602661.4506 | 1249198.7892 | 2602663.4737 | 1249199.4349 | 2602665.557 | 1249200.4031 | 2602667.8594 | 1249201.1268
9 | 2602723.403 | 1249084.4986 | 2602722.8002 | 1249081.6965 | 2602722.7847 | 1249081.5578
10 | 2602723.403 | 1249084.4986 | 2602732.2006 | 1249097.5501
11 | 2602661.2587 | 1249188.6492 | 2602660.0335 | 1249193.563 | 2602658.8386 | 1249198.2655
12 | 2602661.2587 | 1249188.6492 | 2602661.3364 | 1249183.5571 | 2602660.4775 | 1249179.6876 | 2602659.1164 | 1249167.2011 | 2602658.056 | 1249157.739
13 | 2602661.2587 | 1249188.6492 | 2602654.9016 | 1249189.0022 | 2602653.4805 | 1249188.3796
14 | 2602658.056 | 1249157.739 | 2602652.9003 | 1249155.6021 | 2602652.0024 | 1249154.501 | 2602648.397 | 1249146.5054 | 2602643.6974 | 1249137.2974 | 2602639.3975 | 1249129.1014 | 2602633.8971 | 1249121.0049 | 2602629.6036 | 1249115.4995 | 2602625.2042 | 1249110.2053 | 2602618.6008 | 1249103.7984 | 2602613.2376 | 1249099.5433
15 | 2602658.056 | 1249157.739 | 2602657.5296 | 1249135.6357 | 2602655.6758 | 1249127.7076 | 2602653.2169 | 1249122.1251 | 2602652.4601 | 1249120.2087
16 | 2602625.2975 | 1249139.0017 | 2602627.8023 | 1249143.2054 | 2602632.004 | 1249151.5015 | 2602637.2992 | 1249162.5998 | 2602642.2023 | 1249172.5973 | 2602646.4041 | 1249180.6042 | 2602648.4032 | 1249184.2964 | 2602649.8973 | 1249185.9981 | 2602652.003 | 1249187.6001 | 2602653.3013 | 1249188.3011 | 2602653.4805 | 1249188.3796
17 | 2602718.5012 | 1249071.5992 | 2602719.4974 | 1249072.5002 | 2602720.6971 | 1249074.2018 | 2602721.9042 | 1249076.2037 | 2602722.4994 | 1249079.0057 | 2602722.7847 | 1249081.5578
18 | 2602718.5012 | 1249071.5992 | 2602719.8989 | 1249069.4985 | 2602721.1005 | 1249066.8973 | 2602722.9539 | 1249061.5712
19 | 2602718.5012 | 1249071.5992 | 2602716.9012 | 1249070.1976 | 2602713.8972 | 1249068.3061 | 2602704.9452 | 1249062.7931
20 | 2602722.9539 | 1249061.5712 | 2602725.901 | 1249053.1017 | 2602729.4005 | 1249044.4977 | 2602729.9983 | 1249042.6012
21 | 2602704.9452 | 1249062.7931 | 2602704.3037 | 1249062.3981 | 2602695.9028 | 1249057.3022 | 2602694.2137 | 1249056.3135
22 | 2602501.4916 | 1248900.4281 | 2602493.4025 | 1248893.6996 | 2602486.1345 | 1248886.581 | 2602478.6778 | 1248879.2733 | 2602474.2778 | 1248875.0465 | 2602470.2554 | 1248870.1529 | 2602465.0935 | 1248864.0802 | 2602457.4858 | 1248856.7613 | 2602456.8935 | 1248856.2674
23 | 2602526.8356 | 1248920.7494 | 2602511.6002 | 1248908.1052 | 2602502.8974 | 1248901.5975 | 2602501.4916 | 1248900.4281
24 | 2602408.7997 | 1248821.4337 | 2602418.5984 | 1248827.4047 | 2602426.1995 | 1248832.4999 | 2602432.6003 | 1248837.2055 | 2602437.7026 | 1248841.3991 | 2602449.6286 | 1248850.2095 | 2602456.8935 | 1248856.2674
25 | 2602535.3975 | 1248928.506 | 2602528.7031 | 1248922.2992 | 2602526.8356 | 1248920.7494
26 | 2602408.7997 | 1248821.4337 | 2602401.199 | 1248816.8021 | 2602392.503 | 1248811.9067 | 2602384.4031 | 1248807.6008 | 2602370.2155 | 1248801.1621
27 | 2602535.3975 | 1248928.506 | 2602537.0968 | 1248927.3059 | 2602537.7992 | 1248926.8059
28 | 2602357.9847 | 1248795.0052 | 2602360.6012 | 1248796.5066 | 2602368.0973 | 1248800.2008 | 2602370.2155 | 1248801.1621
29 | 2602537.7992 | 1248926.8059 | 2602538.8036 | 1248926.2059 | 2602540.2007 | 1248925.406 | 2602542.7983 | 1248924.7066 | 2602547.9026 | 1248923.7971 | 2602552.1989 | 1248923.1985 | 2602557.801 | 1248923.7011 | 2602561.5005 | 1248923.8028 | 2602565.804 | 1248924.2048 | 2602572.5985 | 1248925.7976 | 2602579.4984 | 1248928.102 | 2602586.7984 | 1248930.5066 | 2602588.4435 | 1248931.1984
30 | 2602537.7992 | 1248926.8059 | 2602537.8003 | 1248924.2042 | 2602536.903 | 1248921.302 | 2602532.2029 | 1248912.5055 | 2602529.7969 | 1248906.5006 | 2602528.9983 | 1248902.2976 | 2602528.1023 | 1248896.3045 | 2602527.1979 | 1248892.3015 | 2602525.9993 | 1248887.7981 | 2602523.7972 | 1248881.5043 | 2602521.7984 | 1248876.8004 | 2602519.203 | 1248872.1964 | 2602516.9014 | 1248869.2046 | 2602513.0977 | 1248865.1004 | 2602506.1997 | 1248858.1042 | 2602496.4036 | 1248847.9048 | 2602488.1016 | 1248839.596 | 2602478.8033 | 1248830.6976 | 2602468.9012 | 1248820.8984 | 2602460.1992 | 1248812.2004 | 2602452.403 | 1248804.0032 | 2602447.2033 | 1248797.697 | 2602441.7021 | 1248790.2011 | 2602437.4991 | 1248783.9065 | 2602434.602 | 1248778.3017 | 2602433.003 | 1248774.0984 | 2602432.0889 | 1248771.2057
31 | 2602357.9847 | 1248795.0052 | 2602353.0978 | 1248792.201 | 2602345.7343 | 1248787.5182
32 | 2602618.3143 | 1248945.4397 | 2602610.6975 | 1248941.7018 | 2602599.3974 | 1248935.8043 | 2602588.4435 | 1248931.1984
33 | 2602430.0024 | 1248762.8011 | 2602430.5 | 1248764.6024 | 2602431.2987 | 1248768.7054 | 2602432.0889 | 1248771.2057
34 | 2602579.2009 | 1249006.4967 | 2602570.2018 | 1248987.2027 | 2602563.6757 | 1248974.831
35 | 2602579.2009 | 1249006.4967 | 2602576.3996 | 1249007.0959 | 2602575.403 | 1249007.1066 | 2602574.2025 | 1249007.1061 | 2602573.4023 | 1249006.9057 | 2602572.3002 | 1249006.4049 | 2602570.6999 | 1249005.6037 | 2602569.0996 | 1249004.7024 | 2602566.6013 | 1249002.9002 | 2602561.801 | 1248999.1958 | 2602548.5993 | 1248990.9961 | 2602541.1873 | 1248986.0745
36 | 2602582.0529 | 1249011.1343 | 2602579.2009 | 1249006.4967
37 | 2602343.425 | 1248786.0496 | 2602345.7343 | 1248787.5182
38 | 2602508.2365 | 1248798.801 | 2602500.7973 | 1248794.0053 | 2602484.6023 | 1248782.4979
39 | 2602508.2365 | 1248798.801 | 2602727.8562 | 1248728.1579
40 | 2602447.9501 | 1248761.9966 | 2602453.869 | 1248763.3776 | 2602460.5349 | 1248766.1932 | 2602470.4083 | 1248772.4123 | 2602484.6023 | 1248782.4979
41 | 2602430.0024 | 1248762.8011 | 2602447.9501 | 1248761.9966
42 | 2602430.0024 | 1248762.8011 | 2602419.2133 | 1248761.6961 | 2602410.667 | 1248759.9916 | 2602403.3217 | 1248756.5865 | 2602396.9585 | 1248752.4954
43 | 2602380.0012 | 1248741.735 | 2602391.7801 | 1248749.1661 | 2602396.9585 | 1248752.4954
44 | 2602603.4504 | 1249026.2136 | 2602607.7983 | 1249029.6015 | 2602611.0971 | 1249031.1039 | 2602616.404 | 1249032.7962 | 2602624.3006 | 1249034.5007 | 2602631.0104 | 1249035.7183
45 | 2602589.6425 | 1249013.4185 | 2602590.1455 | 1249013.6504 | 2602591.9341 | 1249015.4079 | 2602594.1605 | 1249017.6102 | 2602595.798 | 1249019.501 | 2602599.1036 | 1249022.6044 | 2602602.4018 | 1249025.3965 | 2602603.4504 | 1249026.2136
46 | 2602631.0104 | 1249035.7183 | 2602634.802 | 1249036.4064 | 2602647.0999 | 1249038.9023 | 2602648.7539 | 1249039.3191
47 | 2602582.0529 | 1249011.1343 | 2602584.2046 | 1249011.3131 | 2602586.2655 | 1249011.9143 | 2602587.9489 | 1249012.6377 | 2602589.6425 | 1249013.4185
48 | 2602648.7539 | 1249039.3191 | 2602657.397 | 1249041.4973 | 2602665.2845 | 1249044.039
49 | 2602582.0529 | 1249011.1343 | 2602584.0867 | 1249014.5329
50 | 2602668.6998 | 1249045.1396 | 2602665.2845 | 1249044.039
51 | 2602668.6998 | 1249045.1396 | 2602668.9017 | 1249045.2047 | 2602677.8018 | 1249048.3996 | 2602688.2038 | 1249052.7959 | 2602688.2038 | 1249052.7959
52 | 2602541.1873 | 1248986.0745 | 2602536.4017 | 1248982.8969 | 2602524.2039 | 1248975.098 | 2602519.2693 | 1248971.9231
53 | 2602639.2084 | 1248955.0611 | 2602635.2003 | 1248953.2976 | 2602621.8996 | 1248947.199 | 2602618.3143 | 1248945.4397
54 | 2602639.2084 | 1248955.0611 | 2602650.1996 | 1248959.8972 | 2602661.1981 | 1248964.6051 | 2602662.4346 | 1248965.18
55 | 2602645.1491 | 1249105.0697 | 2602644.135 | 1249103.0978 | 2602634.7108 | 1249089.9853 | 2602627.4713 | 1249080.7145
56 | 2602652.4601 | 1249120.2087 | 2602651.1354 | 1249116.8542 | 2602648.533 | 1249111.6497 | 2602645.1491 | 1249105.0697
57 | 2602613.2376 | 1249099.5433 | 2602611.8005 | 1249098.4031 | 2602604.5021 | 1249092.8964 | 2602597.2035 | 1249087.5009 | 2602590.4033 | 1249082.1057 | 2602584.6986 | 1249074.8986 | 2602584.4305 | 1249074.6567
58 | 2602519.2693 | 1248971.9231 | 2602511.3042 | 1248966.7984 | 2602501.0754 | 1248960.0734
59 | 2602393.5131 | 1248969.7118 | 2602394.502 | 1248970.4983 | 2602403.5968 | 1248978.4959 | 2602412.2992 | 1248985.804 | 2602420.9038 | 1248992.3005 | 2602429.9888 | 1248998.0193
60 | 2602315.4962 | 1248893.9742 | 2602331.55 | 1248908.4341 | 2602349.0968 | 1248927.7977 | 2602357.7008 | 1248936.2064 | 2602366.403 | 1248944.2038 | 2602382.4035 | 1248959.3976 | 2602388.5997 | 1248965.8041 | 2602393.5131 | 1248969.7118
61 | 2602429.9888 | 1248998.0193 | 2602432.4978 | 1248999.5987 | 2602446.9 | 1249008.1989 | 2602469.0996 | 1249020.9049 | 2602488.456 | 1249031.2663
62 | 2602315.4962 | 1248893.9742 | 2602319.0611 | 1248890.7402 | 2602322.6491 | 1248886.4165 | 2602326.1155 | 1248884.2275
63 | 2602488.456 | 1249031.2663 | 2602490.1975 | 1249032.1985 | 2602493.6021 | 1249033.3006 | 2602497.6029 | 1249035.1034 | 2602505.2028 | 1249042.5002 | 2602562.9668 | 1249098.911
64 | 2602326.1155 | 1248884.2275 | 2602330.336 | 1248884.5293 | 2602333.9671 | 1248885.965 | 2602337.4695 | 1248888.379 | 2602340.1821 | 1248890.713
65 | 2602326.1155 | 1248884.2275 | 2602327.431 | 1248879.6029 | 2602329.6668 | 1248877.1021 | 2602331.3287 | 1248875.0459 | 2602333.7305 | 1248872.7898 | 2602335.5962 | 1248870.678 | 2602337.3489 | 1248868.166 | 2602338.9579 | 1248865.8984 | 2602341.0729 | 1248863.7201 | 2602343.4745 | 1248862.1311 | 2602346.1324 | 1248861.4539 | 2602348.7825 | 1248861.6106 | 2602351.1984 | 1248862.1007
66 | 2602340.1821 | 1248890.713 | 2602341.2056 | 1248891.5936 | 2602345.2437 | 1248894.9862 | 2602349.297 | 1248898.0008 | 2602353.767 | 1248901.3614
67 | 2602351.1984 | 1248862.1007 | 2602353.1008 | 1248862.9019 | 2602356.6037 | 1248863.8039 | 2602359.9024 | 1248865.8064 | 2602363.7973 | 1248868.5986 | 2602370.6515 | 1248872.426 | 2602378.0559 | 1248878.5216 | 2602383.8682 | 1248882.5152
68 | 2602353.767 | 1248901.3614 | 2602358.6038 | 1248904.9978 | 2602363.0296 | 1248908.4118
69 | 2602411.6198 | 1248900.873 | 2602409.3888 | 1248899.314 | 2602396.202 | 1248890.492 | 2602386.6533 | 1248884.4288 | 2602383.8682 | 1248882.5152
70 | 2602085.8388 | 1248788.2571 | 2602094.0003 | 1248789.8053 | 2602098.1887 | 1248791.3545
71 | 2602085.8388 | 1248788.2571 | 2602057.7004 | 1248782.8997 | 2602053.6011 | 1248781.2973 | 2602048.8 | 1248778.6051 | 2602046.4978 | 1248776.6031 | 2602042.3993 | 1248772.4991 | 2602026.9036 | 1248756.4058 | 2602020.2007 | 1248750.8 | 2602001.7975 | 1248736.2958 | 2601999.5046 | 1248734.4007
72 | 2602343.425 | 1248786.0496 | 2602339.1028 | 1248783.301 | 2602333.6 | 1248779.5965 | 2602326.104 | 1248775.5021 | 2602321.1972 | 1248773.0987 | 2602315.8975 | 1248771.2066 | 2602315.8975 | 1248771.2066
73 | 2602315.8975 | 1248771.2066 | 2602313.4396 | 1248770.4946
74 | 2602313.4396 | 1248770.4946 | 2602293.8 | 1248764.8053 | 2602288.4078 | 1248763.2713
75 | 2602288.4078 | 1248763.2713 | 2602277.5985 | 1248760.1963 | 2602272.4594 | 1248758.9281
76 | 2602265.298 | 1248757.2372 | 2602267.8971 | 1248757.8022 | 2602272.4594 | 1248758.9281
77 | 2602265.298 | 1248757.2372 | 2602261.9026 | 1248756.4992 | 2602258.1197 | 1248755.8051
78 | 2602241.2822 | 1248753.6839 | 2602247.8974 | 1248754.3037 | 2602254.7981 | 1248755.1957 | 2602258.1197 | 1248755.8051
79 | 2602241.2822 | 1248753.6839 | 2602236.104 | 1248753.1987 | 2602225.1033 | 1248752.5053 | 2602224.0794 | 1248752.5312
80 | 2602212.7829 | 1248752.817 | 2602224.0794 | 1248752.5312
81 | 2602212.7829 | 1248752.817 | 2602209.504 | 1248752.8999 | 2602197.597 | 1248752.9957 | 2602187.8041 | 1248752.9033 | 2602182.3982 | 1248752.5011 | 2602173.2027 | 1248749.7961 | 2602170.8037 | 1248748.602
82 | 2602168.5978 | 1248747.5041 | 2602170.8037 | 1248748.602
83 | 2602168.5978 | 1248747.5041 | 2602167.4042 | 1248749.2048 | 2602165.9012 | 1248750.5051 | 2602164.8969 | 1248750.8049 | 2602161.8993 | 1248751.2041
84 | 2602147.3693 | 1248748.0478 | 2602159.0982 | 1248750.7028 | 2602161.8993 | 1248751.2041
85 | 2602147.3693 | 1248748.0478 | 2602146.7014 | 1248747.8966 | 2602134.8031 | 1248744.6015 | 2602125.2982 | 1248741.5962 | 2602120.2928 | 1248739.6967
86 | 2601970.2035 | 1248698.5057 | 2601970.1973 | 1248694.303 | 2601970.8028 | 1248689.7003 | 2601972.1025 | 1248686.4986 | 2601973.5985 | 1248683.4972 | 2601976.0986 | 1248680.5961 | 2601979.097 | 1248678.0065 | 2601983.7038 | 1248675.1062 | 2601988.3026 | 1248673.2064 | 2601992.9012 | 1248672.1962 | 2601998.5038 | 1248671.9979 | 2602002.7999 | 1248672.2994 | 2602010.1986 | 1248675.0036 | 2602014.4717 | 1248676.4392 | 2602029.7975 | 1248681.6032 | 2602039.4011 | 1248683.6966 | 2602047.2004 | 1248684.6998 | 2602055.8983 | 1248685.4032 | 2602067.2392 | 1248685.3069
87 | 2602067.2392 | 1248685.3069 | 2602067.7042 | 1248694.6131 | 2602070.9698 | 1248705.9325 | 2602073.1428 | 1248710.4362 | 2602078.426 | 1248716.6419 | 2602083.7176 | 1248720.5129 | 2602091.1834 | 1248725.0183 | 2602104.0998 | 1248732.2051 | 2602108.0948 | 1248734.1027
88 | 2601970.2035 | 1248698.5057 | 2601942.9475 | 1248586.6496
89 | 2601970.2035 | 1248698.5057 | 2601970.2029 | 1248700.4959 | 2601970.9038 | 1248704.2986 | 2601972.3974 | 1248708.6018 | 2601975.099 | 1248713.4058 | 2601977.8989 | 1248717.3981 | 2601983.0996 | 1248722.2029 | 2601994.3019 | 1248730.1005 | 2601999.5046 | 1248734.4007
90 | 2602120.2928 | 1248739.6967 | 2602118.2017 | 1248738.9032 | 2602108.0948 | 1248734.1027
91 | 2602477.5111 | 1248944.7231 | 2602477.798 | 1248944.904 | 2602488.5013 | 1248951.8017 | 2602499.899 | 1248959.3 | 2602501.0754 | 1248960.0734
92 | 2602716.6041 | 1248991.7025 | 2602721.6995 | 1248993.8061 | 2602729.6034 | 1248996.2001 | 2602737.0016 | 1248998.1047 | 2602744.2036 | 1248999.998 | 2602752.5003 | 1249001.8029 | 2602758.6985 | 1249002.7063 | 2602763.5984 | 1249003.0977 | 2602768.7023 | 1249002.9999 | 2602778.1026 | 1249002.1036 | 2602782.7429 | 1249001.6778
93 | 2602716.6041 | 1248991.7025 | 2602713.498 | 1248998.5055 | 2602712.9007 | 1249000.3064 | 2602712.499 | 1249003.7973 | 2602712.8 | 1249006.099 | 2602713.4361 | 1249008.0903
94 | 2602716.6041 | 1248991.7025 | 2602714.8981 | 1248991.0013 | 2602706.6022 | 1248987.2063 | 2602697.8008 | 1248982.5994 | 2602687.7314 | 1248977.4484
95 | 2602732.5017 | 1249034.6588 | 2602732.8029 | 1249033.7034 | 2602733.5973 | 1249030.0014 | 2602733.101 | 1249025.5984 | 2602731.9015 | 1249023.3964 | 2602729.0037 | 1249020.1041 | 2602722.7014 | 1249015.5984 | 2602716.3988 | 1249011.8042 | 2602714.7007 | 1249010.3025 | 2602713.5992 | 1249008.6009 | 2602713.4361 | 1249008.0903
96 | 2602662.4346 | 1248965.18 | 2602674.0987 | 1248970.6035 | 2602685.0968 | 1248976.1007 | 2602687.7314 | 1248977.4484
97 | 2602732.5017 | 1249034.6588 | 2602729.9983 | 1249042.6012
98 | 2602688.2038 | 1249052.7959 | 2602694.2137 | 1249056.3135
99 | 2602557.3347 | 1249050.2336 | 2602562.1022 | 1249054.9985 | 2602568.2004 | 1249060.2044 | 2602576.5024 | 1249067.5015 | 2602584.4305 | 1249074.6567
100 | 2602530.8346 | 1249024.485 | 2602540.7972 | 1249033.9983 | 2602553.0988 | 1249046 | 2602557.3347 | 1249050.2336
101 | 2602530.8346 | 1249024.485 | 2602529.8012 | 1249023.4981 | 2602527.3157 | 1249021.4142
102 | 2602527.3157 | 1249021.4142 | 2602515.4987 | 1249011.5067 | 2602505.8001 | 1249003.6977 | 2602497.6033 | 1248997.3013 | 2602488.5982 | 1248991.8052 | 2602481.6011 | 1248987.3995 | 2602476.6552 | 1248984.7
103 | 2602386.9313 | 1248926.2012 | 2602387.1354 | 1248926.3463
104 | 2602387.1354 | 1248926.3463 | 2602388.9015 | 1248927.6019 | 2602399.3027 | 1248935.1997 | 2602410.9744 | 1248943.7902
105 | 2602386.9313 | 1248926.2012 | 2602379.9042 | 1248921.2054 | 2602368.5973 | 1248912.7066 | 2602363.0296 | 1248908.4118
106 | 2602435.649 | 1248917.0024 | 2602449.4996 | 1248927.0033 | 2602454.3048 | 1248930.0523
107 | 2602455.9277 | 1248931.082 | 2602454.3048 | 1248930.0523
108 | 2602411.6198 | 1248900.873 | 2602419.7524 | 1248906.556 | 2602435.649 | 1248917.0024 | 2602435.649 | 1248917.0024
109 | 2602477.5111 | 1248944.7231 | 2602463.9998 | 1248936.2039 | 2602455.9277 | 1248931.082

## bus_geodata
| x | y | coords
0 | 2602710.7419 | 1249158.1394
1 | 2602713.4249 | 1249137.8863
2 | 2602706.394 | 1249193.1592
3 | 2602717.3743 | 1249118.9757
4 | 2602673.6246 | 1249198.8135
5 | 2602720.2995 | 1249102.1975
6 | 2602667.8594 | 1249201.1268
7 | 2602702.399 | 1249101.0999
8 | 2602723.403 | 1249084.4986
9 | 2602658.8386 | 1249198.2655
10 | 2602661.2587 | 1249188.6492
11 | 2602658.056 | 1249157.739
12 | 2602653.4805 | 1249188.3796
13 | 2602732.2006 | 1249097.5501
14 | 2602722.7847 | 1249081.5578
15 | 2602718.5012 | 1249071.5992
16 | 2602722.9539 | 1249061.5712
17 | 2602704.9452 | 1249062.7931
18 | 2602501.4916 | 1248900.4281
19 | 2602456.8935 | 1248856.2674
20 | 2602526.8356 | 1248920.7494
21 | 2602408.7997 | 1248821.4337
22 | 2602535.3975 | 1248928.506
23 | 2602370.2155 | 1248801.1621
24 | 2602537.7992 | 1248926.8059
25 | 2602357.9847 | 1248795.0052
26 | 2602588.4435 | 1248931.1984
27 | 2602432.0889 | 1248771.2057
28 | 2602563.6757 | 1248974.831
29 | 2602579.2009 | 1249006.4967
30 | 2602345.7343 | 1248787.5182
31 | 2602508.2365 | 1248798.801
32 | 2602484.6023 | 1248782.4979
33 | 2602727.8562 | 1248728.1579
34 | 2602447.9501 | 1248761.9966
35 | 2602430.0024 | 1248762.8011
36 | 2602396.9585 | 1248752.4954
37 | 2602603.4504 | 1249026.2136
38 | 2602631.0104 | 1249035.7183
39 | 2602589.6425 | 1249013.4185
40 | 2602648.7539 | 1249039.3191
41 | 2602582.0529 | 1249011.1343
42 | 2602665.2845 | 1249044.039
43 | 2602584.0867 | 1249014.5329
44 | 2602668.6998 | 1249045.1396
45 | 2602541.1873 | 1248986.0745
46 | 2602380.0012 | 1248741.735
47 | 2602618.3143 | 1248945.4397
48 | 2602639.2084 | 1248955.0611
49 | 2602627.4713 | 1249080.7145
50 | 2602645.1491 | 1249105.0697
51 | 2602652.4601 | 1249120.2087
52 | 2602613.2376 | 1249099.5433
53 | 2602519.2693 | 1248971.9231
54 | 2602393.5131 | 1248969.7118
55 | 2602429.9888 | 1248998.0193
56 | 2602315.4962 | 1248893.9742
57 | 2602488.456 | 1249031.2663
58 | 2602326.1155 | 1248884.2275
59 | 2602562.9668 | 1249098.911
60 | 2602340.1821 | 1248890.713
61 | 2602351.1984 | 1248862.1007
62 | 2602353.767 | 1248901.3614
63 | 2602383.8682 | 1248882.5152
64 | 2602098.1887 | 1248791.3545
65 | 2602085.8388 | 1248788.2571
66 | 2602343.425 | 1248786.0496
67 | 2602315.8975 | 1248771.2066
68 | 2602313.4396 | 1248770.4946
69 | 2602288.4078 | 1248763.2713
70 | 2602272.4594 | 1248758.9281
71 | 2602265.298 | 1248757.2372
72 | 2602258.1197 | 1248755.8051
73 | 2602241.2822 | 1248753.6839
74 | 2602224.0794 | 1248752.5312
75 | 2602212.7829 | 1248752.817
76 | 2602170.8037 | 1248748.602
77 | 2602168.5978 | 1248747.5041
78 | 2602161.8993 | 1248751.2041
79 | 2602147.3693 | 1248748.0478
80 | 2602067.2392 | 1248685.3069
81 | 2601970.2035 | 1248698.5057
82 | 2602108.0948 | 1248734.1027
83 | 2601999.5046 | 1248734.4007
84 | 2601942.9475 | 1248586.6496
85 | 2602120.2928 | 1248739.6967
86 | 2602625.2975 | 1249139.0017
87 | 2602501.0753 | 1248960.0734
88 | 2602782.7429 | 1249001.6778
89 | 2602716.6041 | 1248991.7025
90 | 2602713.4361 | 1249008.0903
91 | 2602687.7314 | 1248977.4484
92 | 2602732.5017 | 1249034.6588
93 | 2602662.4346 | 1248965.18
94 | 2602729.9983 | 1249042.6012
95 | 2602694.2137 | 1249056.3135
96 | 2602688.2038 | 1249052.7959
97 | 2602584.4305 | 1249074.6567
98 | 2602557.3347 | 1249050.2336
99 | 2602530.8346 | 1249024.485
100 | 2602527.3157 | 1249021.4142
101 | 2602387.1354 | 1248926.3463
102 | 2602386.9313 | 1248926.2012
103 | 2602410.9744 | 1248943.7902
104 | 2602363.0296 | 1248908.4118
105 | 2602476.6552 | 1248984.7
106 | 2602454.3048 | 1248930.0523
107 | 2602435.649 | 1248917.0024
108 | 2602455.9277 | 1248931.082
109 | 2602411.6198 | 1248900.873
110 | 2602477.5111 | 1248944.7231
111 | 2602579.2009 | 1249006.4967

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98478 | -0.29135 | 0.0024027 | 0.00060217
1 | 0.98525 | -0.28228 | 0.0019077 | 0.00047811
2 | 0.98402 | -0.30616 | 0.00086063 | 0.0002157
3 | 0.98573 | -0.27305 | 0.0016669 | 0.00041776
4 | 0.98334 | -0.3195 | 0.0017588 | 0.0004408
5 | 0.98617 | -0.26441 | 0 | 0
6 | 0.98323 | -0.32174 | 0 | 0
7 | 0.98614 | -0.265 | 0.0018583 | 0.00046573
8 | 0.98667 | -0.25471 | 0 | 0
9 | 0.98305 | -0.3251 | 0 | 0
10 | 0.98287 | -0.32862 | 0 | 0
11 | 0.98238 | -0.33821 | 0 | 0
12 | 0.98286 | -0.32899 | 0.00090073 | 0.00022575
13 | 0.98663 | -0.25556 | 0.0030216 | 0.00075728
14 | 0.98676 | -0.25292 | 0.0016999 | 0.00042603
15 | 0.98712 | -0.24594 | 0 | 0
16 | 0.9868 | -0.25214 | 0.0019494 | 0.00048856
17 | 0.98785 | -0.2318 | 0.0015684 | 0.00039309
18 | 0.97938 | -0.39622 | 0.0044032 | 0.0011036
19 | 0.97766 | -0.4299 | 0.0022006 | 0.00055151
20 | 0.97989 | -0.38624 | 0.0011921 | 0.00029877
21 | 0.97615 | -0.45947 | 0.00061855 | 0.00015502
22 | 0.98008 | -0.38256 | 0 | 0
23 | 0.97507 | -0.48072 | 0.00082167 | 0.00020593
24 | 0.98013 | -0.38163 | 0 | 0
25 | 0.97474 | -0.4872 | 0.00080717 | 0.0002023
26 | 0.98122 | -0.36037 | 0.0027434 | 0.00068757
27 | 0.97839 | -0.41585 | 0.0009747 | 0.00024428
28 | 0.99493 | -0.096131 | 0.0008975 | 0.00022493
29 | 0.99496 | -0.095574 | 0 | 0
30 | 0.9744 | -0.49378 | 0.00078147 | 0.00019586
31 | 0.97807 | -0.42201 | 0.00059585 | 0.00014933
32 | 0.97812 | -0.42117 | 0.0019826 | 0.00049689
33 | 0.97786 | -0.42621 | 0.00099656 | 0.00024976
34 | 0.97826 | -0.4184 | 0 | 0
35 | 0.97832 | -0.41723 | 0 | 0
36 | 0.97815 | -0.42058 | 0.0027915 | 0.00069963
37 | 0.99325 | -0.1281 | 0.0013611 | 0.00034113
38 | 0.99172 | -0.15743 | 0.0020522 | 0.00051432
39 | 0.99424 | -0.10923 | 0.0012374 | 0.00031013
40 | 0.9908 | -0.17508 | 0.00096627 | 0.00024217
41 | 0.99466 | -0.10115 | 0 | 0
42 | 0.98993 | -0.19172 | 0.0038893 | 0.00097474
43 | 0.99466 | -0.10127 | 0.0017955 | 0.00045
44 | 0.98976 | -0.19508 | 0.0017945 | 0.00044974
45 | 0.99736 | -0.049953 | 0.0016133 | 0.00040432
46 | 0.9781 | -0.42146 | 0.0024158 | 0.00060545
47 | 0.98195 | -0.34613 | 0.0015243 | 0.00038202
48 | 0.98247 | -0.33593 | 0.0019616 | 0.00049161
49 | 0.98213 | -0.34319 | 0.0021005 | 0.00052643
50 | 0.98219 | -0.34205 | 0.0010476 | 0.00026255
51 | 0.98224 | -0.34109 | 0.0010034 | 0.00025146
52 | 0.98149 | -0.35573 | 0.0015783 | 0.00039557
53 | 0.99879 | -0.022822 | 0.0016011 | 0.00040128
54 | 0.99427 | -0.11031 | 0.0026 | 0.00065162
55 | 0.99403 | -0.11499 | 0.00217 | 0.00054386
56 | 0.9951 | -0.094317 | 0 | 0
57 | 0.99381 | -0.11922 | 0.0012081 | 0.00030279
58 | 0.99521 | -0.092187 | 0 | 0
59 | 0.99359 | -0.12343 | 0.0023523 | 0.00058954
60 | 0.99505 | -0.095196 | 0.0013771 | 0.00034512
61 | 0.99584 | -0.079947 | 0.0014868 | 0.00037263
62 | 0.9949 | -0.098031 | 0.002037 | 0.00051052
63 | 0.99657 | -0.065945 | 0.0019256 | 0.00048259
64 | 0.97005 | -0.57985 | 0.00054409 | 0.00013636
65 | 0.97006 | -0.57972 | 0 | 0
66 | 0.97434 | -0.495 | 0.001545 | 0.00038722
67 | 0.97368 | -0.50806 | 0.001065 | 0.00026692
68 | 0.97363 | -0.50907 | 0.0010208 | 0.00025583
69 | 0.97313 | -0.51893 | 0.0010553 | 0.00026448
70 | 0.97283 | -0.52487 | 0.00093761 | 0.00023499
71 | 0.9727 | -0.52738 | 0.001229 | 0.00030802
72 | 0.97258 | -0.52972 | 0.0018653 | 0.00046749
73 | 0.97234 | -0.53456 | 0.0017213 | 0.0004314
74 | 0.97212 | -0.53894 | 0.0017326 | 0.00043423
75 | 0.97199 | -0.54144 | 0.0035128 | 0.00088038
76 | 0.97165 | -0.54814 | 0.00059936 | 0.00015021
77 | 0.97163 | -0.5485 | 0 | 0
78 | 0.97157 | -0.54968 | 0.00089749 | 0.00022493
79 | 0.97148 | -0.55161 | 0.00055227 | 0.00013841
80 | 0.97088 | -0.56341 | 0 | 0
81 | 0.9703 | -0.57502 | 0 | 0
82 | 0.97123 | -0.55646 | 0.00046705 | 0.00011705
83 | 0.97011 | -0.57866 | 0.0035206 | 0.00088235
84 | 0.97015 | -0.57799 | 0.0013909 | 0.00034859
85 | 0.97131 | -0.55499 | 0.00051482 | 0.00012903
86 | 0.98276 | -0.33076 | 0.0017092 | 0.00042837
87 | 1 | 0 | -0.15709 | -0.039751
88 | 0.98448 | -0.29705 | 0.0017056 | 0.00042746
89 | 0.98458 | -0.29497 | 0 | 0
90 | 0.98504 | -0.28624 | 0.0014402 | 0.00036095
91 | 0.98377 | -0.31075 | 0.001098 | 0.00027519
92 | 0.986 | -0.26761 | 0.0016934 | 0.00042442
93 | 0.98307 | -0.32426 | 0.0023019 | 0.0005769
94 | 0.98623 | -0.26318 | 0.0016209 | 0.00040624
95 | 0.98843 | -0.22069 | 0.0028408 | 0.00071197
96 | 0.98876 | -0.21435 | 0.0011074 | 0.00027753
97 | 0.98109 | -0.36358 | 0.003268 | 0.00081903
98 | 0.98082 | -0.36891 | 0.0012526 | 0.00031394
99 | 0.98058 | -0.37346 | 0.0020021 | 0.00050178
100 | 0.98056 | -0.37387 | 0.0020952 | 0.00052512
101 | 0.99467 | -0.10252 | 0.0020394 | 0.00051112
102 | 0.99467 | -0.1025 | 0.0013532 | 0.00033914
103 | 0.99461 | -0.10371 | 0.0022821 | 0.00057195
104 | 0.99483 | -0.099525 | 0.0016122 | 0.00040406
105 | 0.98041 | -0.37695 | 0.0027065 | 0.0006783
106 | 0.99841 | -0.030519 | 0.0019699 | 0.0004937
107 | 0.99787 | -0.040941 | 0.0026913 | 0.00067449
108 | 0.99846 | -0.029573 | 0.0019526 | 0.00048938
109 | 0.99725 | -0.052836 | 0.0010027 | 0.0002513
110 | 0.99916 | -0.016155 | 0.0028477 | 0.0007137
111 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.024752 | -0.0062224 | 0.024763 | 0.006229 | 1.0725e-05 | 6.6038e-06 | 0.037407 | 0.037407 | 0.037407 | 0.98478 | -0.29135 | 0.98525 | -0.28228 | 10.2768
1 | 0.022349 | 0.0056202 | -0.022334 | -0.0056106 | 1.5806e-05 | 9.6464e-06 | 0.033777 | 0.033777 | 0.033777 | 0.98478 | -0.29135 | 0.98402 | -0.30616 | 9.2794
2 | -0.026671 | -0.0067071 | 0.026682 | 0.0067144 | 1.1763e-05 | 7.2821e-06 | 0.040288 | 0.040288 | 0.040288 | 0.98525 | -0.28228 | 0.98573 | -0.27305 | 11.0683
3 | 0.021473 | 0.0053949 | -0.021459 | -0.0053866 | 1.3659e-05 | 8.3036e-06 | 0.032476 | 0.032476 | 0.032476 | 0.98402 | -0.30616 | 0.98334 | -0.3195 | 8.9219
4 | -0.028349 | -0.0071321 | 0.028361 | 0.0071394 | 1.1703e-05 | 7.273e-06 | 0.042805 | 0.042805 | 0.042805 | 0.98573 | -0.27305 | 0.98617 | -0.26441 | 11.7595
5 | 0.019701 | 0.0049458 | -0.019698 | -0.0049445 | 2.0995e-06 | 1.2638e-06 | 0.029814 | 0.029814 | 0.029814 | 0.98334 | -0.3195 | 0.98323 | -0.32174 | 8.1908
6 | 0.0018583 | 0.00046554 | -0.0018583 | -0.00046573 | 5.272e-08 | -1.9439e-07 | 0.002804 | 0.002804 | 0.002804 | 0.98617 | -0.26441 | 0.98614 | -0.265 | 0.77034
7 | -0.030219 | -0.007605 | 0.030233 | 0.0076137 | 1.4018e-05 | 8.7418e-06 | 0.045609 | 0.045608 | 0.045609 | 0.98617 | -0.26441 | 0.98667 | -0.25471 | 12.5298
8 | 0.019698 | 0.0049445 | -0.019695 | -0.0049426 | 3.1577e-06 | 1.9008e-06 | 0.029814 | 0.029814 | 0.029814 | 0.98323 | -0.32174 | 0.98305 | -0.3251 | 8.1908
9 | -0.033255 | -0.0083709 | 0.033258 | 0.0083726 | 2.8366e-06 | 1.777e-06 | 0.050166 | 0.050165 | 0.050166 | 0.98667 | -0.25471 | 0.98676 | -0.25292 | 13.7817
10 | 0.0030217 | 0.00075716 | -0.0030216 | -0.00075728 | 1.2258e-07 | -1.2257e-07 | 0.0045571 | 0.0045571 | 0.0045571 | 0.98667 | -0.25471 | 0.98663 | -0.25556 | 1.252
11 | 0.019695 | 0.0049426 | -0.019692 | -0.0049406 | 3.3054e-06 | 1.9897e-06 | 0.029814 | 0.029814 | 0.029814 | 0.98305 | -0.3251 | 0.98287 | -0.32862 | 8.1908
12 | 0.017082 | 0.0042872 | -0.017074 | -0.0042826 | 7.8112e-06 | 4.6047e-06 | 0.025863 | 0.025863 | 0.025863 | 0.98287 | -0.32862 | 0.98238 | -0.33821 | 7.1053
13 | 0.0026101 | 0.0006534 | -0.0026101 | -0.00065348 | 4.6361e-08 | -7.0683e-08 | 0.0039513 | 0.0039513 | 0.0039513 | 0.98287 | -0.32862 | 0.98286 | -0.32899 | 1.0855
14 | 0.012922 | 0.0032427 | -0.012911 | -0.0032368 | 1.0786e-05 | 5.9533e-06 | 0.019574 | 0.019575 | 0.019575 | 0.98238 | -0.33821 | 0.98149 | -0.35573 | 5.3776
15 | 0.0041522 | 0.0010399 | -0.0041517 | -0.00104 | 5.6976e-07 | -1.2162e-07 | 0.0062891 | 0.0062893 | 0.0062893 | 0.98238 | -0.33821 | 0.98224 | -0.34109 | 1.7278
16 | 0.0017093 | 0.00042773 | -0.0017092 | -0.00042837 | 1.4426e-07 | -6.3565e-07 | 0.0025877 | 0.0025879 | 0.0025879 | 0.98286 | -0.32899 | 0.98276 | -0.33076 | 0.71097
17 | -0.034958 | -0.0087987 | 0.034969 | 0.008806 | 1.1673e-05 | 7.3274e-06 | 0.052729 | 0.052729 | 0.052729 | 0.98676 | -0.25292 | 0.98712 | -0.24594 | 14.486
18 | 0.063366 | 0.016077 | -0.063347 | -0.016065 | 1.8894e-05 | 1.181e-05 | 0.09559 | 0.09559 | 0.09559 | 0.98712 | -0.24594 | 0.9868 | -0.25214 | 13.1304
19 | -0.098335 | -0.024883 | 0.098402 | 0.024925 | 6.678e-05 | 4.2325e-05 | 0.14832 | 0.14832 | 0.14832 | 0.98712 | -0.24594 | 0.98785 | -0.2318 | 20.3734
20 | 0.061398 | 0.015576 | -0.061365 | -0.015556 | 3.2584e-05 | 2.0337e-05 | 0.09265 | 0.09265 | 0.09265 | 0.9868 | -0.25214 | 0.98623 | -0.26318 | 12.7267
21 | -0.09997 | -0.025318 | 0.10002 | 0.025352 | 5.3368e-05 | 3.3834e-05 | 0.15068 | 0.15068 | 0.15068 | 0.98785 | -0.2318 | 0.98843 | -0.22069 | 20.6979
22 | 0.029585 | 0.0074751 | -0.029537 | -0.0074454 | 4.7681e-05 | 2.9726e-05 | 0.044971 | 0.044972 | 0.044972 | 0.97938 | -0.39622 | 0.97766 | -0.4299 | 12.3548
23 | -0.033988 | -0.0085787 | 0.034004 | 0.0085882 | 1.6261e-05 | 9.5886e-06 | 0.051661 | 0.051661 | 0.051661 | 0.97938 | -0.39622 | 0.97989 | -0.38624 | 7.0963
24 | 0.027337 | 0.0068939 | -0.027298 | -0.0068699 | 3.8629e-05 | 2.3978e-05 | 0.041622 | 0.041623 | 0.041623 | 0.97766 | -0.4299 | 0.97615 | -0.45947 | 11.4348
25 | -0.035196 | -0.008887 | 0.035203 | 0.0088907 | 6.1951e-06 | 3.6736e-06 | 0.053471 | 0.053471 | 0.053471 | 0.97989 | -0.38624 | 0.98008 | -0.38256 | 7.345
26 | 0.026679 | 0.0067149 | -0.026652 | -0.0066981 | 2.7078e-05 | 1.6785e-05 | 0.04068 | 0.04068 | 0.04068 | 0.97615 | -0.45947 | 0.97507 | -0.48072 | 11.1758
27 | -0.035203 | -0.0088907 | 0.035204 | 0.0088916 | 1.5745e-06 | 9.3366e-07 | 0.053471 | 0.053471 | 0.053471 | 0.98008 | -0.38256 | 0.98013 | -0.38163 | 7.3449
28 | 0.025831 | 0.0064921 | -0.025823 | -0.0064872 | 7.9856e-06 | 4.94e-06 | 0.039426 | 0.039426 | 0.039426 | 0.97507 | -0.48072 | 0.97474 | -0.4872 | 10.8313
29 | -0.04498 | -0.011341 | 0.045025 | 0.011369 | 4.5817e-05 | 2.8001e-05 | 0.068312 | 0.068311 | 0.068312 | 0.98013 | -0.38163 | 0.98122 | -0.36037 | 9.3835
30 | 0.0097754 | 0.0024498 | -0.0097594 | -0.0024421 | 1.5911e-05 | 7.7595e-06 | 0.014841 | 0.014842 | 0.014842 | 0.98013 | -0.38163 | 0.97839 | -0.41585 | 4.0774
31 | 0.025016 | 0.0062849 | -0.025008 | -0.0062801 | 7.8558e-06 | 4.8488e-06 | 0.038194 | 0.038194 | 0.038194 | 0.97474 | -0.4872 | 0.9744 | -0.49378 | 10.4928
32 | -0.047769 | -0.012057 | 0.047801 | 0.012077 | 3.261e-05 | 2.0033e-05 | 0.072472 | 0.072472 | 0.072472 | 0.98122 | -0.36037 | 0.98195 | -0.34613 | 9.9549
33 | 0.0087847 | 0.0021978 | -0.0087842 | -0.0021975 | 5.8031e-07 | 2.6252e-07 | 0.013359 | 0.013359 | 0.013359 | 0.97839 | -0.41585 | 0.97832 | -0.41723 | 3.6701
34 | -0.0008975 | -0.00022493 | 0.00089752 | 0.00022449 | 2.3832e-08 | -4.4289e-07 | 0.0013423 | 0.0013421 | 0.0013423 | 0.99493 | -0.096131 | 0.99496 | -0.095574 | 0.36876
35 | -0.11863 | -0.030272 | 0.1189 | 0.030439 | 0.00026207 | 0.00016657 | 0.17762 | 0.17762 | 0.17762 | 0.99496 | -0.095574 | 0.99736 | -0.049953 | 24.3978
36 | 0.11774 | 0.030048 | -0.1177 | -0.030028 | 3.1694e-05 | 2.0143e-05 | 0.17627 | 0.17627 | 0.17627 | 0.99496 | -0.095574 | 0.99466 | -0.10115 | 24.2135
37 | 0.024226 | 0.0060842 | -0.024225 | -0.0060833 | 1.405e-06 | 8.651e-07 | 0.037 | 0.037 | 0.037 | 0.9744 | -0.49378 | 0.97434 | -0.495 | 10.165
38 | -0.0015926 | -0.00039633 | 0.0015927 | 0.00039601 | 6.3167e-08 | -3.2001e-07 | 0.0024219 | 0.0024218 | 0.0024219 | 0.97807 | -0.42201 | 0.97812 | -0.42117 | 0.66537
39 | 0.00099675 | 0.00024699 | -0.00099656 | -0.00024976 | 1.9882e-07 | -2.7675e-06 | 0.0015154 | 0.0015165 | 0.0015165 | 0.97807 | -0.42201 | 0.97786 | -0.42621 | 0.41661
40 | -0.0035753 | -0.00089289 | 0.0035757 | 0.00089266 | 4.7012e-07 | -2.3132e-07 | 0.005438 | 0.0054378 | 0.005438 | 0.97812 | -0.42117 | 0.97826 | -0.4184 | 1.4939
41 | -0.0035757 | -0.00089266 | 0.0035759 | 0.00089257 | 1.9861e-07 | -9.7785e-08 | 0.0054378 | 0.0054377 | 0.0054378 | 0.97826 | -0.4184 | 0.97832 | -0.41723 | 1.4939
42 | 0.0052082 | 0.001305 | -0.0052074 | -0.0013049 | 8.2884e-07 | 8.8277e-08 | 0.0079216 | 0.0079217 | 0.0079217 | 0.97832 | -0.41723 | 0.97815 | -0.42058 | 2.1763
43 | 0.0024159 | 0.00060526 | -0.0024158 | -0.00060545 | 1.0172e-07 | -1.8698e-07 | 0.0036751 | 0.0036752 | 0.0036752 | 0.97815 | -0.42058 | 0.9781 | -0.42146 | 1.0097
44 | 0.11316 | 0.028832 | -0.113 | -0.02873 | 0.00015985 | 0.00010154 | 0.1697 | 0.1697 | 0.1697 | 0.99325 | -0.1281 | 0.99172 | -0.15743 | 23.3101
45 | -0.11452 | -0.029173 | 0.11463 | 0.029239 | 0.0001044 | 6.6328e-05 | 0.17174 | 0.17174 | 0.17174 | 0.99325 | -0.1281 | 0.99424 | -0.10923 | 23.5901
46 | 0.11095 | 0.028216 | -0.11085 | -0.028156 | 9.4257e-05 | 5.9858e-05 | 0.16662 | 0.16662 | 0.16662 | 0.99172 | -0.15743 | 0.9908 | -0.17508 | 22.8871
47 | -0.11586 | -0.029549 | 0.11591 | 0.029578 | 4.5217e-05 | 2.8731e-05 | 0.17359 | 0.17359 | 0.17359 | 0.99424 | -0.10923 | 0.99466 | -0.10115 | 23.8445
48 | 0.10989 | 0.027914 | -0.1098 | -0.027858 | 8.798e-05 | 5.5864e-05 | 0.16517 | 0.16517 | 0.16517 | 0.9908 | -0.17508 | 0.98993 | -0.19172 | 22.6878
49 | 0.0017955 | 0.00044995 | -0.0017955 | -0.00045 | 1.0716e-08 | -4.455e-08 | 0.0026861 | 0.0026861 | 0.0026861 | 0.99466 | -0.10115 | 0.99466 | -0.10127 | 0.73794
50 | 0.10591 | 0.026883 | -0.10589 | -0.026872 | 1.7078e-05 | 1.0838e-05 | 0.15932 | 0.15932 | 0.15932 | 0.98993 | -0.19172 | 0.98976 | -0.19508 | 21.8848
51 | 0.1041 | 0.026422 | -0.104 | -0.026361 | 9.6412e-05 | 6.1165e-05 | 0.15662 | 0.15662 | 0.15662 | 0.98976 | -0.19508 | 0.98876 | -0.21435 | 21.5142
52 | -0.12051 | -0.030843 | 0.12067 | 0.030944 | 0.00015854 | 0.00010078 | 0.18002 | 0.18002 | 0.18002 | 0.99736 | -0.049953 | 0.99879 | -0.022822 | 24.7284
53 | -0.049326 | -0.012459 | 0.04935 | 0.012474 | 2.4122e-05 | 1.4855e-05 | 0.074781 | 0.074781 | 0.074781 | 0.98195 | -0.34613 | 0.98247 | -0.33593 | 10.2722
54 | -0.051311 | -0.012966 | 0.05134 | 0.012983 | 2.8718e-05 | 1.7737e-05 | 0.077752 | 0.077752 | 0.077752 | 0.98247 | -0.33593 | 0.98307 | -0.32426 | 10.6802
55 | -0.0021005 | -0.00052643 | 0.0021006 | 0.00052612 | 1.1442e-07 | -3.0805e-07 | 0.0031824 | 0.0031823 | 0.0031824 | 0.98213 | -0.34319 | 0.98219 | -0.34205 | 0.87429
56 | -0.0031482 | -0.00078867 | 0.0031483 | 0.00078855 | 1.4351e-07 | -1.211e-07 | 0.0047694 | 0.0047693 | 0.0047694 | 0.98219 | -0.34205 | 0.98224 | -0.34109 | 1.3103
57 | 0.011333 | 0.0028412 | -0.011328 | -0.002839 | 4.2385e-06 | 2.229e-06 | 0.017182 | 0.017182 | 0.017182 | 0.98149 | -0.35573 | 0.98109 | -0.36358 | 4.7203
58 | -0.12227 | -0.031345 | 0.1224 | 0.031432 | 0.00013546 | 8.6124e-05 | 0.18241 | 0.18241 | 0.18241 | 0.99879 | -0.022822 | 1 | 0 | 25.056
59 | 0.0057329 | 0.001435 | -0.0057316 | -0.0014348 | 1.2767e-06 | 2.1735e-07 | 0.0085792 | 0.0085794 | 0.0085794 | 0.99427 | -0.11031 | 0.99403 | -0.11499 | 2.357
60 | -0.0083329 | -0.0020866 | 0.0083393 | 0.0020893 | 6.347e-06 | 2.6493e-06 | 0.01247 | 0.01247 | 0.01247 | 0.99427 | -0.11031 | 0.9951 | -0.094317 | 3.4259
61 | 0.0035616 | 0.0008909 | -0.0035609 | -0.00089131 | 7.1698e-07 | -4.1301e-07 | 0.005331 | 0.0053313 | 0.0053313 | 0.99403 | -0.11499 | 0.99381 | -0.11922 | 1.4646
62 | -0.0083393 | -0.0020893 | 0.0083401 | 0.0020896 | 8.4603e-07 | 3.5295e-07 | 0.01247 | 0.01247 | 0.01247 | 0.9951 | -0.094317 | 0.99521 | -0.092187 | 3.4258
63 | 0.0023528 | 0.00058853 | -0.0023523 | -0.00058954 | 4.7131e-07 | -1.0105e-06 | 0.0035223 | 0.0035228 | 0.0035228 | 0.99381 | -0.11922 | 0.99359 | -0.12343 | 0.9678
64 | 0.010705 | 0.0026833 | -0.010704 | -0.0026825 | 1.5342e-06 | 7.7441e-07 | 0.016006 | 0.016006 | 0.016006 | 0.99521 | -0.092187 | 0.99505 | -0.095196 | 4.3974
65 | -0.019045 | -0.0047729 | 0.019056 | 0.0047795 | 1.1112e-05 | 6.6363e-06 | 0.028476 | 0.028476 | 0.028476 | 0.99521 | -0.092187 | 0.99584 | -0.079947 | 7.8231
66 | 0.0093266 | 0.0023374 | -0.0093254 | -0.0023368 | 1.2596e-06 | 5.819e-07 | 0.013947 | 0.013947 | 0.013947 | 0.99505 | -0.095196 | 0.9949 | -0.098031 | 3.8317
67 | -0.020543 | -0.0051522 | 0.020557 | 0.0051604 | 1.372e-05 | 8.2754e-06 | 0.030698 | 0.030697 | 0.030698 | 0.99584 | -0.079947 | 0.99657 | -0.065945 | 8.4334
68 | 0.0072884 | 0.0018263 | -0.0072878 | -0.0018261 | 5.1871e-07 | 1.8082e-07 | 0.010901 | 0.010901 | 0.010901 | 0.9949 | -0.098031 | 0.99483 | -0.099525 | 2.9947
69 | -0.022483 | -0.005643 | 0.022497 | 0.0056516 | 1.4065e-05 | 8.5679e-06 | 0.033573 | 0.033572 | 0.033573 | 0.99657 | -0.065945 | 0.99725 | -0.052836 | 9.2232
70 | -0.00054409 | -0.00013636 | 0.0005441 | 0.00013621 | 3.3362e-09 | -1.5555e-07 | 0.00083461 | 0.00083456 | 0.00083461 | 0.97005 | -0.57985 | 0.97006 | -0.57972 | 0.22929
71 | -0.0005441 | -0.00013621 | 0.00054412 | 0.00013493 | 2.7379e-08 | -1.2774e-06 | 0.00083456 | 0.00083409 | 0.00083456 | 0.97006 | -0.57972 | 0.97011 | -0.57866 | 0.22927
72 | 0.02268 | 0.0056961 | -0.022666 | -0.0056875 | 1.4125e-05 | 8.6491e-06 | 0.034641 | 0.034641 | 0.034641 | 0.97434 | -0.495 | 0.97368 | -0.50806 | 9.5168
73 | 0.021601 | 0.0054205 | -0.0216 | -0.0054199 | 1.0459e-06 | 6.3755e-07 | 0.033013 | 0.033013 | 0.033013 | 0.97368 | -0.50806 | 0.97363 | -0.50907 | 9.0696
74 | 0.020579 | 0.0051641 | -0.020569 | -0.0051582 | 9.6656e-06 | 5.8622e-06 | 0.031453 | 0.031454 | 0.031454 | 0.97363 | -0.50907 | 0.97313 | -0.51893 | 8.6411
75 | 0.019514 | 0.0048937 | -0.019508 | -0.0048904 | 5.52e-06 | 3.3275e-06 | 0.02984 | 0.02984 | 0.02984 | 0.97313 | -0.51893 | 0.97283 | -0.52487 | 8.1978
76 | 0.018571 | 0.0046554 | -0.018568 | -0.0046541 | 2.2267e-06 | 1.3337e-06 | 0.028406 | 0.028406 | 0.028406 | 0.97283 | -0.52487 | 0.9727 | -0.52738 | 7.8038
77 | 0.017339 | 0.0043461 | -0.017338 | -0.0043449 | 1.9316e-06 | 1.1454e-06 | 0.026526 | 0.026526 | 0.026526 | 0.9727 | -0.52738 | 0.97258 | -0.52972 | 7.2873
78 | 0.015472 | 0.0038774 | -0.015469 | -0.0038754 | 3.568e-06 | 2.0728e-06 | 0.023672 | 0.023672 | 0.023672 | 0.97258 | -0.52972 | 0.97234 | -0.53456 | 6.5033
79 | 0.013747 | 0.003444 | -0.013745 | -0.0034424 | 2.8626e-06 | 1.6182e-06 | 0.021038 | 0.021038 | 0.021038 | 0.97234 | -0.53456 | 0.97212 | -0.53894 | 5.7796
80 | 0.012012 | 0.0030081 | -0.012011 | -0.0030073 | 1.4325e-06 | 7.7669e-07 | 0.018386 | 0.018386 | 0.018386 | 0.97212 | -0.53894 | 0.97199 | -0.54144 | 5.0511
81 | 0.0084977 | 0.002127 | -0.008495 | -0.0021258 | 2.7074e-06 | 1.2041e-06 | 0.013008 | 0.013008 | 0.013008 | 0.97199 | -0.54144 | 0.97165 | -0.54814 | 3.5737
82 | 0.0078957 | 0.0019755 | -0.0078955 | -0.0019755 | 1.3508e-07 | 5.5929e-08 | 0.01209 | 0.01209 | 0.01209 | 0.97165 | -0.54814 | 0.97163 | -0.5485 | 3.3216
83 | 0.0078955 | 0.0019755 | -0.0078951 | -0.0019753 | 4.4607e-07 | 1.8471e-07 | 0.01209 | 0.012091 | 0.012091 | 0.97163 | -0.5485 | 0.97157 | -0.54968 | 3.3216
84 | 0.0069976 | 0.0017504 | -0.006997 | -0.0017501 | 6.4039e-07 | 2.257e-07 | 0.010716 | 0.010716 | 0.010716 | 0.97157 | -0.54968 | 0.97148 | -0.55161 | 2.944
85 | 0.0064447 | 0.0016117 | -0.0064436 | -0.0016114 | 1.0358e-06 | 3.1193e-07 | 0.0098701 | 0.0098702 | 0.0098702 | 0.97148 | -0.55161 | 0.97131 | -0.55499 | 2.7116
86 | 0.0054596 | 0.0013649 | -0.0054565 | -0.0013644 | 3.0136e-06 | 5.0986e-07 | 0.0083664 | 0.0083669 | 0.0083669 | 0.97088 | -0.56341 | 0.9703 | -0.57502 | 2.2986
87 | -0.0054596 | -0.0013649 | 0.0054614 | 0.0013652 | 1.804e-06 | 3.0431e-07 | 0.0083664 | 0.0083661 | 0.0083664 | 0.97088 | -0.56341 | 0.97123 | -0.55646 | 2.2985
88 | 0.0013911 | 0.00034729 | -0.0013909 | -0.00034859 | 1.9644e-07 | -1.2961e-06 | 0.0021328 | 0.0021334 | 0.0021334 | 0.9703 | -0.57502 | 0.97015 | -0.57799 | 0.58609
89 | 0.0040655 | 0.0010171 | -0.0040648 | -0.0010173 | 7.0446e-07 | -1.4606e-07 | 0.006234 | 0.0062342 | 0.0062342 | 0.9703 | -0.57502 | 0.97011 | -0.57866 | 1.7127
90 | -0.0059284 | -0.0014823 | 0.0059288 | 0.0014824 | 4.1523e-07 | 9.9589e-08 | 0.0090816 | 0.0090816 | 0.0090816 | 0.97123 | -0.55646 | 0.97131 | -0.55499 | 2.495
91 | 0.033033 | 0.0083192 | -0.033008 | -0.0083032 | 2.5496e-05 | 1.5949e-05 | 0.049168 | 0.049168 | 0.049168 | 1 | 0 | 0.99916 | -0.016155 | 13.5078
92 | -0.0017056 | -0.00042746 | 0.0017057 | 0.0004267 | 1.6879e-07 | -7.5333e-07 | 0.0025779 | 0.0025776 | 0.0025779 | 0.98448 | -0.29705 | 0.98458 | -0.29497 | 0.70823
93 | -0.056522 | -0.014309 | 0.056546 | 0.014324 | 2.37e-05 | 1.4728e-05 | 0.085474 | 0.085474 | 0.085474 | 0.98458 | -0.29497 | 0.98504 | -0.28624 | 11.7409
94 | 0.054816 | 0.013883 | -0.054775 | -0.013857 | 4.1504e-05 | 2.5744e-05 | 0.082896 | 0.082897 | 0.082897 | 0.98458 | -0.29497 | 0.98377 | -0.31075 | 11.3869
95 | -0.057986 | -0.014685 | 0.058038 | 0.014717 | 5.1923e-05 | 3.2312e-05 | 0.087649 | 0.087649 | 0.087649 | 0.98504 | -0.28624 | 0.986 | -0.26761 | 12.0398
96 | 0.053677 | 0.013582 | -0.053642 | -0.01356 | 3.4792e-05 | 2.1554e-05 | 0.081236 | 0.081236 | 0.081236 | 0.98377 | -0.31075 | 0.98307 | -0.32426 | 11.1588
97 | -0.059731 | -0.015142 | 0.059744 | 0.01515 | 1.2705e-05 | 7.9188e-06 | 0.090205 | 0.090205 | 0.090205 | 0.986 | -0.26761 | 0.98623 | -0.26318 | 12.3908
98 | -0.10286 | -0.026064 | 0.1029 | 0.026084 | 3.1352e-05 | 1.9887e-05 | 0.15496 | 0.15496 | 0.15496 | 0.98843 | -0.22069 | 0.98876 | -0.21435 | 21.2853
99 | 0.0080605 | 0.0020199 | -0.0080584 | -0.0020191 | 2.0452e-06 | 8.4827e-07 | 0.012225 | 0.012225 | 0.012225 | 0.98109 | -0.36358 | 0.98082 | -0.36891 | 3.3586
100 | 0.0068058 | 0.0017051 | -0.0068043 | -0.0017047 | 1.4772e-06 | 4.7918e-07 | 0.010325 | 0.010325 | 0.010325 | 0.98082 | -0.36891 | 0.98058 | -0.37346 | 2.8366
101 | 0.0048022 | 0.0012029 | -0.0048021 | -0.0012029 | 9.304e-08 | 6.0553e-10 | 0.007287 | 0.007287 | 0.007287 | 0.98058 | -0.37346 | 0.98056 | -0.37387 | 2.0019
102 | 0.0027069 | 0.00067776 | -0.0027065 | -0.0006783 | 3.9686e-07 | -5.3709e-07 | 0.0041075 | 0.0041077 | 0.0041077 | 0.98056 | -0.37387 | 0.98041 | -0.37695 | 1.1285
103 | -0.0043216 | -0.0010828 | 0.0043216 | 0.0010828 | 3.9258e-09 | -7.3857e-10 | 0.006465 | 0.006465 | 0.006465 | 0.99467 | -0.10252 | 0.99467 | -0.1025 | 1.7761
104 | 0.0022822 | 0.00057165 | -0.0022821 | -0.00057195 | 1.2912e-07 | -3.0076e-07 | 0.0034141 | 0.0034142 | 0.0034142 | 0.99467 | -0.10252 | 0.99461 | -0.10371 | 0.93797
105 | -0.0056748 | -0.0014219 | 0.0056756 | 0.001422 | 8.0531e-07 | 1.2856e-07 | 0.0084893 | 0.0084892 | 0.0084893 | 0.99467 | -0.1025 | 0.99483 | -0.099525 | 2.3322
106 | 0.026217 | 0.0065936 | -0.026204 | -0.0065855 | 1.3045e-05 | 8.0508e-06 | 0.039082 | 0.039082 | 0.039082 | 0.99841 | -0.030519 | 0.99787 | -0.040941 | 10.7367
107 | -0.028187 | -0.0070873 | 0.028188 | 0.0070881 | 1.2724e-06 | 7.8922e-07 | 0.042017 | 0.042017 | 0.042017 | 0.99841 | -0.030519 | 0.99846 | -0.029573 | 11.5433
108 | 0.023513 | 0.0059111 | -0.023499 | -0.0059029 | 1.3348e-05 | 8.1648e-06 | 0.035068 | 0.035069 | 0.035069 | 0.99787 | -0.040941 | 0.99725 | -0.052836 | 9.6342
109 | -0.030141 | -0.0075775 | 0.03016 | 0.0075895 | 1.9326e-05 | 1.2035e-05 | 0.044927 | 0.044927 | 0.044927 | 0.99846 | -0.029573 | 0.99916 | -0.016155 | 12.3427

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.15849 | 0.040103

## res_load
| p_mw | q_mvar
0 | 0.0024027 | 0.00060217
1 | 0.0019077 | 0.00047811
2 | 0.00086063 | 0.0002157
3 | 0.0016669 | 0.00041776
4 | 0.0017588 | 0.0004408
5 | 0.0018583 | 0.00046573
6 | 0.00090073 | 0.00022575
7 | 0.0030216 | 0.00075728
8 | 0.0016999 | 0.00042603
9 | 0.0019494 | 0.00048856
10 | 0.0015684 | 0.00039309
11 | 0.0044032 | 0.0011036
12 | 0.0022006 | 0.00055151
13 | 0.0011921 | 0.00029877
14 | 0.00061855 | 0.00015502
15 | 0.00082167 | 0.00020593
16 | 0.00080717 | 0.0002023
17 | 0.0027434 | 0.00068757
18 | 0.0009747 | 0.00024428
19 | 0.0008975 | 0.00022493
20 | 0.00078147 | 0.00019586
21 | 0.00059585 | 0.00014933
22 | 0.0019826 | 0.00049689
23 | 0.00099656 | 0.00024976
24 | 0.0027915 | 0.00069963
25 | 0.0013611 | 0.00034113
26 | 0.0020522 | 0.00051432
27 | 0.0012374 | 0.00031013
28 | 0.00096627 | 0.00024217
29 | 0.0038893 | 0.00097474
30 | 0.0017955 | 0.00045
31 | 0.0017945 | 0.00044974
32 | 0.0016133 | 0.00040432
33 | 0.0024158 | 0.00060545
34 | 0.0015243 | 0.00038202
35 | 0.0019616 | 0.00049161
36 | 0.0021005 | 0.00052643
37 | 0.0010476 | 0.00026255
38 | 0.0010034 | 0.00025146
39 | 0.0015783 | 0.00039557
40 | 0.0016011 | 0.00040128
41 | 0.0026 | 0.00065162
42 | 0.00217 | 0.00054386
43 | 0.0012081 | 0.00030279
44 | 0.0023523 | 0.00058954
45 | 0.0013771 | 0.00034512
46 | 0.0014868 | 0.00037263
47 | 0.002037 | 0.00051052
48 | 0.0019256 | 0.00048259
49 | 0.00054409 | 0.00013636
50 | 0.001545 | 0.00038722
51 | 0.001065 | 0.00026692
52 | 0.0010208 | 0.00025583
53 | 0.0010553 | 0.00026448
54 | 0.00093761 | 0.00023499
55 | 0.001229 | 0.00030802
56 | 0.0018653 | 0.00046749
57 | 0.0017213 | 0.0004314
58 | 0.0017326 | 0.00043423
59 | 0.0035128 | 0.00088038
60 | 0.00059936 | 0.00015021
61 | 0.00089749 | 0.00022493
62 | 0.00055227 | 0.00013841
63 | 0.00046705 | 0.00011705
64 | 0.0035206 | 0.00088235
65 | 0.0013909 | 0.00034859
66 | 0.00051482 | 0.00012903
67 | 0.0017092 | 0.00042837
68 | 0.0014038 | 0.00035184
69 | 0.0017056 | 0.00042746
70 | 0.0014402 | 0.00036095
71 | 0.001098 | 0.00027519
72 | 0.0016934 | 0.00042442
73 | 0.0023019 | 0.0005769
74 | 0.0016209 | 0.00040624
75 | 0.0028408 | 0.00071197
76 | 0.0011074 | 0.00027753
77 | 0.003268 | 0.00081903
78 | 0.0012526 | 0.00031394
79 | 0.0020021 | 0.00050178
80 | 0.0020952 | 0.00052512
81 | 0.0020394 | 0.00051112
82 | 0.0013532 | 0.00033914
83 | 0.0022821 | 0.00057195
84 | 0.0016122 | 0.00040406
85 | 0.0027065 | 0.0006783
86 | 0.0019699 | 0.0004937
87 | 0.0026913 | 0.00067449
88 | 0.0019526 | 0.00048938
89 | 0.0010027 | 0.0002513
90 | 0.0028477 | 0.0007137

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1