## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2618-1_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2618-1_0_6_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2618-1_0_6_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_2618-1_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2618-1_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2618-1_0_6_node_71 | 0.4 | n |  | TRUE
6 | bus_LV_2618-1_0_6_node_29 | 0.4 | n |  | TRUE
7 | bus_LV_2618-1_0_6_node_74 | 0.4 | n |  | TRUE
8 | bus_LV_2618-1_0_6_node_69 | 0.4 | n |  | TRUE
9 | bus_LV_2618-1_0_6_node_30 | 0.4 | n |  | TRUE
10 | bus_LV_2618-1_0_6_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2618-1_0_6_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2618-1_0_6_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2618-1_0_6_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2618-1_0_6_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2618-1_0_6_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_2618-1_0_6_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_2618-1_0_6_node_210 | 0.4 | n |  | TRUE
18 | bus_LV_2618-1_0_6_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_2618-1_0_6_node_167 | 0.4 | n |  | TRUE
20 | bus_LV_2618-1_0_6_node_157 | 0.4 | n |  | TRUE
21 | bus_LV_2618-1_0_6_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_2618-1_0_6_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_2618-1_0_6_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_2618-1_0_6_node_179 | 0.4 | n |  | TRUE
25 | bus_LV_2618-1_0_6_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2618-1_0_6_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_2618-1_0_6_node_180 | 0.4 | n |  | TRUE
28 | bus_LV_2618-1_0_6_node_38 | 0.4 | n |  | TRUE
29 | bus_LV_2618-1_0_6_node_278 | 0.4 | n |  | TRUE
30 | bus_LV_2618-1_0_6_node_181 | 0.4 | n |  | TRUE
31 | bus_LV_2618-1_0_6_node_135 | 0.4 | n |  | TRUE
32 | bus_LV_2618-1_0_6_node_36 | 0.4 | n |  | TRUE
33 | bus_LV_2618-1_0_6_node_277 | 0.4 | n |  | TRUE
34 | bus_LV_2618-1_0_6_node_133 | 0.4 | n |  | TRUE
35 | bus_LV_2618-1_0_6_node_15 | 0.4 | n |  | TRUE
36 | bus_LV_2618-1_0_6_node_16 | 0.4 | n |  | TRUE
37 | bus_LV_2618-1_0_6_node_17 | 0.4 | n |  | TRUE
38 | bus_LV_2618-1_0_6_node_18 | 0.4 | n |  | TRUE
39 | bus_LV_2618-1_0_6_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_2618-1_0_6_node_21 | 0.4 | n |  | TRUE
41 | bus_LV_2618-1_0_6_node_54 | 0.4 | n |  | TRUE
42 | bus_LV_2618-1_0_6_node_20 | 0.4 | n |  | TRUE
43 | bus_LV_2618-1_0_6_node_52 | 0.4 | n |  | TRUE
44 | bus_LV_2618-1_0_6_node_211 | 0.4 | n |  | TRUE
45 | bus_LV_2618-1_0_6_node_24 | 0.4 | n |  | TRUE
46 | bus_LV_2618-1_0_6_node_25 | 0.4 | n |  | TRUE
47 | bus_LV_2618-1_0_6_node_27 | 0.4 | n |  | TRUE
48 | bus_LV_2618-1_0_6_node_46 | 0.4 | n |  | TRUE
49 | bus_LV_2618-1_0_6_node_45 | 0.4 | n |  | TRUE
50 | bus_LV_2618-1_0_6_node_238 | 0.4 | n |  | TRUE
51 | bus_LV_2618-1_0_6_node_182 | 0.4 | n |  | TRUE
52 | bus_LV_2618-1_0_6_node_156 | 0.4 | n |  | TRUE
53 | bus_LV_2618-1_0_6_node_31 | 0.4 | n |  | TRUE
54 | bus_LV_2618-1_0_6_node_32 | 0.4 | n |  | TRUE
55 | bus_LV_2618-1_0_6_node_33 | 0.4 | n |  | TRUE
56 | bus_LV_2618-1_0_6_node_34 | 0.4 | n |  | TRUE
57 | bus_LV_2618-1_0_6_node_274 | 0.4 | n |  | TRUE
58 | bus_LV_2618-1_0_6_node_275 | 0.4 | n |  | TRUE
59 | bus_LV_2618-1_0_6_node_35 | 0.4 | n |  | TRUE
60 | bus_LV_2618-1_0_6_node_37 | 0.4 | n |  | TRUE
61 | bus_LV_2618-1_0_6_node_286 | 0.4 | n |  | TRUE
62 | bus_LV_2618-1_0_6_node_285 | 0.4 | n |  | TRUE
63 | bus_LV_2618-1_0_6_node_39 | 0.4 | n |  | TRUE
64 | bus_LV_2618-1_0_6_node_40 | 0.4 | n |  | TRUE
65 | bus_LV_2618-1_0_6_node_41 | 0.4 | n |  | TRUE
66 | bus_LV_2618-1_0_6_node_43 | 0.4 | n |  | TRUE
67 | bus_LV_2618-1_0_6_node_44 | 0.4 | n |  | TRUE
68 | bus_LV_2618-1_0_6_node_42 | 0.4 | n |  | TRUE
69 | bus_LV_2618-1_0_6_node_236 | 0.4 | n |  | TRUE
70 | bus_LV_2618-1_0_6_node_164 | 0.4 | n |  | TRUE
71 | bus_LV_2618-1_0_6_node_242 | 0.4 | n |  | TRUE
72 | bus_LV_2618-1_0_6_node_245 | 0.4 | n |  | TRUE
73 | bus_LV_2618-1_0_6_node_152 | 0.4 | n |  | TRUE
74 | bus_LV_2618-1_0_6_node_165 | 0.4 | n |  | TRUE
75 | bus_LV_2618-1_0_6_node_166 | 0.4 | n |  | TRUE
76 | bus_LV_2618-1_0_6_node_163 | 0.4 | n |  | TRUE
77 | bus_LV_2618-1_0_6_node_216 | 0.4 | n |  | TRUE
78 | bus_LV_2618-1_0_6_node_239 | 0.4 | n |  | TRUE
79 | bus_LV_2618-1_0_6_node_47 | 0.4 | n |  | TRUE
80 | bus_LV_2618-1_0_6_node_48 | 0.4 | n |  | TRUE
81 | bus_LV_2618-1_0_6_node_49 | 0.4 | n |  | TRUE
82 | bus_LV_2618-1_0_6_node_50 | 0.4 | n |  | TRUE
83 | bus_LV_2618-1_0_6_node_51 | 0.4 | n |  | TRUE
84 | bus_LV_2618-1_0_6_node_205 | 0.4 | n |  | TRUE
85 | bus_LV_2618-1_0_6_node_224 | 0.4 | n |  | TRUE
86 | bus_LV_2618-1_0_6_node_200 | 0.4 | n |  | TRUE
87 | bus_LV_2618-1_0_6_node_204 | 0.4 | n |  | TRUE
88 | bus_LV_2618-1_0_6_node_59 | 0.4 | n |  | TRUE
89 | bus_LV_2618-1_0_6_node_199 | 0.4 | n |  | TRUE
90 | bus_LV_2618-1_0_6_node_53 | 0.4 | n |  | TRUE
91 | bus_LV_2618-1_0_6_node_55 | 0.4 | n |  | TRUE
92 | bus_LV_2618-1_0_6_node_57 | 0.4 | n |  | TRUE
93 | bus_LV_2618-1_0_6_node_260 | 0.4 | n |  | TRUE
94 | bus_LV_2618-1_0_6_node_60 | 0.4 | n |  | TRUE
95 | bus_LV_2618-1_0_6_node_61 | 0.4 | n |  | TRUE
96 | bus_LV_2618-1_0_6_node_62 | 0.4 | n |  | TRUE
97 | bus_LV_2618-1_0_6_node_63 | 0.4 | n |  | TRUE
98 | bus_LV_2618-1_0_6_node_64 | 0.4 | n |  | TRUE
99 | bus_LV_2618-1_0_6_node_72 | 0.4 | n |  | TRUE
100 | bus_LV_2618-1_0_6_node_91 | 0.4 | n |  | TRUE
101 | bus_LV_2618-1_0_6_node_81 | 0.4 | n |  | TRUE
102 | bus_LV_2618-1_0_6_node_70 | 0.4 | n |  | TRUE
103 | bus_LV_2618-1_0_6_node_89 | 0.4 | n |  | TRUE
104 | bus_LV_2618-1_0_6_node_82 | 0.4 | n |  | TRUE
105 | bus_LV_2618-1_0_6_node_65 | 0.4 | n |  | TRUE
106 | bus_LV_2618-1_0_6_node_66 | 0.4 | n |  | TRUE
107 | bus_LV_2618-1_0_6_node_67 | 0.4 | n |  | TRUE
108 | bus_LV_2618-1_0_6_node_68 | 0.4 | n |  | TRUE
109 | bus_LV_2618-1_0_6_node_264 | 0.4 | n |  | TRUE
110 | bus_LV_2618-1_0_6_node_92 | 0.4 | n |  | TRUE
111 | bus_LV_2618-1_0_6_node_262 | 0.4 | n |  | TRUE
112 | bus_LV_2618-1_0_6_node_73 | 0.4 | n |  | TRUE
113 | bus_LV_2618-1_0_6_node_113 | 0.4 | n |  | TRUE
114 | bus_LV_2618-1_0_6_node_111 | 0.4 | n |  | TRUE
115 | bus_LV_2618-1_0_6_node_144 | 0.4 | n |  | TRUE
116 | bus_LV_2618-1_0_6_node_110 | 0.4 | n |  | TRUE
117 | bus_LV_2618-1_0_6_node_145 | 0.4 | n |  | TRUE
118 | bus_LV_2618-1_0_6_node_76 | 0.4 | n |  | TRUE
119 | bus_LV_2618-1_0_6_node_232 | 0.4 | n |  | TRUE
120 | bus_LV_2618-1_0_6_node_231 | 0.4 | n |  | TRUE
121 | bus_LV_2618-1_0_6_node_77 | 0.4 | n |  | TRUE
122 | bus_LV_2618-1_0_6_node_78 | 0.4 | n |  | TRUE
123 | bus_LV_2618-1_0_6_node_79 | 0.4 | n |  | TRUE
124 | bus_LV_2618-1_0_6_node_155 | 0.4 | n |  | TRUE
125 | bus_LV_2618-1_0_6_node_80 | 0.4 | n |  | TRUE
126 | bus_LV_2618-1_0_6_node_153 | 0.4 | n |  | TRUE
127 | bus_LV_2618-1_0_6_node_154 | 0.4 | n |  | TRUE
128 | bus_LV_2618-1_0_6_node_237 | 0.4 | n |  | TRUE
129 | bus_LV_2618-1_0_6_node_173 | 0.4 | n |  | TRUE
130 | bus_LV_2618-1_0_6_node_172 | 0.4 | n |  | TRUE
131 | bus_LV_2618-1_0_6_node_83 | 0.4 | n |  | TRUE
132 | bus_LV_2618-1_0_6_node_197 | 0.4 | n |  | TRUE
133 | bus_LV_2618-1_0_6_node_268 | 0.4 | n |  | TRUE
134 | bus_LV_2618-1_0_6_node_84 | 0.4 | n |  | TRUE
135 | bus_LV_2618-1_0_6_node_85 | 0.4 | n |  | TRUE
136 | bus_LV_2618-1_0_6_node_86 | 0.4 | n |  | TRUE
137 | bus_LV_2618-1_0_6_node_87 | 0.4 | n |  | TRUE
138 | bus_LV_2618-1_0_6_node_88 | 0.4 | n |  | TRUE
139 | bus_LV_2618-1_0_6_node_225 | 0.4 | n |  | TRUE
140 | bus_LV_2618-1_0_6_node_235 | 0.4 | n |  | TRUE
141 | bus_LV_2618-1_0_6_node_190 | 0.4 | n |  | TRUE
142 | bus_LV_2618-1_0_6_node_206 | 0.4 | n |  | TRUE
143 | bus_LV_2618-1_0_6_node_259 | 0.4 | n |  | TRUE
144 | bus_LV_2618-1_0_6_node_117 | 0.4 | n |  | TRUE
145 | bus_LV_2618-1_0_6_node_261 | 0.4 | n |  | TRUE
146 | bus_LV_2618-1_0_6_node_188 | 0.4 | n |  | TRUE
147 | bus_LV_2618-1_0_6_node_207 | 0.4 | n |  | TRUE
148 | bus_LV_2618-1_0_6_node_90 | 0.4 | n |  | TRUE
149 | bus_LV_2618-1_0_6_node_93 | 0.4 | n |  | TRUE
150 | bus_LV_2618-1_0_6_node_94 | 0.4 | n |  | TRUE
151 | bus_LV_2618-1_0_6_node_95 | 0.4 | n |  | TRUE
152 | bus_LV_2618-1_0_6_node_96 | 0.4 | n |  | TRUE
153 | bus_LV_2618-1_0_6_node_97 | 0.4 | n |  | TRUE
154 | bus_LV_2618-1_0_6_node_98 | 0.4 | n |  | TRUE
155 | bus_LV_2618-1_0_6_node_158 | 0.4 | n |  | TRUE
156 | bus_LV_2618-1_0_6_node_126 | 0.4 | n |  | TRUE
157 | bus_LV_2618-1_0_6_node_171 | 0.4 | n |  | TRUE
158 | bus_LV_2618-1_0_6_node_124 | 0.4 | n |  | TRUE
159 | bus_LV_2618-1_0_6_node_99 | 0.4 | n |  | TRUE
160 | bus_LV_2618-1_0_6_node_100 | 0.4 | n |  | TRUE
161 | bus_LV_2618-1_0_6_node_101 | 0.4 | n |  | TRUE
162 | bus_LV_2618-1_0_6_node_282 | 0.4 | n |  | TRUE
163 | bus_LV_2618-1_0_6_node_102 | 0.4 | n |  | TRUE
164 | bus_LV_2618-1_0_6_node_103 | 0.4 | n |  | TRUE
165 | bus_LV_2618-1_0_6_node_280 | 0.4 | n |  | TRUE
166 | bus_LV_2618-1_0_6_node_281 | 0.4 | n |  | TRUE
167 | bus_LV_2618-1_0_6_node_283 | 0.4 | n |  | TRUE
168 | bus_LV_2618-1_0_6_node_122 | 0.4 | n |  | TRUE
169 | bus_LV_2618-1_0_6_node_198 | 0.4 | n |  | TRUE
170 | bus_LV_2618-1_0_6_node_120 | 0.4 | n |  | TRUE
171 | bus_LV_2618-1_0_6_node_104 | 0.4 | n |  | TRUE
172 | bus_LV_2618-1_0_6_node_105 | 0.4 | n |  | TRUE
173 | bus_LV_2618-1_0_6_node_106 | 0.4 | n |  | TRUE
174 | bus_LV_2618-1_0_6_node_107 | 0.4 | n |  | TRUE
175 | bus_LV_2618-1_0_6_node_108 | 0.4 | n |  | TRUE
176 | bus_LV_2618-1_0_6_node_109 | 0.4 | n |  | TRUE
177 | bus_LV_2618-1_0_6_node_150 | 0.4 | n |  | TRUE
178 | bus_LV_2618-1_0_6_node_128 | 0.4 | n |  | TRUE
179 | bus_LV_2618-1_0_6_node_129 | 0.4 | n |  | TRUE
180 | bus_LV_2618-1_0_6_node_148 | 0.4 | n |  | TRUE
181 | bus_LV_2618-1_0_6_node_112 | 0.4 | n |  | TRUE
182 | bus_LV_2618-1_0_6_node_114 | 0.4 | n |  | TRUE
183 | bus_LV_2618-1_0_6_node_115 | 0.4 | n |  | TRUE
184 | bus_LV_2618-1_0_6_node_116 | 0.4 | n |  | TRUE
185 | bus_LV_2618-1_0_6_node_118 | 0.4 | n |  | TRUE
186 | bus_LV_2618-1_0_6_node_119 | 0.4 | n |  | TRUE
187 | bus_LV_2618-1_0_6_node_121 | 0.4 | n |  | TRUE
188 | bus_LV_2618-1_0_6_node_123 | 0.4 | n |  | TRUE
189 | bus_LV_2618-1_0_6_node_162 | 0.4 | n |  | TRUE
190 | bus_LV_2618-1_0_6_node_125 | 0.4 | n |  | TRUE
191 | bus_LV_2618-1_0_6_node_127 | 0.4 | n |  | TRUE
192 | bus_LV_2618-1_0_6_node_159 | 0.4 | n |  | TRUE
193 | bus_LV_2618-1_0_6_node_160 | 0.4 | n |  | TRUE
194 | bus_LV_2618-1_0_6_node_130 | 0.4 | n |  | TRUE
195 | bus_LV_2618-1_0_6_node_168 | 0.4 | n |  | TRUE
196 | bus_LV_2618-1_0_6_node_169 | 0.4 | n |  | TRUE
197 | bus_LV_2618-1_0_6_node_131 | 0.4 | n |  | TRUE
198 | bus_LV_2618-1_0_6_node_132 | 0.4 | n |  | TRUE
199 | bus_LV_2618-1_0_6_node_134 | 0.4 | n |  | TRUE
200 | bus_LV_2618-1_0_6_node_136 | 0.4 | n |  | TRUE
201 | bus_LV_2618-1_0_6_node_137 | 0.4 | n |  | TRUE
202 | bus_LV_2618-1_0_6_node_226 | 0.4 | n |  | TRUE
203 | bus_LV_2618-1_0_6_node_279 | 0.4 | n |  | TRUE
204 | bus_LV_2618-1_0_6_node_196 | 0.4 | n |  | TRUE
205 | bus_LV_2618-1_0_6_node_138 | 0.4 | n |  | TRUE
206 | bus_LV_2618-1_0_6_node_140 | 0.4 | n |  | TRUE
207 | bus_LV_2618-1_0_6_node_139 | 0.4 | n |  | TRUE
208 | bus_LV_2618-1_0_6_node_141 | 0.4 | n |  | TRUE
209 | bus_LV_2618-1_0_6_node_143 | 0.4 | n |  | TRUE
210 | bus_LV_2618-1_0_6_node_276 | 0.4 | n |  | TRUE
211 | bus_LV_2618-1_0_6_node_142 | 0.4 | n |  | TRUE
212 | bus_LV_2618-1_0_6_node_183 | 0.4 | n |  | TRUE
213 | bus_LV_2618-1_0_6_node_195 | 0.4 | n |  | TRUE
214 | bus_LV_2618-1_0_6_node_193 | 0.4 | n |  | TRUE
215 | bus_LV_2618-1_0_6_node_146 | 0.4 | n |  | TRUE
216 | bus_LV_2618-1_0_6_node_147 | 0.4 | n |  | TRUE
217 | bus_LV_2618-1_0_6_node_149 | 0.4 | n |  | TRUE
218 | bus_LV_2618-1_0_6_node_151 | 0.4 | n |  | TRUE
219 | bus_LV_2618-1_0_6_node_161 | 0.4 | n |  | TRUE
220 | bus_LV_2618-1_0_6_node_186 | 0.4 | n |  | TRUE
221 | bus_LV_2618-1_0_6_node_209 | 0.4 | n |  | TRUE
222 | bus_LV_2618-1_0_6_node_270 | 0.4 | n |  | TRUE
223 | bus_LV_2618-1_0_6_node_246 | 0.4 | n |  | TRUE
224 | bus_LV_2618-1_0_6_node_269 | 0.4 | n |  | TRUE
225 | bus_LV_2618-1_0_6_node_244 | 0.4 | n |  | TRUE
226 | bus_LV_2618-1_0_6_node_170 | 0.4 | n |  | TRUE
227 | bus_LV_2618-1_0_6_node_184 | 0.4 | n |  | TRUE
228 | bus_LV_2618-1_0_6_node_185 | 0.4 | n |  | TRUE
229 | bus_LV_2618-1_0_6_node_174 | 0.4 | n |  | TRUE
230 | bus_LV_2618-1_0_6_node_175 | 0.4 | n |  | TRUE
231 | bus_LV_2618-1_0_6_node_255 | 0.4 | n |  | TRUE
232 | bus_LV_2618-1_0_6_node_178 | 0.4 | n |  | TRUE
233 | bus_LV_2618-1_0_6_node_256 | 0.4 | n |  | TRUE
234 | bus_LV_2618-1_0_6_node_257 | 0.4 | n |  | TRUE
235 | bus_LV_2618-1_0_6_node_287 | 0.4 | n |  | TRUE
236 | bus_LV_2618-1_0_6_node_214 | 0.4 | n |  | TRUE
237 | bus_LV_2618-1_0_6_node_176 | 0.4 | n |  | TRUE
238 | bus_LV_2618-1_0_6_node_177 | 0.4 | n |  | TRUE
239 | bus_LV_2618-1_0_6_node_201 | 0.4 | n |  | TRUE
240 | bus_LV_2618-1_0_6_node_202 | 0.4 | n |  | TRUE
241 | bus_LV_2618-1_0_6_node_215 | 0.4 | n |  | TRUE
242 | bus_LV_2618-1_0_6_node_208 | 0.4 | n |  | TRUE
243 | bus_LV_2618-1_0_6_node_187 | 0.4 | n |  | TRUE
244 | bus_LV_2618-1_0_6_node_189 | 0.4 | n |  | TRUE
245 | bus_LV_2618-1_0_6_node_191 | 0.4 | n |  | TRUE
246 | bus_LV_2618-1_0_6_node_192 | 0.4 | n |  | TRUE
247 | bus_LV_2618-1_0_6_node_229 | 0.4 | n |  | TRUE
248 | bus_LV_2618-1_0_6_node_227 | 0.4 | n |  | TRUE
249 | bus_LV_2618-1_0_6_node_194 | 0.4 | n |  | TRUE
250 | bus_LV_2618-1_0_6_node_203 | 0.4 | n |  | TRUE
251 | bus_LV_2618-1_0_6_node_243 | 0.4 | n |  | TRUE
252 | bus_LV_2618-1_0_6_node_273 | 0.4 | n |  | TRUE
253 | bus_LV_2618-1_0_6_node_248 | 0.4 | n |  | TRUE
254 | bus_LV_2618-1_0_6_node_212 | 0.4 | n |  | TRUE
255 | bus_LV_2618-1_0_6_node_213 | 0.4 | n |  | TRUE
256 | bus_LV_2618-1_0_6_node_223 | 0.4 | n |  | TRUE
257 | bus_LV_2618-1_0_6_node_220 | 0.4 | n |  | TRUE
258 | bus_LV_2618-1_0_6_node_218 | 0.4 | n |  | TRUE
259 | bus_LV_2618-1_0_6_node_247 | 0.4 | n |  | TRUE
260 | bus_LV_2618-1_0_6_node_221 | 0.4 | n |  | TRUE
261 | bus_LV_2618-1_0_6_node_219 | 0.4 | n |  | TRUE
262 | bus_LV_2618-1_0_6_node_217 | 0.4 | n |  | TRUE
263 | bus_LV_2618-1_0_6_node_258 | 0.4 | n |  | TRUE
264 | bus_LV_2618-1_0_6_node_222 | 0.4 | n |  | TRUE
265 | bus_LV_2618-1_0_6_node_240 | 0.4 | n |  | TRUE
266 | bus_LV_2618-1_0_6_node_228 | 0.4 | n |  | TRUE
267 | bus_LV_2618-1_0_6_node_230 | 0.4 | n |  | TRUE
268 | bus_LV_2618-1_0_6_node_249 | 0.4 | n |  | TRUE
269 | bus_LV_2618-1_0_6_node_233 | 0.4 | n |  | TRUE
270 | bus_LV_2618-1_0_6_node_234 | 0.4 | n |  | TRUE
271 | bus_LV_2618-1_0_6_node_241 | 0.4 | n |  | TRUE
272 | bus_LV_2618-1_0_6_node_251 | 0.4 | n |  | TRUE
273 | bus_LV_2618-1_0_6_node_265 | 0.4 | n |  | TRUE
274 | bus_LV_2618-1_0_6_node_266 | 0.4 | n |  | TRUE
275 | bus_LV_2618-1_0_6_node_250 | 0.4 | n |  | TRUE
276 | bus_LV_2618-1_0_6_node_252 | 0.4 | n |  | TRUE
277 | bus_LV_2618-1_0_6_node_253 | 0.4 | n |  | TRUE
278 | bus_LV_2618-1_0_6_node_267 | 0.4 | n |  | TRUE
279 | bus_LV_2618-1_0_6_node_263 | 0.4 | n |  | TRUE
280 | bus_LV_2618-1_0_6_node_271 | 0.4 | n |  | TRUE
281 | bus_LV_2618-1_0_6_node_272 | 0.4 | n |  | TRUE
282 | bus_MV_287_0_node_6 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2618-1_0_6_load_0 | 0 | 0.0030179 | 0.00075636 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2618-1_0_6_load_2 | 1 | 0.0044412 | 0.0011131 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2618-1_0_6_load_1 | 2 | 0.0061312 | 0.0015366 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2618-1_0_6_load_3 | 3 | 0.0039908 | 0.0010002 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2618-1_0_6_load_4 | 4 | 0.0042626 | 0.0010683 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2618-1_0_6_load_29 | 6 | 0.0046044 | 0.001154 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2618-1_0_6_load_74 | 7 | 0.005922 | 0.0014842 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2618-1_0_6_load_69 | 8 | 0.0020457 | 0.00051271 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2618-1_0_6_load_30 | 9 | 0.0013952 | 0.00034966 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2618-1_0_6_load_5 | 10 | 0.0023634 | 0.00059233 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2618-1_0_6_load_6 | 11 | 0.006612 | 0.0016571 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2618-1_0_6_load_7 | 12 | 0.0016425 | 0.00041164 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2618-1_0_6_load_8 | 13 | 0.0026202 | 0.00065667 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2618-1_0_6_load_9 | 14 | 0.0080142 | 0.0020085 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2618-1_0_6_load_210 | 17 | 0.0015868 | 0.00039768 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2618-1_0_6_load_22 | 18 | 0.003428 | 0.00085915 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2618-1_0_6_load_167 | 19 | 0.0064371 | 0.0016133 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2618-1_0_6_load_157 | 20 | 0.011497 | 0.0028813 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2618-1_0_6_load_10 | 21 | 0.0022238 | 0.00055733 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2618-1_0_6_load_11 | 22 | 0.0013549 | 0.00033956 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2618-1_0_6_load_12 | 23 | 0.0025889 | 0.00064883 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2618-1_0_6_load_179 | 24 | 0.001909 | 0.00047844 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2618-1_0_6_load_14 | 26 | 0.0021132 | 0.00052962 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2618-1_0_6_load_180 | 27 | 0.0016881 | 0.00042307 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2618-1_0_6_load_38 | 28 | 0.0029547 | 0.00074051 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2618-1_0_6_load_278 | 29 | 0.0013344 | 0.00033442 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2618-1_0_6_load_181 | 30 | 0.0026973 | 0.000676 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2618-1_0_6_load_277 | 33 | 0.0013153 | 0.00032965 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2618-1_0_6_load_133 | 34 | 0.0015098 | 0.00037839 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2618-1_0_6_load_15 | 35 | 0.0013302 | 0.00033338 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2618-1_0_6_load_16 | 36 | 0.0014451 | 0.00036217 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2618-1_0_6_load_17 | 37 | 0.0014467 | 0.00036259 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2618-1_0_6_load_18 | 38 | 0.0014149 | 0.0003546 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2618-1_0_6_load_19 | 39 | 0.0014197 | 0.0003558 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2618-1_0_6_load_21 | 40 | 0.0014501 | 0.00036343 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2618-1_0_6_load_54 | 41 | 0.0014434 | 0.00036174 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2618-1_0_6_load_20 | 42 | 0.0012913 | 0.00032364 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2618-1_0_6_load_52 | 43 | 0.0017675 | 0.00044297 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2618-1_0_6_load_24 | 45 | 0.00092704 | 0.00023234 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2618-1_0_6_load_25 | 46 | 0.00081123 | 0.00020331 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2618-1_0_6_load_46 | 48 | 0.0024994 | 0.0006264 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2618-1_0_6_load_45 | 49 | 0.0011966 | 0.0002999 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2618-1_0_6_load_182 | 51 | 0.0084457 | 0.0021167 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2618-1_0_6_load_156 | 52 | 0.0019185 | 0.00048082 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2618-1_0_6_load_31 | 53 | 0.002631 | 0.0006594 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2618-1_0_6_load_33 | 55 | 0.00042096 | 0.0001055 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2618-1_0_6_load_34 | 56 | 0.0026489 | 0.00066387 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2618-1_0_6_load_274 | 57 | 0.0016699 | 0.00041853 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2618-1_0_6_load_275 | 58 | 0.0011172 | 0.00028001 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2618-1_0_6_load_35 | 59 | 0.0026219 | 0.00065711 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2618-1_0_6_load_285 | 62 | 0.0023555 | 0.00059035 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2618-1_0_6_load_39 | 63 | 0.0014512 | 0.00036369 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2618-1_0_6_load_40 | 64 | 0.0013544 | 0.00033944 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2618-1_0_6_load_43 | 66 | 0.00049916 | 0.0001251 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2618-1_0_6_load_42 | 68 | 0.0023298 | 0.0005839 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2618-1_0_6_load_242 | 71 | 0.0019075 | 0.00047806 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2618-1_0_6_load_245 | 72 | 0.0020643 | 0.00051735 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2618-1_0_6_load_165 | 74 | 0.00088805 | 0.00022257 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2618-1_0_6_load_166 | 75 | 0.00067953 | 0.00017031 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2618-1_0_6_load_163 | 76 | 0.001648 | 0.00041302 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2618-1_0_6_load_216 | 77 | 0.001123 | 0.00028146 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2618-1_0_6_load_239 | 78 | 0.0036025 | 0.00090287 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2618-1_0_6_load_47 | 79 | 0.001107 | 0.00027745 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2618-1_0_6_load_48 | 80 | 0.0015847 | 0.00039716 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2618-1_0_6_load_49 | 81 | 0.0018587 | 0.00046582 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2618-1_0_6_load_50 | 82 | 0.001286 | 0.0003223 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2618-1_0_6_load_205 | 84 | 0.0017616 | 0.0004415 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2618-1_0_6_load_224 | 85 | 0.0013741 | 0.00034439 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2618-1_0_6_load_200 | 86 | 0.0027721 | 0.00069476 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2618-1_0_6_load_204 | 87 | 0.0022186 | 0.00055604 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2618-1_0_6_load_199 | 89 | 0.001763 | 0.00044185 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2618-1_0_6_load_53 | 90 | 0.001743 | 0.00043683 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2618-1_0_6_load_55 | 91 | 0.0016217 | 0.00040643 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2618-1_0_6_load_260 | 93 | 0.0013958 | 0.00034982 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2618-1_0_6_load_60 | 94 | 0.0047199 | 0.0011829 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2618-1_0_6_load_64 | 98 | 0.0035148 | 0.00088089 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2618-1_0_6_load_72 | 99 | 0.0011313 | 0.00028354 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2618-1_0_6_load_91 | 100 | 0.005364 | 0.0013444 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2618-1_0_6_load_81 | 101 | 0.0014738 | 0.00036937 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2618-1_0_6_load_70 | 102 | 0.0040187 | 0.0010072 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2618-1_0_6_load_89 | 103 | 0.0042695 | 0.00107 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2618-1_0_6_load_82 | 104 | 0.0058034 | 0.0014545 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2618-1_0_6_load_65 | 105 | 0.0016005 | 0.00040112 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2618-1_0_6_load_66 | 106 | 0.0017413 | 0.00043641 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2618-1_0_6_load_67 | 107 | 0.0017233 | 0.00043191 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2618-1_0_6_load_68 | 108 | 0.0028914 | 0.00072464 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2618-1_0_6_load_92 | 110 | 0.0050236 | 0.001259 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2618-1_0_6_load_113 | 113 | 0.006154 | 0.0015424 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2618-1_0_6_load_111 | 114 | 0.0066451 | 0.0016654 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2618-1_0_6_load_144 | 115 | 0.0045151 | 0.0011316 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2618-1_0_6_load_110 | 116 | 0.0026494 | 0.000664 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2618-1_0_6_load_145 | 117 | 0.0027064 | 0.00067829 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2618-1_0_6_load_76 | 118 | 0.0029185 | 0.00073144 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2618-1_0_6_load_232 | 119 | 0.0018721 | 0.00046919 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2618-1_0_6_load_231 | 120 | 0.0018648 | 0.00046737 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2618-1_0_6_load_77 | 121 | 0.0012539 | 0.00031426 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2618-1_0_6_load_78 | 122 | 0.0012514 | 0.00031362 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2618-1_0_6_load_79 | 123 | 0.00094829 | 0.00023766 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2618-1_0_6_load_155 | 124 | 0.0039215 | 0.00098283 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2618-1_0_6_load_153 | 126 | 0.0012899 | 0.00032328 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2618-1_0_6_load_237 | 128 | 0.001554 | 0.00038946 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2618-1_0_6_load_173 | 129 | 0.0013393 | 0.00033565 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2618-1_0_6_load_172 | 130 | 0.001041 | 0.00026089 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2618-1_0_6_load_83 | 131 | 0.0035728 | 0.00089542 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2618-1_0_6_load_197 | 132 | 0.002275 | 0.00057017 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2618-1_0_6_load_268 | 133 | 0.0023382 | 0.000586 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2618-1_0_6_load_84 | 134 | 0.0017368 | 0.00043529 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2618-1_0_6_load_85 | 135 | 0.0022075 | 0.00055324 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2618-1_0_6_load_86 | 136 | 0.00090453 | 0.0002267 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2618-1_0_6_load_87 | 137 | 0.0027987 | 0.00070142 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2618-1_0_6_load_235 | 140 | 0.00089357 | 0.00022395 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2618-1_0_6_load_190 | 141 | 0.0018512 | 0.00046395 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2618-1_0_6_load_259 | 143 | 0.0022158 | 0.00055534 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2618-1_0_6_load_117 | 144 | 0.0016859 | 0.00042252 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2618-1_0_6_load_261 | 145 | 0.0029943 | 0.00075044 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2618-1_0_6_load_188 | 146 | 0.0011321 | 0.00028374 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2618-1_0_6_load_207 | 147 | 0.0024793 | 0.00062138 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2618-1_0_6_load_90 | 148 | 0.0056166 | 0.0014076 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2618-1_0_6_load_93 | 149 | 0.001226 | 0.00030727 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2618-1_0_6_load_94 | 150 | 0.0019283 | 0.00048328 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2618-1_0_6_load_96 | 152 | 0.00096758 | 0.0002425 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2618-1_0_6_load_97 | 153 | 0.0019032 | 0.00047698 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2618-1_0_6_load_98 | 154 | 0.0011405 | 0.00028585 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2618-1_0_6_load_158 | 155 | 0.00099327 | 0.00024894 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2618-1_0_6_load_126 | 156 | 0.0011937 | 0.00029917 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2618-1_0_6_load_171 | 157 | 0.0021897 | 0.00054879 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_2618-1_0_6_load_124 | 158 | 0.0016151 | 0.00040479 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_2618-1_0_6_load_99 | 159 | 0.0019992 | 0.00050105 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_2618-1_0_6_load_100 | 160 | 0.00084141 | 0.00021088 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_2618-1_0_6_load_102 | 163 | 0.0016894 | 0.00042341 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_2618-1_0_6_load_103 | 164 | 0.0017324 | 0.00043417 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_2618-1_0_6_load_280 | 165 | 0.0021775 | 0.00054574 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_2618-1_0_6_load_281 | 166 | 0.0016437 | 0.00041196 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_2618-1_0_6_load_283 | 167 | 0.002899 | 0.00072657 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_2618-1_0_6_load_122 | 168 | 0.002154 | 0.00053985 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_2618-1_0_6_load_198 | 169 | 0.001739 | 0.00043583 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_2618-1_0_6_load_120 | 170 | 0.0049277 | 0.001235 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_2618-1_0_6_load_104 | 171 | 0.0026312 | 0.00065944 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_2618-1_0_6_load_105 | 172 | 0.0018571 | 0.00046543 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_2618-1_0_6_load_106 | 173 | 0.0017093 | 0.0004284 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_2618-1_0_6_load_107 | 174 | 0.0012624 | 0.0003164 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_2618-1_0_6_load_108 | 175 | 0.001713 | 0.00042932 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_2618-1_0_6_load_109 | 176 | 0.002423 | 0.00060726 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_2618-1_0_6_load_150 | 177 | 0.0032215 | 0.00080738 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_2618-1_0_6_load_128 | 178 | 0.0018822 | 0.00047173 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_2618-1_0_6_load_129 | 179 | 0.0024377 | 0.00061094 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_2618-1_0_6_load_148 | 180 | 0.0017497 | 0.00043852 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_2618-1_0_6_load_112 | 181 | 0.0035532 | 0.00089051 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_2618-1_0_6_load_114 | 182 | 0.003786 | 0.00094886 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_2618-1_0_6_load_115 | 183 | 0.0027789 | 0.00069647 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_2618-1_0_6_load_116 | 184 | 0.001606 | 0.00040249 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_2618-1_0_6_load_118 | 185 | 0.0015941 | 0.00039952 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_2618-1_0_6_load_119 | 186 | 0.0016432 | 0.00041183 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_2618-1_0_6_load_121 | 187 | 0.0030109 | 0.00075461 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_2618-1_0_6_load_123 | 188 | 0.0034108 | 0.00085482 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_2618-1_0_6_load_162 | 189 | 0.0040909 | 0.0010253 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_2618-1_0_6_load_125 | 190 | 0.0015854 | 0.00039733 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_2618-1_0_6_load_127 | 191 | 0.0027101 | 0.00067921 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_2618-1_0_6_load_159 | 192 | 0.0017365 | 0.00043522 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_2618-1_0_6_load_160 | 193 | 0.0019215 | 0.00048158 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_2618-1_0_6_load_130 | 194 | 0.0022063 | 0.00055295 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_2618-1_0_6_load_168 | 195 | 0.0035154 | 0.00088104 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_2618-1_0_6_load_169 | 196 | 0.0015114 | 0.0003788 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_2618-1_0_6_load_131 | 197 | 0.0018417 | 0.00046158 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_2618-1_0_6_load_132 | 198 | 0.0014971 | 0.00037521 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_2618-1_0_6_load_136 | 200 | 0.0063007 | 0.0015791 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_2618-1_0_6_load_137 | 201 | 0.0014133 | 0.00035422 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_2618-1_0_6_load_226 | 202 | 0.001766 | 0.00044259 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_2618-1_0_6_load_279 | 203 | 0.0048989 | 0.0012278 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_2618-1_0_6_load_196 | 204 | 0.0012369 | 0.00031 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_2618-1_0_6_load_138 | 205 | 0.0026504 | 0.00066425 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_2618-1_0_6_load_139 | 207 | 0.0035676 | 0.00089414 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_2618-1_0_6_load_141 | 208 | 0.0011696 | 0.00029313 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_2618-1_0_6_load_143 | 209 | 0.0019683 | 0.0004933 | 0 | 0 |  | 1 | TRUE | wye
174 | LV_2618-1_0_6_load_276 | 210 | 0.0016542 | 0.00041459 | 0 | 0 |  | 1 | TRUE | wye
175 | LV_2618-1_0_6_load_142 | 211 | 0.0021695 | 0.00054372 | 0 | 0 |  | 1 | TRUE | wye
176 | LV_2618-1_0_6_load_183 | 212 | 0.002562 | 0.00064209 | 0 | 0 |  | 1 | TRUE | wye
177 | LV_2618-1_0_6_load_195 | 213 | 0.0013125 | 0.00032894 | 0 | 0 |  | 1 | TRUE | wye
178 | LV_2618-1_0_6_load_193 | 214 | 0.0033523 | 0.00084016 | 0 | 0 |  | 1 | TRUE | wye
179 | LV_2618-1_0_6_load_146 | 215 | 0.0019525 | 0.00048934 | 0 | 0 |  | 1 | TRUE | wye
180 | LV_2618-1_0_6_load_147 | 216 | 0.0024057 | 0.00060292 | 0 | 0 |  | 1 | TRUE | wye
181 | LV_2618-1_0_6_load_149 | 217 | 0.0026324 | 0.00065974 | 0 | 0 |  | 1 | TRUE | wye
182 | LV_2618-1_0_6_load_151 | 218 | 0.0026177 | 0.00065605 | 0 | 0 |  | 1 | TRUE | wye
183 | LV_2618-1_0_6_load_161 | 219 | 0.0020489 | 0.00051349 | 0 | 0 |  | 1 | TRUE | wye
184 | LV_2618-1_0_6_load_186 | 220 | 0.0021185 | 0.00053094 | 0 | 0 |  | 1 | TRUE | wye
185 | LV_2618-1_0_6_load_270 | 222 | 0.0022851 | 0.00057269 | 0 | 0 |  | 1 | TRUE | wye
186 | LV_2618-1_0_6_load_246 | 223 | 0.0023215 | 0.00058182 | 0 | 0 |  | 1 | TRUE | wye
187 | LV_2618-1_0_6_load_269 | 224 | 0.0023458 | 0.00058791 | 0 | 0 |  | 1 | TRUE | wye
188 | LV_2618-1_0_6_load_244 | 225 | 0.0015768 | 0.00039518 | 0 | 0 |  | 1 | TRUE | wye
189 | LV_2618-1_0_6_load_170 | 226 | 0.0023796 | 0.00059639 | 0 | 0 |  | 1 | TRUE | wye
190 | LV_2618-1_0_6_load_184 | 227 | 0.0010563 | 0.00026473 | 0 | 0 |  | 1 | TRUE | wye
191 | LV_2618-1_0_6_load_185 | 228 | 0.0010486 | 0.00026279 | 0 | 0 |  | 1 | TRUE | wye
192 | LV_2618-1_0_6_load_174 | 229 | 0.0029229 | 0.00073254 | 0 | 0 |  | 1 | TRUE | wye
193 | LV_2618-1_0_6_load_175 | 230 | 0.0015093 | 0.00037827 | 0 | 0 |  | 1 | TRUE | wye
194 | LV_2618-1_0_6_load_255 | 231 | 0.002549 | 0.00063883 | 0 | 0 |  | 1 | TRUE | wye
195 | LV_2618-1_0_6_load_178 | 232 | 0.0014187 | 0.00035555 | 0 | 0 |  | 1 | TRUE | wye
196 | LV_2618-1_0_6_load_287 | 235 | 0.0022846 | 0.00057258 | 0 | 0 |  | 1 | TRUE | wye
197 | LV_2618-1_0_6_load_214 | 236 | 0.0026323 | 0.00065971 | 0 | 0 |  | 1 | TRUE | wye
198 | LV_2618-1_0_6_load_176 | 237 | 0.0015245 | 0.00038206 | 0 | 0 |  | 1 | TRUE | wye
199 | LV_2618-1_0_6_load_177 | 238 | 0.0014513 | 0.00036372 | 0 | 0 |  | 1 | TRUE | wye
200 | LV_2618-1_0_6_load_201 | 239 | 0.0027198 | 0.00068165 | 0 | 0 |  | 1 | TRUE | wye
201 | LV_2618-1_0_6_load_202 | 240 | 0.0018647 | 0.00046733 | 0 | 0 |  | 1 | TRUE | wye
202 | LV_2618-1_0_6_load_215 | 241 | 0.0029892 | 0.00074917 | 0 | 0 |  | 1 | TRUE | wye
203 | LV_2618-1_0_6_load_208 | 242 | 0.0023229 | 0.00058217 | 0 | 0 |  | 1 | TRUE | wye
204 | LV_2618-1_0_6_load_187 | 243 | 0.0017342 | 0.00043463 | 0 | 0 |  | 1 | TRUE | wye
205 | LV_2618-1_0_6_load_191 | 245 | 0.0025009 | 0.00062679 | 0 | 0 |  | 1 | TRUE | wye
206 | LV_2618-1_0_6_load_192 | 246 | 0.0013837 | 0.00034678 | 0 | 0 |  | 1 | TRUE | wye
207 | LV_2618-1_0_6_load_229 | 247 | 0.0021729 | 0.00054459 | 0 | 0 |  | 1 | TRUE | wye
208 | LV_2618-1_0_6_load_227 | 248 | 0.003667 | 0.00091905 | 0 | 0 |  | 1 | TRUE | wye
209 | LV_2618-1_0_6_load_194 | 249 | 0.0013151 | 0.00032959 | 0 | 0 |  | 1 | TRUE | wye
210 | LV_2618-1_0_6_load_203 | 250 | 0.0010468 | 0.00026236 | 0 | 0 |  | 1 | TRUE | wye
211 | LV_2618-1_0_6_load_243 | 251 | 0.0010754 | 0.00026953 | 0 | 0 |  | 1 | TRUE | wye
212 | LV_2618-1_0_6_load_273 | 252 | 0.0010586 | 0.00026532 | 0 | 0 |  | 1 | TRUE | wye
213 | LV_2618-1_0_6_load_248 | 253 | 0.0024256 | 0.00060792 | 0 | 0 |  | 1 | TRUE | wye
214 | LV_2618-1_0_6_load_213 | 255 | 0.00143 | 0.0003584 | 0 | 0 |  | 1 | TRUE | wye
215 | LV_2618-1_0_6_load_223 | 256 | 0.0019489 | 0.00048843 | 0 | 0 |  | 1 | TRUE | wye
216 | LV_2618-1_0_6_load_220 | 257 | 0.01185 | 0.0029699 | 0 | 0 |  | 1 | TRUE | wye
217 | LV_2618-1_0_6_load_247 | 259 | 0.0068789 | 0.001724 | 0 | 0 |  | 1 | TRUE | wye
218 | LV_2618-1_0_6_load_221 | 260 | 0.0014439 | 0.00036188 | 0 | 0 |  | 1 | TRUE | wye
219 | LV_2618-1_0_6_load_219 | 261 | 0.0016072 | 0.00040281 | 0 | 0 |  | 1 | TRUE | wye
220 | LV_2618-1_0_6_load_217 | 262 | 0.005788 | 0.0014506 | 0 | 0 |  | 1 | TRUE | wye
221 | LV_2618-1_0_6_load_258 | 263 | 0.0016043 | 0.00040207 | 0 | 0 |  | 1 | TRUE | wye
222 | LV_2618-1_0_6_load_222 | 264 | 0.0019871 | 0.00049803 | 0 | 0 |  | 1 | TRUE | wye
223 | LV_2618-1_0_6_load_240 | 265 | 0.0016675 | 0.00041792 | 0 | 0 |  | 1 | TRUE | wye
224 | LV_2618-1_0_6_load_228 | 266 | 0.0017934 | 0.00044948 | 0 | 0 |  | 1 | TRUE | wye
225 | LV_2618-1_0_6_load_230 | 267 | 0.0019614 | 0.00049158 | 0 | 0 |  | 1 | TRUE | wye
226 | LV_2618-1_0_6_load_249 | 268 | 0.0021247 | 0.0005325 | 0 | 0 |  | 1 | TRUE | wye
227 | LV_2618-1_0_6_load_233 | 269 | 0.002954 | 0.00074035 | 0 | 0 |  | 1 | TRUE | wye
228 | LV_2618-1_0_6_load_241 | 271 | 0.0014287 | 0.00035807 | 0 | 0 |  | 1 | TRUE | wye
229 | LV_2618-1_0_6_load_251 | 272 | 0.0014295 | 0.00035827 | 0 | 0 |  | 1 | TRUE | wye
230 | LV_2618-1_0_6_load_265 | 273 | 0.0024536 | 0.00061493 | 0 | 0 |  | 1 | TRUE | wye
231 | LV_2618-1_0_6_load_266 | 274 | 0.0024795 | 0.00062143 | 0 | 0 |  | 1 | TRUE | wye
232 | LV_2618-1_0_6_load_250 | 275 | 0.0014217 | 0.00035631 | 0 | 0 |  | 1 | TRUE | wye
233 | LV_2618-1_0_6_load_252 | 276 | 0.0014506 | 0.00036356 | 0 | 0 |  | 1 | TRUE | wye
234 | LV_2618-1_0_6_load_253 | 277 | 0.0015189 | 0.00038067 | 0 | 0 |  | 1 | TRUE | wye
235 | LV_2618-1_0_6_load_267 | 278 | 0.0058868 | 0.0014754 | 0 | 0 |  | 1 | TRUE | wye
236 | LV_2618-1_0_6_load_263 | 279 | 0.0010742 | 0.00026922 | 0 | 0 |  | 1 | TRUE | wye
237 | LV_2618-1_0_6_load_271 | 280 | 0.0014653 | 0.00036723 | 0 | 0 |  | 1 | TRUE | wye
238 | LV_2618-1_0_6_load_272 | 281 | 0.0036639 | 0.00091827 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 94 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2618-1_0_6_line_0 |  | 0 | 1 | 0.0065934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2618-1_0_6_line_1 |  | 1 | 4 | 0.023281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2618-1_0_6_line_2 |  | 2 | 3 | 0.030837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2618-1_0_6_line_3 |  | 3 | 5 | 0.015368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2618-1_0_6_line_4 |  | 4 | 6 | 0.0094012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2618-1_0_6_line_5 |  | 5 | 7 | 0.022194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2618-1_0_6_line_6 |  | 5 | 8 | 0.014529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2618-1_0_6_line_7 |  | 6 | 9 | 0.016397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2618-1_0_6_line_8 |  | 7 | 115 | 0.0038268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2618-1_0_6_line_9 |  | 8 | 102 | 0.0087289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2618-1_0_6_line_10 |  | 9 | 53 | 0.017097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2618-1_0_6_line_11 |  | 10 | 11 | 0.018787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2618-1_0_6_line_12 |  | 10 | 12 | 0.011949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_2618-1_0_6_line_13 |  | 11 | 13 | 0.011555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_2618-1_0_6_line_14 |  | 12 | 14 | 0.018794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_2618-1_0_6_line_15 |  | 13 | 15 | 0.018332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_2618-1_0_6_line_16 |  | 14 | 16 | 0.0020115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2618-1_0_6_line_17 |  | 15 | 17 | 0.022534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2618-1_0_6_line_18 |  | 15 | 18 | 0.0049771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2618-1_0_6_line_19 |  | 16 | 19 | 0.024691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2618-1_0_6_line_20 |  | 16 | 20 | 0.015272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_2618-1_0_6_line_21 |  | 17 | 44 | 0.038556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2618-1_0_6_line_22 |  | 18 | 42 | 0.030363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2618-1_0_6_line_23 |  | 19 | 51 | 0.0087295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2618-1_0_6_line_24 |  | 20 | 52 | 0.0063463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2618-1_0_6_line_25 |  | 21 | 22 | 0.045291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2618-1_0_6_line_26 |  | 21 | 23 | 0.042672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2618-1_0_6_line_27 |  | 21 | 24 | 0.043636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2618-1_0_6_line_28 |  | 22 | 25 | 0.04007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2618-1_0_6_line_29 |  | 23 | 26 | 0.016733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2618-1_0_6_line_30 |  | 24 | 27 | 0.030979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2618-1_0_6_line_31 |  | 25 | 28 | 0.034813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2618-1_0_6_line_32 |  | 25 | 29 | 0.045705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2618-1_0_6_line_33 |  | 26 | 31 | 0.020252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2618-1_0_6_line_34 |  | 27 | 30 | 0.021963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2618-1_0_6_line_35 |  | 28 | 32 | 0.058253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2618-1_0_6_line_36 |  | 29 | 33 | 0.024189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2618-1_0_6_line_37 |  | 31 | 34 | 0.017252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2618-1_0_6_line_38 |  | 32 | 59 | 0.014025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2618-1_0_6_line_39 |  | 33 | 210 | 0.018041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2618-1_0_6_line_40 |  | 34 | 197 | 0.045678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2618-1_0_6_line_41 |  | 35 | 36 | 0.0087652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2618-1_0_6_line_42 |  | 35 | 37 | 0.0056912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2618-1_0_6_line_43 |  | 36 | 38 | 0.0063924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2618-1_0_6_line_44 |  | 37 | 39 | 0.006407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2618-1_0_6_line_45 |  | 38 | 40 | 0.0064035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2618-1_0_6_line_46 |  | 39 | 41 | 0.0063993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2618-1_0_6_line_47 |  | 40 | 42 | 0.0032567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2618-1_0_6_line_48 |  | 41 | 43 | 0.0097575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2618-1_0_6_line_49 |  | 43 | 90 | 0.026395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2618-1_0_6_line_50 |  | 44 | 254 | 0.041524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2618-1_0_6_line_51 |  | 44 | 255 | 0.017371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_2618-1_0_6_line_52 |  | 45 | 46 | 0.010434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2618-1_0_6_line_53 |  | 46 | 47 | 0.05729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2618-1_0_6_line_54 |  | 47 | 48 | 0.011003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2618-1_0_6_line_55 |  | 47 | 49 | 0.026582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2618-1_0_6_line_56 |  | 48 | 50 | 0.015256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2618-1_0_6_line_57 |  | 50 | 78 | 0.014085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2618-1_0_6_line_58 |  | 51 | 212 | 0.0058113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2618-1_0_6_line_59 |  | 52 | 113 | 0.010354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2618-1_0_6_line_60 |  | 53 | 54 | 0.01092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2618-1_0_6_line_61 |  | 54 | 55 | 0.013882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2618-1_0_6_line_62 |  | 54 | 56 | 0.024088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2618-1_0_6_line_63 |  | 56 | 57 | 0.036062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2618-1_0_6_line_64 |  | 57 | 58 | 0.028163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2618-1_0_6_line_65 |  | 58 | 67 | 0.013256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2618-1_0_6_line_66 |  | 59 | 60 | 0.048774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2618-1_0_6_line_67 |  | 60 | 61 | 0.24686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2618-1_0_6_line_68 |  | 61 | 62 | 0.043739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2618-1_0_6_line_69 |  | 63 | 64 | 0.034844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2618-1_0_6_line_70 |  | 63 | 65 | 0.022117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2618-1_0_6_line_71 |  | 65 | 66 | 0.025988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2618-1_0_6_line_72 |  | 65 | 67 | 0.013864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2618-1_0_6_line_73 |  | 66 | 70 | 0.035687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2618-1_0_6_line_74 |  | 67 | 71 | 0.050857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2618-1_0_6_line_75 |  | 68 | 69 | 0.013332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2618-1_0_6_line_76 |  | 69 | 72 | 0.0083212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_2618-1_0_6_line_77 |  | 69 | 73 | 0.003201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2618-1_0_6_line_78 |  | 70 | 74 | 0.015332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_2618-1_0_6_line_79 |  | 70 | 75 | 0.022505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_2618-1_0_6_line_80 |  | 70 | 76 | 0.013357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2618-1_0_6_line_81 |  | 71 | 77 | 0.021485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2618-1_0_6_line_82 |  | 72 | 225 | 0.019222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_2618-1_0_6_line_83 |  | 73 | 128 | 0.051401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2618-1_0_6_line_84 |  | 73 | 218 | 0.035892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2618-1_0_6_line_85 |  | 74 | 222 | 0.026509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_2618-1_0_6_line_86 |  | 75 | 223 | 0.006698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_2618-1_0_6_line_87 |  | 77 | 241 | 0.021799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2618-1_0_6_line_88 |  | 78 | 273 | 0.022611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2618-1_0_6_line_89 |  | 79 | 80 | 0.014731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2618-1_0_6_line_90 |  | 79 | 81 | 0.01531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2618-1_0_6_line_91 |  | 80 | 82 | 0.017459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2618-1_0_6_line_92 |  | 81 | 83 | 0.014485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2618-1_0_6_line_93 |  | 82 | 84 | 0.020555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2618-1_0_6_line_94 |  | 83 | 85 | 0.022354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2618-1_0_6_line_95 |  | 83 | 86 | 0.02989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2618-1_0_6_line_96 |  | 84 | 87 | 0.0023988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2618-1_0_6_line_97 |  | 85 | 88 | 0.01419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2618-1_0_6_line_98 |  | 86 | 89 | 0.01047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2618-1_0_6_line_99 |  | 87 | 142 | 0.023557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2618-1_0_6_line_100 |  | 88 | 93 | 0.019604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2618-1_0_6_line_101 |  | 88 | 92 | 0.029015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2618-1_0_6_line_102 |  | 89 | 169 | 0.017624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2618-1_0_6_line_103 |  | 91 | 92 | 0.010895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2618-1_0_6_line_104 |  | 94 | 95 | 0.027784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_2618-1_0_6_line_105 |  | 94 | 96 | 0.03068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_2618-1_0_6_line_106 |  | 95 | 97 | 0.024401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_2618-1_0_6_line_107 |  | 96 | 98 | 0.02204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_2618-1_0_6_line_108 |  | 97 | 99 | 0.022437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2618-1_0_6_line_109 |  | 97 | 100 | 0.015258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_2618-1_0_6_line_110 |  | 98 | 101 | 0.016672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_2618-1_0_6_line_111 |  | 99 | 102 | 0.020079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2618-1_0_6_line_112 |  | 100 | 103 | 0.0014062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_2618-1_0_6_line_113 |  | 101 | 104 | 0.0056223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
114 | LV_2618-1_0_6_line_114 |  | 103 | 148 | 0.02382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_2618-1_0_6_line_115 |  | 104 | 131 | 0.03493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
116 | LV_2618-1_0_6_line_116 |  | 105 | 106 | 0.0069951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2618-1_0_6_line_117 |  | 105 | 107 | 0.011612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2618-1_0_6_line_118 |  | 106 | 108 | 0.021736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2618-1_0_6_line_119 |  | 108 | 109 | 0.031143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2618-1_0_6_line_120 |  | 109 | 110 | 0.030672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_2618-1_0_6_line_121 |  | 109 | 111 | 0.011412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
122 | LV_2618-1_0_6_line_122 |  | 110 | 148 | 0.006777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_2618-1_0_6_line_123 |  | 111 | 279 | 0.03257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2618-1_0_6_line_124 |  | 111 | 145 | 0.0027117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
125 | LV_2618-1_0_6_line_125 |  | 112 | 113 | 0.013574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2618-1_0_6_line_126 |  | 112 | 114 | 0.014243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2618-1_0_6_line_127 |  | 114 | 116 | 0.025535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2618-1_0_6_line_128 |  | 115 | 117 | 0.022241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2618-1_0_6_line_129 |  | 116 | 181 | 0.011753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2618-1_0_6_line_130 |  | 117 | 203 | 0.010725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2618-1_0_6_line_131 |  | 118 | 119 | 0.03217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2618-1_0_6_line_132 |  | 119 | 120 | 0.0080099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2618-1_0_6_line_133 |  | 120 | 269 | 0.0043882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2618-1_0_6_line_134 |  | 121 | 122 | 0.017173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2618-1_0_6_line_135 |  | 121 | 123 | 0.020625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2618-1_0_6_line_136 |  | 122 | 124 | 0.16539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2618-1_0_6_line_137 |  | 123 | 125 | 0.053362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2618-1_0_6_line_138 |  | 124 | 127 | 0.028366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2618-1_0_6_line_139 |  | 125 | 128 | 0.021107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2618-1_0_6_line_140 |  | 125 | 129 | 0.0012074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2618-1_0_6_line_141 |  | 126 | 127 | 0.026351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2618-1_0_6_line_142 |  | 129 | 130 | 0.021617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2618-1_0_6_line_143 |  | 130 | 157 | 0.01214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2618-1_0_6_line_144 |  | 131 | 132 | 0.013819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
145 | LV_2618-1_0_6_line_145 |  | 132 | 133 | 0.0067519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
146 | LV_2618-1_0_6_line_146 |  | 133 | 224 | 0.015171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
147 | LV_2618-1_0_6_line_147 |  | 134 | 135 | 0.011597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
148 | LV_2618-1_0_6_line_148 |  | 134 | 136 | 0.0068162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
149 | LV_2618-1_0_6_line_149 |  | 135 | 137 | 0.013861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
150 | LV_2618-1_0_6_line_150 |  | 136 | 138 | 0.017611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
151 | LV_2618-1_0_6_line_151 |  | 137 | 139 | 0.013011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
152 | LV_2618-1_0_6_line_152 |  | 138 | 140 | 0.016692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
153 | LV_2618-1_0_6_line_153 |  | 138 | 141 | 0.02719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_2618-1_0_6_line_154 |  | 138 | 142 | 0.027874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_2618-1_0_6_line_155 |  | 139 | 143 | 0.017133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
156 | LV_2618-1_0_6_line_156 |  | 139 | 144 | 0.019538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_2618-1_0_6_line_157 |  | 140 | 145 | 0.03306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
158 | LV_2618-1_0_6_line_158 |  | 141 | 146 | 0.018263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_2618-1_0_6_line_159 |  | 142 | 147 | 0.022056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_2618-1_0_6_line_160 |  | 143 | 263 | 0.029886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
161 | LV_2618-1_0_6_line_161 |  | 144 | 183 | 0.0092178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_2618-1_0_6_line_162 |  | 146 | 243 | 0.020171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_2618-1_0_6_line_163 |  | 147 | 253 | 0.033804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_2618-1_0_6_line_164 |  | 149 | 150 | 0.0070346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_2618-1_0_6_line_165 |  | 149 | 151 | 0.031504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_2618-1_0_6_line_166 |  | 150 | 152 | 0.022657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_2618-1_0_6_line_167 |  | 151 | 153 | 0.034426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_2618-1_0_6_line_168 |  | 151 | 154 | 0.0043604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_2618-1_0_6_line_169 |  | 152 | 155 | 0.014912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_2618-1_0_6_line_170 |  | 154 | 156 | 0.015921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_2618-1_0_6_line_171 |  | 155 | 157 | 0.010896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_2618-1_0_6_line_172 |  | 156 | 158 | 0.044417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_2618-1_0_6_line_173 |  | 158 | 190 | 0.00090518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_2618-1_0_6_line_174 |  | 159 | 160 | 0.021401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_2618-1_0_6_line_175 |  | 159 | 161 | 0.017113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_2618-1_0_6_line_176 |  | 159 | 162 | 0.28496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_2618-1_0_6_line_177 |  | 160 | 163 | 0.013473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_2618-1_0_6_line_178 |  | 161 | 164 | 0.0034599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_2618-1_0_6_line_179 |  | 162 | 165 | 0.012375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_2618-1_0_6_line_180 |  | 163 | 168 | 0.01604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_2618-1_0_6_line_181 |  | 164 | 169 | 0.021332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_2618-1_0_6_line_182 |  | 165 | 166 | 0.0078712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_2618-1_0_6_line_183 |  | 166 | 167 | 0.00046386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_2618-1_0_6_line_184 |  | 168 | 170 | 0.022677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_2618-1_0_6_line_185 |  | 170 | 186 | 0.014376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_2618-1_0_6_line_186 |  | 171 | 172 | 0.015242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_2618-1_0_6_line_187 |  | 171 | 173 | 0.017752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_2618-1_0_6_line_188 |  | 172 | 174 | 0.0072107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
189 | LV_2618-1_0_6_line_189 |  | 173 | 175 | 0.01118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
190 | LV_2618-1_0_6_line_190 |  | 174 | 176 | 0.020701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
191 | LV_2618-1_0_6_line_191 |  | 176 | 177 | 0.0012037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
192 | LV_2618-1_0_6_line_192 |  | 177 | 180 | 0.020591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
193 | LV_2618-1_0_6_line_193 |  | 178 | 179 | 0.019234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
194 | LV_2618-1_0_6_line_194 |  | 179 | 194 | 0.0061397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
195 | LV_2618-1_0_6_line_195 |  | 180 | 215 | 0.009849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
196 | LV_2618-1_0_6_line_196 |  | 182 | 183 | 0.0088161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
197 | LV_2618-1_0_6_line_197 |  | 182 | 184 | 0.0028213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
198 | LV_2618-1_0_6_line_198 |  | 184 | 185 | 0.0038513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_2618-1_0_6_line_199 |  | 186 | 187 | 0.025474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
200 | LV_2618-1_0_6_line_200 |  | 187 | 188 | 0.012523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
201 | LV_2618-1_0_6_line_201 |  | 188 | 189 | 0.016745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
202 | LV_2618-1_0_6_line_202 |  | 190 | 191 | 0.025893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
203 | LV_2618-1_0_6_line_203 |  | 191 | 192 | 0.020093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
204 | LV_2618-1_0_6_line_204 |  | 192 | 193 | 0.033018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
205 | LV_2618-1_0_6_line_205 |  | 193 | 219 | 0.026419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
206 | LV_2618-1_0_6_line_206 |  | 194 | 195 | 0.052553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
207 | LV_2618-1_0_6_line_207 |  | 195 | 196 | 0.0028914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
208 | LV_2618-1_0_6_line_208 |  | 196 | 226 | 0.022387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
209 | LV_2618-1_0_6_line_209 |  | 197 | 198 | 0.02243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
210 | LV_2618-1_0_6_line_210 |  | 198 | 199 | 0.0064417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
211 | LV_2618-1_0_6_line_211 |  | 199 | 200 | 0.010118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
212 | LV_2618-1_0_6_line_212 |  | 199 | 201 | 0.024316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
213 | LV_2618-1_0_6_line_213 |  | 200 | 202 | 0.01224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
214 | LV_2618-1_0_6_line_214 |  | 201 | 203 | 0.0053293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
215 | LV_2618-1_0_6_line_215 |  | 202 | 204 | 0.009513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
216 | LV_2618-1_0_6_line_216 |  | 204 | 249 | 0.0076084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
217 | LV_2618-1_0_6_line_217 |  | 205 | 206 | 0.0087375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
218 | LV_2618-1_0_6_line_218 |  | 206 | 209 | 0.0069253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
219 | LV_2618-1_0_6_line_219 |  | 207 | 208 | 0.023179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
220 | LV_2618-1_0_6_line_220 |  | 208 | 210 | 0.010151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
221 | LV_2618-1_0_6_line_221 |  | 209 | 213 | 0.010256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
222 | LV_2618-1_0_6_line_222 |  | 211 | 212 | 0.01301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
223 | LV_2618-1_0_6_line_223 |  | 213 | 214 | 0.00081918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
224 | LV_2618-1_0_6_line_224 |  | 214 | 249 | 0.0078349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
225 | LV_2618-1_0_6_line_225 |  | 215 | 216 | 0.018126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
226 | LV_2618-1_0_6_line_226 |  | 216 | 217 | 0.0091659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
227 | LV_2618-1_0_6_line_227 |  | 217 | 218 | 0.015905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
228 | LV_2618-1_0_6_line_228 |  | 219 | 220 | 0.030649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
229 | LV_2618-1_0_6_line_229 |  | 220 | 221 | 0.007428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
230 | LV_2618-1_0_6_line_230 |  | 221 | 242 | 0.022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
231 | LV_2618-1_0_6_line_231 |  | 222 | 224 | 0.0067955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
232 | LV_2618-1_0_6_line_232 |  | 223 | 225 | 0.037807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
233 | LV_2618-1_0_6_line_233 |  | 226 | 227 | 0.0039873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
234 | LV_2618-1_0_6_line_234 |  | 227 | 228 | 0.0068523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
235 | LV_2618-1_0_6_line_235 |  | 228 | 242 | 0.012868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
236 | LV_2618-1_0_6_line_236 |  | 229 | 230 | 0.029195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
237 | LV_2618-1_0_6_line_237 |  | 229 | 231 | 0.04844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
238 | LV_2618-1_0_6_line_238 |  | 230 | 232 | 0.0028963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
239 | LV_2618-1_0_6_line_239 |  | 231 | 233 | 0.036275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
240 | LV_2618-1_0_6_line_240 |  | 232 | 236 | 0.017024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
241 | LV_2618-1_0_6_line_241 |  | 233 | 278 | 0.05348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
242 | LV_2618-1_0_6_line_242 |  | 233 | 234 | 0.030709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
243 | LV_2618-1_0_6_line_243 |  | 234 | 235 | 0.046932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
244 | LV_2618-1_0_6_line_244 |  | 235 | 237 | 0.055155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
245 | LV_2618-1_0_6_line_245 |  | 236 | 241 | 0.0065853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
246 | LV_2618-1_0_6_line_246 |  | 237 | 238 | 0.0084605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
247 | LV_2618-1_0_6_line_247 |  | 238 | 239 | 0.026559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
248 | LV_2618-1_0_6_line_248 |  | 239 | 240 | 0.022181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
249 | LV_2618-1_0_6_line_249 |  | 240 | 250 | 0.014179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
250 | LV_2618-1_0_6_line_250 |  | 243 | 244 | 0.034854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
251 | LV_2618-1_0_6_line_251 |  | 244 | 245 | 0.048104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
252 | LV_2618-1_0_6_line_252 |  | 244 | 246 | 0.04488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
253 | LV_2618-1_0_6_line_253 |  | 245 | 247 | 0.0012739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
254 | LV_2618-1_0_6_line_254 |  | 247 | 248 | 0.033194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
255 | LV_2618-1_0_6_line_255 |  | 248 | 266 | 0.0091249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
256 | LV_2618-1_0_6_line_256 |  | 250 | 251 | 0.00684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
257 | LV_2618-1_0_6_line_257 |  | 251 | 252 | 0.011327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
258 | LV_2618-1_0_6_line_258 |  | 254 | 256 | 0.023763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
259 | LV_2618-1_0_6_line_259 |  | 254 | 257 | 0.024833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
260 | LV_2618-1_0_6_line_260 |  | 255 | 258 | 0.018936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
261 | LV_2618-1_0_6_line_261 |  | 256 | 259 | 0.010668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
262 | LV_2618-1_0_6_line_262 |  | 257 | 260 | 0.03497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
263 | LV_2618-1_0_6_line_263 |  | 258 | 261 | 0.010922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
264 | LV_2618-1_0_6_line_264 |  | 258 | 262 | 0.062521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
265 | LV_2618-1_0_6_line_265 |  | 259 | 265 | 0.010187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
266 | LV_2618-1_0_6_line_266 |  | 260 | 264 | 0.058234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
267 | LV_2618-1_0_6_line_267 |  | 261 | 263 | 0.0076077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
268 | LV_2618-1_0_6_line_268 |  | 265 | 270 | 0.0066291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
269 | LV_2618-1_0_6_line_269 |  | 266 | 267 | 0.0183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
270 | LV_2618-1_0_6_line_270 |  | 267 | 268 | 0.010984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
271 | LV_2618-1_0_6_line_271 |  | 269 | 270 | 0.016974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
272 | LV_2618-1_0_6_line_272 |  | 270 | 271 | 0.036939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
273 | LV_2618-1_0_6_line_273 |  | 271 | 272 | 0.0064647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
274 | LV_2618-1_0_6_line_274 |  | 272 | 275 | 0.00042197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
275 | LV_2618-1_0_6_line_275 |  | 273 | 274 | 0.024693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
276 | LV_2618-1_0_6_line_276 |  | 274 | 278 | 0.010438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
277 | LV_2618-1_0_6_line_277 |  | 275 | 276 | 0.0099038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
278 | LV_2618-1_0_6_line_278 |  | 276 | 277 | 0.029491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
279 | LV_2618-1_0_6_line_279 |  | 279 | 280 | 0.0018261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
280 | LV_2618-1_0_6_line_280 |  | 280 | 281 | 0.0055875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2618-1_0_6_trafo_60 | 0.63 MVA 20/0.4 kV | 282 | 94 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2612124.0883 | 1252399.5383 | 2612125.4051 | 1252399.4448 | 2612130.6214 | 1252398.672
1 | 2612153.6512 | 1252395.2598 | 2612130.6214 | 1252398.672
2 | 2612042.6541 | 1252395.1741 | 2612056.3224 | 1252399.8938 | 2612069.3495 | 1252402.0994 | 2612072.514 | 1252402.1058
3 | 2612030.9899 | 1252385.5776 | 2612035.7097 | 1252391.2353 | 2612041.8446 | 1252394.8945 | 2612042.6541 | 1252395.1741
4 | 2612153.6512 | 1252395.2598 | 2612162.951 | 1252393.8819
5 | 2612030.9899 | 1252385.5776 | 2612024.728 | 1252392.5251 | 2612012.4869 | 1252396.4027
6 | 2612030.9899 | 1252385.5776 | 2612035.538 | 1252379.127 | 2612040.5726 | 1252374.8032
7 | 2612179.0415 | 1252390.7408 | 2612165.2287 | 1252393.5444 | 2612162.951 | 1252393.8819
8 | 2612008.7969 | 1252397.3866 | 2612010.0797 | 1252397.1652 | 2612012.4869 | 1252396.4027
9 | 2612040.5726 | 1252374.8032 | 2612047.1945 | 1252369.1161
10 | 2612179.0415 | 1252390.7408 | 2612195.7968 | 1252387.34
11 | 2611933.6088 | 1252321.9717 | 2611924.9002 | 1252319.332 | 2611915.2277 | 1252318.7972
12 | 2611933.6088 | 1252321.9717 | 2611933.799 | 1252322.0294 | 2611943.8 | 1252328.1979
13 | 2611903.6868 | 1252318.5606 | 2611907.9993 | 1252318.3976 | 2611915.2277 | 1252318.7972
14 | 2611958.1035 | 1252340.3893 | 2611943.8 | 1252328.1979 | 2611943.8 | 1252328.1979
15 | 2611885.3675 | 1252319.253 | 2611903.6868 | 1252318.5606
16 | 2611959.6344 | 1252341.6941 | 2611958.1035 | 1252340.3893
17 | 2611885.3675 | 1252319.253 | 2611887.3879 | 1252312.6082 | 2611888.8491 | 1252306.4182 | 2611888.8609 | 1252300.5366 | 2611887.0026 | 1252297.7533
18 | 2611885.3675 | 1252319.253 | 2611880.4361 | 1252319.9268
19 | 2611959.6344 | 1252341.6941 | 2611947.1976 | 1252349.7966 | 2611938.0249 | 1252353.3805
20 | 2611959.6344 | 1252341.6941 | 2611971.4241 | 1252351.4019
21 | 2611858.3332 | 1252276.2265 | 2611860.5373 | 1252283.4578 | 2611861.9793 | 1252286.874 | 2611865.5 | 1252288.5266 | 2611887.0026 | 1252297.7533
22 | 2611880.4361 | 1252319.9268 | 2611867.6449 | 1252321.6748 | 2611850.1944 | 1252321.9473
23 | 2611930.0271 | 1252356.8556 | 2611933.0984 | 1252355.3053 | 2611938.0249 | 1252353.3805
24 | 2611977.0962 | 1252354.2484 | 2611971.4241 | 1252351.4019
25 | 2611789.6078 | 1252445.2745 | 2611763.8035 | 1252441.247 | 2611744.6395 | 1252441.8763
26 | 2611789.6078 | 1252445.2745 | 2611805.4355 | 1252447.7448 | 2611825.0947 | 1252450.2632 | 2611831.7057 | 1252451.9919
27 | 2611789.6078 | 1252445.2745 | 2611775.9178 | 1252486.7078
28 | 2611706.7561 | 1252434.3524 | 2611708.6144 | 1252437.1801 | 2611713.8991 | 1252439.6588 | 2611740.1687 | 1252442.0231 | 2611744.6395 | 1252441.8763
29 | 2611848.1261 | 1252454.2322 | 2611840.9476 | 1252454.4085 | 2611831.7057 | 1252451.9919
30 | 2611775.9178 | 1252486.7078 | 2611765.2945 | 1252488.6032 | 2611752.731 | 1252488.5784 | 2611745.1364 | 1252487.9038
31 | 2611706.7561 | 1252434.3524 | 2611695.6332 | 1252434.6196 | 2611682.7538 | 1252434.0161 | 2611672.1775 | 1252431.8621
32 | 2611706.7561 | 1252434.3524 | 2611721.9802 | 1252432.192 | 2611751.2865 | 1252424.3832
33 | 2611867.3986 | 1252449.002 | 2611858.6301 | 1252452.965 | 2611853.5118 | 1252454.1 | 2611848.1261 | 1252454.2322
34 | 2611745.1364 | 1252487.9038 | 2611740.313 | 1252487.4754 | 2611723.5371 | 1252484.0568
35 | 2611617.2303 | 1252412.7296 | 2611656.7107 | 1252427.6943 | 2611667.5401 | 1252430.9176 | 2611672.1775 | 1252431.8621
36 | 2611774.6597 | 1252418.1555 | 2611770.608 | 1252419.235 | 2611751.2865 | 1252424.3832
37 | 2611867.3986 | 1252449.002 | 2611882.1249 | 1252440.0146
38 | 2611617.2303 | 1252412.7296 | 2611603.8619 | 1252408.4889
39 | 2611792.0923 | 1252413.511 | 2611774.6597 | 1252418.1555
40 | 2611882.1249 | 1252440.0146 | 2611883.7777 | 1252439.0059 | 2611897.6991 | 1252431.6956 | 2611921.4884 | 1252421.6255 | 2611923.4169 | 1252420.5989
41 | 2611834.1644 | 1252321.1917 | 2611825.4133 | 1252320.6954
42 | 2611819.7312 | 1252320.3731 | 2611825.4133 | 1252320.6954
43 | 2611840.5465 | 1252321.5537 | 2611834.1644 | 1252321.1917
44 | 2611819.7312 | 1252320.3731 | 2611813.3345 | 1252320.0103
45 | 2611846.9398 | 1252321.9163 | 2611840.5465 | 1252321.5537
46 | 2611813.3345 | 1252320.0103 | 2611806.9455 | 1252319.648
47 | 2611846.9398 | 1252321.9163 | 2611848.0702 | 1252321.9804 | 2611850.1944 | 1252321.9473
48 | 2611806.9455 | 1252319.648 | 2611797.2037 | 1252319.0955
49 | 2611797.2037 | 1252319.0955 | 2611794.2363 | 1252318.9272 | 2611770.9125 | 1252316.7731
50 | 2611816.799 | 1252276.8999 | 2611837.2014 | 1252277.7966 | 2611848.8455 | 1252277.4751 | 2611855.9025 | 1252276.6997 | 2611858.3332 | 1252276.2265
51 | 2611858.3332 | 1252276.2265 | 2611863.897 | 1252275.0034 | 2611874.8388 | 1252270.9334
52 | 2612236.3906 | 1252446.0579 | 2612246.8245 | 1252446.0794
53 | 2612291.4693 | 1252426.7809 | 2612292.5358 | 1252432.8427 | 2612291.0996 | 1252437.6984 | 2612285.901 | 1252441.1789 | 2612277.6546 | 1252444.2639 | 2612268.196 | 1252446.1234 | 2612246.8245 | 1252446.0794
54 | 2612291.4693 | 1252426.7809 | 2612301.7236 | 1252430.7693
55 | 2612291.4693 | 1252426.7809 | 2612284.6947 | 1252422.3863 | 2612274.6145 | 1252414.6271 | 2612269.9373 | 1252411.221
56 | 2612315.6929 | 1252436.8932 | 2612304.2868 | 1252431.7662 | 2612301.7236 | 1252430.7693
57 | 2612315.6929 | 1252436.8932 | 2612329.6996 | 1252438.3737
58 | 2611930.0271 | 1252356.8556 | 2611924.8392 | 1252359.4742
59 | 2611977.0962 | 1252354.2484 | 2611986.3498 | 1252358.8924
60 | 2612206.4988 | 1252385.1678 | 2612195.7968 | 1252387.34
61 | 2612206.4988 | 1252385.1678 | 2612209.8353 | 1252388.2322 | 2612215.9752 | 1252389.4122 | 2612219.0186 | 1252389.9976
62 | 2612206.4988 | 1252385.1678 | 2612230.0989 | 1252380.3464
63 | 2612230.0989 | 1252380.3464 | 2612235.4869 | 1252379.2456 | 2612245.6297 | 1252378.6439 | 2612261.5635 | 1252380.1221 | 2612265.9289 | 1252380.6718
64 | 2612265.9289 | 1252380.6718 | 2612293.8708 | 1252384.1902
65 | 2612307.0929 | 1252384.7524 | 2612298.1889 | 1252384.7339 | 2612293.8708 | 1252384.1902
66 | 2611556.4735 | 1252407.9527 | 2611562.3562 | 1252405.6182 | 2611576.1172 | 1252403.021 | 2611585.3372 | 1252403.4725 | 2611594.5542 | 1252405.5363 | 2611603.8619 | 1252408.4889
67 | 2611556.4735 | 1252407.9527 | 2611424.279 | 1252199.4725
68 | 2611383.07 | 1252187.6748 | 2611397.2833 | 1252193.4169 | 2611419.1405 | 1252195.36 | 2611424.279 | 1252199.4725
69 | 2612339.5511 | 1252370.2756 | 2612368.0786 | 1252350.2694
70 | 2612319.4418 | 1252379.2298 | 2612335.8822 | 1252372.8486 | 2612339.5511 | 1252370.2756
71 | 2612319.4418 | 1252379.2298 | 2612322.6142 | 1252374.033 | 2612321.9136 | 1252369.8288 | 2612320.2144 | 1252355.9273 | 2612320.2507 | 1252354.2952
72 | 2612307.0929 | 1252384.7524 | 2612317.2408 | 1252381.6824 | 2612319.4418 | 1252379.2298
73 | 2612320.5859 | 1252318.6147 | 2612320.7302 | 1252332.7465 | 2612320.2507 | 1252354.2952
74 | 2612307.0929 | 1252384.7524 | 2612310.9095 | 1252389.152 | 2612316.7487 | 1252393.4002 | 2612328.1543 | 1252398.8162 | 2612341.1786 | 1252402.3455 | 2612349.8085 | 1252403.5309 | 2612352.7832 | 1252403.7159
75 | 2612413.2021 | 1252323.299 | 2612401.7291 | 1252330.089
76 | 2612413.2021 | 1252323.299 | 2612410.4017 | 1252320.1022 | 2612407.4996 | 1252318.6063 | 2612406.7123 | 1252318.4322
77 | 2612413.2021 | 1252323.299 | 2612416.0049 | 1252321.7372
78 | 2612320.5859 | 1252318.6147 | 2612307.4843 | 1252319.5772 | 2612305.3047 | 1252319.3178
79 | 2612320.5859 | 1252318.6147 | 2612334.6068 | 1252318.3102 | 2612343.0872 | 1252318.3674
80 | 2612320.5859 | 1252318.6147 | 2612322.1307 | 1252305.3473
81 | 2612374.2494 | 1252403.7351 | 2612359.6092 | 1252404.1405 | 2612352.7832 | 1252403.7159
82 | 2612387.5909 | 1252318.6327 | 2612397.1012 | 1252318.6847 | 2612404.3016 | 1252317.8992 | 2612406.7123 | 1252318.4322
83 | 2612416.0049 | 1252321.7372 | 2612444.6885 | 1252302.8958 | 2612458.9691 | 1252293.5211
84 | 2612416.0049 | 1252321.7372 | 2612426.3669 | 1252335.4789 | 2612433.6757 | 1252340.5975 | 2612441.1327 | 1252343.3927 | 2612442.9257 | 1252343.3243
85 | 2612305.3047 | 1252319.3178 | 2612278.9811 | 1252316.1857
86 | 2612343.0872 | 1252318.3674 | 2612349.785 | 1252318.4126
87 | 2612374.2494 | 1252403.7351 | 2612396.0398 | 1252403.1318
88 | 2612352.1852 | 1252440.7504 | 2612329.6996 | 1252438.3737
89 | 2611965.8336 | 1252125.4014 | 2611971.309 | 1252139.0765
90 | 2611965.8336 | 1252125.4014 | 2611964.0547 | 1252120.9586 | 2611959.1672 | 1252111.6379
91 | 2611971.309 | 1252139.0765 | 2611977.7988 | 1252155.285
92 | 2611952.4404 | 1252098.8097 | 2611959.1672 | 1252111.6379
93 | 2611986.6051 | 1252173.8551 | 2611978.3207 | 1252156.5883 | 2611977.7988 | 1252155.285
94 | 2611952.4404 | 1252098.8097 | 2611940.2755 | 1252098.9965 | 2611930.09 | 1252098.8042
95 | 2611952.4404 | 1252098.8097 | 2611945.0981 | 1252083.7073 | 2611941.6821 | 1252071.0632
96 | 2611986.6051 | 1252173.8551 | 2611987.3607 | 1252175.4299 | 2611987.6626 | 1252176.0079
97 | 2611915.9023 | 1252098.5363 | 2611930.09 | 1252098.8042
98 | 2611938.9513 | 1252060.9551 | 2611941.6821 | 1252071.0632
99 | 2611998.5686 | 1252196.8888 | 2611987.6626 | 1252176.0079
100 | 2611922.6419 | 1252116.9507 | 2611915.9023 | 1252098.5363
101 | 2611886.8545 | 1252099.8124 | 2611897.3603 | 1252099.0551 | 2611906.8925 | 1252098.3737 | 2611910.3712 | 1252098.4363 | 2611915.9023 | 1252098.5363
102 | 2611938.9513 | 1252060.9551 | 2611938.7086 | 1252060.0568 | 2611935.8538 | 1252043.6095
103 | 2611886.8545 | 1252099.8124 | 2611888.8403 | 1252110.5245
104 | 2612104.4898 | 1252335.516 | 2612109.3986 | 1252333.6025 | 2612130.3224 | 1252325.2878
105 | 2612158.789 | 1252313.8458 | 2612140.6034 | 1252321.2024 | 2612130.3224 | 1252325.2878
106 | 2612081.826 | 1252344.7204 | 2612091.8026 | 1252340.5157 | 2612104.4898 | 1252335.516
107 | 2612158.789 | 1252313.8458 | 2612173.2036 | 1252309.2055 | 2612179.9303 | 1252307.6851
108 | 2612081.826 | 1252344.7204 | 2612073.8945 | 1252348.807 | 2612066.7999 | 1252353.3067 | 2612062.7627 | 1252356.4445
109 | 2612081.826 | 1252344.7204 | 2612074.7494 | 1252331.2024
110 | 2612179.9303 | 1252307.6851 | 2612181.1984 | 1252307.3984 | 2612191.9008 | 1252306.2974 | 2612196.5109 | 1252306.4639
111 | 2612062.7627 | 1252356.4445 | 2612054.2011 | 1252363.0987 | 2612047.1945 | 1252369.1161
112 | 2612074.7494 | 1252331.2024 | 2612074.0972 | 1252329.9566
113 | 2612196.5109 | 1252306.4639 | 2612202.1295 | 1252306.6667
114 | 2612062.8948 | 1252308.9356 | 2612072.9638 | 1252327.7914 | 2612074.0972 | 1252329.9566
115 | 2612236.8359 | 1252310.4483 | 2612222.201 | 1252308.3053 | 2612203 | 1252306.6982 | 2612202.1295 | 1252306.6667
116 | 2612102.5888 | 1252258.6501 | 2612095.8904 | 1252260.6656
117 | 2612113.7082 | 1252255.3045 | 2612102.5888 | 1252258.6501
118 | 2612075.0766 | 1252266.9282 | 2612095.8904 | 1252260.6656
119 | 2612045.2546 | 1252275.9013 | 2612075.0766 | 1252266.9282
120 | 2612045.2546 | 1252275.9013 | 2612059.7026 | 1252302.9576
121 | 2612045.2546 | 1252275.9013 | 2612039.5548 | 1252266.0056
122 | 2612062.8948 | 1252308.9356 | 2612059.7026 | 1252302.9576
123 | 2612039.5548 | 1252266.0056 | 2612011.0449 | 1252281.7522
124 | 2612039.5548 | 1252266.0056 | 2612038.1613 | 1252263.6793
125 | 2611999.146 | 1252363.4211 | 2611986.3498 | 1252358.8924 | 2611986.3498 | 1252358.8924
126 | 2611999.146 | 1252363.4211 | 2612012.6106 | 1252358.7759
127 | 2612033.1403 | 1252343.8603 | 2612024.8732 | 1252350.5312 | 2612015.6149 | 1252357.7395 | 2612012.6106 | 1252358.7759
128 | 2611986.8796 | 1252401.1698 | 2612008.7969 | 1252397.3866
129 | 2612042.2872 | 1252336.4794 | 2612033.1403 | 1252343.8603
130 | 2611986.8796 | 1252401.1698 | 2611978.3084 | 1252402.6493 | 2611976.2985 | 1252402.9134
131 | 2611736.299 | 1252276.5844 | 2611728.6015 | 1252277.1035 | 2611704.4889 | 1252281.1807
132 | 2611736.299 | 1252276.5844 | 2611744.2908 | 1252276.0455
133 | 2611748.669 | 1252275.7503 | 2611744.2908 | 1252276.0455
134 | 2612495.4624 | 1252192.945 | 2612491.6502 | 1252209.6891
135 | 2612486.9051 | 1252229.7595 | 2612488.3636 | 1252224.1246 | 2612491.6502 | 1252209.6891
136 | 2612495.4624 | 1252192.945 | 2612455.5093 | 1252032.4512
137 | 2612476.6139 | 1252281.9378 | 2612478.0358 | 1252276.8041 | 2612478.4446 | 1252272.58 | 2612479.6832 | 1252257.6617 | 2612486.9051 | 1252229.7595
138 | 2612437.9767 | 1252012.1138 | 2612441.8326 | 1252023.029 | 2612450.2618 | 1252030.2514 | 2612455.5093 | 1252032.4512
139 | 2612476.6139 | 1252281.9378 | 2612458.9691 | 1252293.5211
140 | 2612476.6139 | 1252281.9378 | 2612477.6733 | 1252281.3585
141 | 2612437.9767 | 1252012.1138 | 2612441.1114 | 1252010.6528 | 2612444.5866 | 1252001.5986 | 2612442.8087 | 1251996.536 | 2612435.8726 | 1251992.9055
142 | 2612477.6733 | 1252281.3585 | 2612491.4588 | 1252273.8192 | 2612496.964 | 1252271.6841
143 | 2612508.3456 | 1252267.4798 | 2612506.2005 | 1252268.1019 | 2612496.964 | 1252271.6841
144 | 2612250.5095 | 1252312.4505 | 2612236.8359 | 1252310.4483
145 | 2612250.5095 | 1252312.4505 | 2612257.1901 | 1252313.4288
146 | 2612257.1901 | 1252313.4288 | 2612263.1705 | 1252314.3045 | 2612272.2332 | 1252315.3828
147 | 2611977.6611 | 1252229.0754 | 2611988.8666 | 1252226.0867
148 | 2611995.4525 | 1252224.3301 | 2611988.8666 | 1252226.0867
149 | 2611977.6611 | 1252229.0754 | 2611967.8013 | 1252231.7052 | 2611964.3123 | 1252232.8008
150 | 2612012.5934 | 1252220.9995 | 2612006.3979 | 1252221.0981 | 2611999.7003 | 1252223.1971 | 2611995.4525 | 1252224.3301
151 | 2611951.8994 | 1252236.6987 | 2611964.3123 | 1252232.8008
152 | 2612012.5934 | 1252220.9995 | 2612021.1715 | 1252235.3188
153 | 2612012.5934 | 1252220.9995 | 2612038.5766 | 1252212.99
154 | 2611998.5686 | 1252196.8888 | 2612011.2097 | 1252218.6173 | 2612012.5934 | 1252220.9995
155 | 2611951.8994 | 1252236.6987 | 2611939.5016 | 1252240.2985 | 2611935.6343 | 1252241.9946
156 | 2611951.8994 | 1252236.6987 | 2611953.9624 | 1252242.729 | 2611959.0431 | 1252254.8733
157 | 2612038.1613 | 1252263.6793 | 2612021.1715 | 1252235.3188
158 | 2612038.5766 | 1252212.99 | 2612056.0295 | 1252207.61
159 | 2611998.5686 | 1252196.8888 | 2612019.6913 | 1252190.5389
160 | 2611908.6281 | 1252254.7787 | 2611925.5972 | 1252246.3968 | 2611935.6343 | 1252241.9946
161 | 2611959.0431 | 1252254.8733 | 2611961.1644 | 1252259.9437 | 2611960.7797 | 1252263.6453 | 2611960.7797 | 1252263.6453
162 | 2612056.0295 | 1252207.61 | 2612075.3051 | 1252201.6682
163 | 2612019.6913 | 1252190.5389 | 2612052.0641 | 1252180.807
164 | 2612562.888 | 1252259.7466 | 2612558.3766 | 1252259.3727 | 2612555.87 | 1252259.4463
165 | 2612594.082 | 1252263.9734 | 2612574.6202 | 1252260.719 | 2612562.888 | 1252259.7466
166 | 2612533.3365 | 1252261.1402 | 2612539.6463 | 1252259.9225 | 2612555.87 | 1252259.4463
167 | 2612594.082 | 1252263.9734 | 2612597.3493 | 1252249.771 | 2612596.0405 | 1252240.64 | 2612586.2016 | 1252236.5499
168 | 2612594.082 | 1252263.9734 | 2612598.3422 | 1252264.9027
169 | 2612518.81 | 1252264.4449 | 2612523.9745 | 1252262.947 | 2612533.3365 | 1252261.1402
170 | 2612598.3422 | 1252264.9027 | 2612613.8973 | 1252268.296
171 | 2612518.81 | 1252264.4449 | 2612508.3456 | 1252267.4798
172 | 2612613.8973 | 1252268.296 | 2612657.2938 | 1252277.763
173 | 2612657.2938 | 1252277.763 | 2612658.1782 | 1252277.9559
174 | 2611968.6514 | 1252015.8372 | 2611962.9653 | 1252013.4528 | 2611957.3301 | 1252012.5186 | 2611947.9599 | 1252014.2168
175 | 2611931.614 | 1252019.1825 | 2611944.4665 | 1252014.8499 | 2611947.9599 | 1252014.2168
176 | 2611947.9599 | 1252014.2168 | 2611959.2042 | 1251729.482
177 | 2611968.6514 | 1252015.8372 | 2611978.9499 | 1252020.1559 | 2611981.0562 | 1252021.093
178 | 2611931.614 | 1252019.1825 | 2611932.2057 | 1252022.5914
179 | 2611959.2042 | 1251729.482 | 2611966.2019 | 1251728.5065 | 2611970.8032 | 1251725.8565
180 | 2611995.7115 | 1252027.6128 | 2611981.0562 | 1252021.093
181 | 2611932.2057 | 1252022.5914 | 2611935.8538 | 1252043.6095
182 | 2611970.8032 | 1251725.8565 | 2611976.8021 | 1251722.4016 | 2611977.6285 | 1251721.936
183 | 2611978.0327 | 1251721.7084 | 2611977.6285 | 1251721.936
184 | 2611995.7115 | 1252027.6128 | 2612008.173 | 1252033.1566 | 2612015.6076 | 1252038.2955
185 | 2612027.2733 | 1252046.6948 | 2612019.1752 | 1252040.7616 | 2612015.6076 | 1252038.2955
186 | 2612559.8989 | 1252330.3984 | 2612552.8318 | 1252330.1963 | 2612544.6732 | 1252330.6602
187 | 2612577.6268 | 1252331.137 | 2612575.0758 | 1252330.8325 | 2612559.8989 | 1252330.3984
188 | 2612537.474 | 1252331.0695 | 2612544.6732 | 1252330.6602
189 | 2612577.6268 | 1252331.137 | 2612588.7279 | 1252332.4622
190 | 2612516.8111 | 1252332.3063 | 2612518.1392 | 1252332.169 | 2612537.474 | 1252331.0695
191 | 2612516.8111 | 1252332.3063 | 2612515.6137 | 1252332.4302
192 | 2612495.1319 | 1252334.5487 | 2612515.6137 | 1252332.4302
193 | 2612669.4793 | 1252339.3197 | 2612653.2205 | 1252338.1473 | 2612650.2934 | 1252337.9623
194 | 2612669.4793 | 1252339.3197 | 2612675.6031 | 1252339.7612
195 | 2612495.1319 | 1252334.5487 | 2612487.6925 | 1252335.3182 | 2612485.378 | 1252335.8277
196 | 2611952.8645 | 1252267.5278 | 2611960.7797 | 1252263.6453
197 | 2611950.3316 | 1252268.7703 | 2611952.8645 | 1252267.5278
198 | 2611946.8739 | 1252270.4663 | 2611950.3316 | 1252268.7703
199 | 2612027.2733 | 1252046.6948 | 2612047.822 | 1252061.7503
200 | 2612057.9237 | 1252069.1515 | 2612047.822 | 1252061.7503
201 | 2612071.4308 | 1252079.0478 | 2612057.9237 | 1252069.1515
202 | 2612683.3097 | 1252284.1833 | 2612660.9384 | 1252278.558 | 2612658.1782 | 1252277.9559
203 | 2612702.7957 | 1252289.083 | 2612683.3097 | 1252284.1833
204 | 2612702.7957 | 1252289.083 | 2612718.8677 | 1252293.1243 | 2612734.4615 | 1252298.3477
205 | 2612758.554 | 1252308.981 | 2612745.1917 | 1252301.942 | 2612734.4615 | 1252298.3477
206 | 2612728.0197 | 1252343.5409 | 2612675.6031 | 1252339.7612
207 | 2612728.0197 | 1252343.5409 | 2612730.9037 | 1252343.7488
208 | 2612753.2329 | 1252345.359 | 2612730.9037 | 1252343.7488
209 | 2611923.4169 | 1252420.5989 | 2611935.055 | 1252414.4035 | 2611942.8956 | 1252409.5035
210 | 2611946.7408 | 1252404.4648 | 2611943.9929 | 1252408.8177 | 2611942.8956 | 1252409.5035
211 | 2611946.7408 | 1252404.4648 | 2611936.6459 | 1252403.7744
212 | 2611946.7408 | 1252404.4648 | 2611966.3075 | 1252404.2262 | 2611971.0146 | 1252403.6077
213 | 2611924.434 | 1252402.9392 | 2611936.6459 | 1252403.7744
214 | 2611971.0146 | 1252403.6077 | 2611976.2985 | 1252402.9134
215 | 2611924.434 | 1252402.9392 | 2611916.2599 | 1252402.3802 | 2611914.9401 | 1252402.3915
216 | 2611914.9401 | 1252402.3915 | 2611907.332 | 1252402.4566
217 | 2611881.5042 | 1252402.2885 | 2611872.7749 | 1252401.9104
218 | 2611881.5042 | 1252402.2885 | 2611888.4227 | 1252402.5942
219 | 2611801.9016 | 1252410.8976 | 2611805.1557 | 1252410.0306 | 2611824.5773 | 1252406.1179
220 | 2611792.0923 | 1252413.511 | 2611801.9016 | 1252410.8976
221 | 2611898.6782 | 1252402.5307 | 2611888.8834 | 1252402.6145 | 2611888.4227 | 1252402.5942
222 | 2611924.8392 | 1252359.4742 | 2611913.2253 | 1252365.3364
223 | 2611898.6782 | 1252402.5307 | 2611899.4974 | 1252402.5237
224 | 2611899.4974 | 1252402.5237 | 2611907.332 | 1252402.4566
225 | 2612467.6758 | 1252339.7248 | 2612485.378 | 1252335.8277
226 | 2612467.6758 | 1252339.7248 | 2612458.7242 | 1252341.6954
227 | 2612442.9257 | 1252343.3243 | 2612448.5961 | 1252343.1081 | 2612457.5253 | 1252341.9594 | 2612458.7242 | 1252341.6954
228 | 2612758.554 | 1252308.981 | 2612765.2186 | 1252312.4918 | 2612784.8786 | 1252324.6511
229 | 2612790.6498 | 1252329.324 | 2612785.0983 | 1252324.7869 | 2612784.8786 | 1252324.6511
230 | 2612790.6498 | 1252329.324 | 2612786.1137 | 1252336.8303 | 2612782.7364 | 1252342.36 | 2612776.8736 | 1252345.7052
231 | 2612278.9811 | 1252316.1857 | 2612272.2332 | 1252315.3828
232 | 2612387.5909 | 1252318.6327 | 2612374.1016 | 1252318.559 | 2612363.1828 | 1252318.503 | 2612349.785 | 1252318.4126
233 | 2612757.2099 | 1252345.6457 | 2612753.2329 | 1252345.359
234 | 2612757.2099 | 1252345.6457 | 2612764.0445 | 1252346.1386
235 | 2612764.0445 | 1252346.1386 | 2612767.9453 | 1252346.4198 | 2612776.8736 | 1252345.7052 | 2612776.8736 | 1252345.7052
236 | 2612422.5349 | 1252402.3982 | 2612451.7188 | 1252401.5902
237 | 2612451.7188 | 1252401.5902 | 2612464.0815 | 1252448.4263
238 | 2612419.6397 | 1252402.4784 | 2612422.5349 | 1252402.3982
239 | 2612433.6365 | 1252467.6806 | 2612442.4 | 1252462.6957 | 2612447.3032 | 1252459.804 | 2612450.9987 | 1252457.0989 | 2612453.4028 | 1252454.9025 | 2612456.0042 | 1252452.2061 | 2612464.0815 | 1252448.4263
240 | 2612419.6397 | 1252402.4784 | 2612402.6226 | 1252402.9495
241 | 2612387.2178 | 1252441.1221 | 2612433.6365 | 1252467.6806
242 | 2612464.1354 | 1252464.509 | 2612448.5395 | 1252467.5784 | 2612433.6365 | 1252467.6806
243 | 2612464.1354 | 1252464.509 | 2612475.7969 | 1252459.2967 | 2612485.1033 | 1252454.5019 | 2612491.2989 | 1252450.6013 | 2612496.3014 | 1252447.1984 | 2612503.1618 | 1252439.3632
244 | 2612540.5472 | 1252398.8122 | 2612503.1618 | 1252439.3632
245 | 2612396.0398 | 1252403.1318 | 2612402.6226 | 1252402.9495
246 | 2612549.0034 | 1252398.5455 | 2612540.5472 | 1252398.8122
247 | 2612549.0034 | 1252398.5455 | 2612575.5489 | 1252397.7084
248 | 2612597.7185 | 1252397.0092 | 2612575.5489 | 1252397.7084
249 | 2612597.7185 | 1252397.0092 | 2612611.8905 | 1252396.5622
250 | 2612108.0078 | 1252190.0836 | 2612103.3232 | 1252193.0315 | 2612075.3051 | 1252201.6682
251 | 2612108.0078 | 1252190.0836 | 2612108.8918 | 1252189.5294 | 2612109.649 | 1252184.5388 | 2612108.1745 | 1252178.6208 | 2612097.6374 | 1252161.4104 | 2612088.9416 | 1252151.5863 | 2612086.9339 | 1252149.9119
252 | 2612108.0078 | 1252190.0836 | 2612109.8287 | 1252192.6334 | 2612123.5828 | 1252216.0544 | 2612127.1293 | 1252223.5221 | 2612129.275 | 1252229.465
253 | 2612086.9339 | 1252149.9119 | 2612085.9555 | 1252149.096
254 | 2612085.9555 | 1252149.096 | 2612083.382 | 1252146.9498 | 2612056.6208 | 1252133.7428
255 | 2612048.4381 | 1252129.7045 | 2612056.6208 | 1252133.7428
256 | 2612611.8905 | 1252396.5622 | 2612618.0992 | 1252396.3664 | 2612618.727 | 1252396.3418
257 | 2612618.727 | 1252396.3418 | 2612630.0457 | 1252395.8983
258 | 2611816.799 | 1252276.8999 | 2611793.0668 | 1252275.694
259 | 2611816.799 | 1252276.8999 | 2611816.5984 | 1252271.496 | 2611812.7011 | 1252261.9042 | 2611808.6833 | 1252253.7701
260 | 2611892.0146 | 1252262.985 | 2611877.6031 | 1252269.9052 | 2611874.8388 | 1252270.9334
261 | 2611782.4092 | 1252275.2211 | 2611787.1992 | 1252275.3959 | 2611793.0668 | 1252275.694
262 | 2611793.1964 | 1252222.416 | 2611808.6833 | 1252253.7701
263 | 2611892.0146 | 1252262.985 | 2611901.8071 | 1252258.148
264 | 2611892.0146 | 1252262.985 | 2611864.1131 | 1252207.0352
265 | 2611772.2289 | 1252274.8498 | 2611782.4092 | 1252275.2211
266 | 2611793.1964 | 1252222.416 | 2611771.6043 | 1252178.7018 | 2611767.4507 | 1252170.1829
267 | 2611901.8071 | 1252258.148 | 2611908.6281 | 1252254.7787
268 | 2611765.6042 | 1252274.6082 | 2611772.2289 | 1252274.8498
269 | 2612032.0281 | 1252121.6059 | 2612048.4381 | 1252129.7045
270 | 2612032.0281 | 1252121.6059 | 2612022.1781 | 1252116.7448
271 | 2611765.6042 | 1252274.6082 | 2611748.669 | 1252275.7503
272 | 2611765.6042 | 1252274.6082 | 2611761.8078 | 1252248.2835 | 2611762.0373 | 1252237.9443
273 | 2611762.0373 | 1252237.9443 | 2611762.1808 | 1252231.4811
274 | 2611762.1902 | 1252231.0593 | 2611762.1808 | 1252231.4811
275 | 2612352.1852 | 1252440.7504 | 2612365.4763 | 1252442.1553 | 2612376.7917 | 1252441.6176
276 | 2612387.2178 | 1252441.1221 | 2612376.7917 | 1252441.6176
277 | 2611762.1902 | 1252231.0593 | 2611762.3545 | 1252223.6573 | 2611762.4114 | 1252221.1579
278 | 2611762.4114 | 1252221.1579 | 2611763.0824 | 1252191.6747
279 | 2612009.4464 | 1252282.635 | 2612011.0449 | 1252281.7522
280 | 2612004.5554 | 1252285.3365 | 2612009.4464 | 1252282.635

## bus_geodata
| x | y | coords
0 | 2612124.0883 | 1252399.5383
1 | 2612130.6214 | 1252398.672
2 | 2612072.514 | 1252402.1058
3 | 2612042.6541 | 1252395.1741
4 | 2612153.6512 | 1252395.2598
5 | 2612030.9899 | 1252385.5776
6 | 2612162.951 | 1252393.8819
7 | 2612012.4869 | 1252396.4027
8 | 2612040.5726 | 1252374.8032
9 | 2612179.0415 | 1252390.7408
10 | 2611933.6088 | 1252321.9717
11 | 2611915.2277 | 1252318.7972
12 | 2611943.8 | 1252328.1979
13 | 2611903.6868 | 1252318.5606
14 | 2611958.1035 | 1252340.3893
15 | 2611885.3675 | 1252319.253
16 | 2611959.6344 | 1252341.6941
17 | 2611887.0026 | 1252297.7533
18 | 2611880.4361 | 1252319.9268
19 | 2611938.0249 | 1252353.3805
20 | 2611971.4241 | 1252351.4019
21 | 2611789.6078 | 1252445.2745
22 | 2611744.6395 | 1252441.8763
23 | 2611831.7057 | 1252451.9919
24 | 2611775.9178 | 1252486.7078
25 | 2611706.7561 | 1252434.3524
26 | 2611848.1261 | 1252454.2322
27 | 2611745.1364 | 1252487.9038
28 | 2611672.1775 | 1252431.8621
29 | 2611751.2865 | 1252424.3832
30 | 2611723.5371 | 1252484.0568
31 | 2611867.3986 | 1252449.002
32 | 2611617.2303 | 1252412.7296
33 | 2611774.6597 | 1252418.1555
34 | 2611882.1249 | 1252440.0146
35 | 2611825.4133 | 1252320.6954
36 | 2611834.1644 | 1252321.1917
37 | 2611819.7312 | 1252320.3731
38 | 2611840.5465 | 1252321.5537
39 | 2611813.3345 | 1252320.0103
40 | 2611846.9398 | 1252321.9163
41 | 2611806.9455 | 1252319.648
42 | 2611850.1944 | 1252321.9473
43 | 2611797.2037 | 1252319.0955
44 | 2611858.3332 | 1252276.2265
45 | 2612236.3906 | 1252446.0579
46 | 2612246.8245 | 1252446.0794
47 | 2612291.4693 | 1252426.7809
48 | 2612301.7236 | 1252430.7693
49 | 2612269.9373 | 1252411.221
50 | 2612315.6929 | 1252436.8932
51 | 2611930.0271 | 1252356.8556
52 | 2611977.0962 | 1252354.2484
53 | 2612195.7968 | 1252387.34
54 | 2612206.4988 | 1252385.1678
55 | 2612219.0186 | 1252389.9976
56 | 2612230.0989 | 1252380.3464
57 | 2612265.9289 | 1252380.6718
58 | 2612293.8708 | 1252384.1902
59 | 2611603.8619 | 1252408.4889
60 | 2611556.4735 | 1252407.9527
61 | 2611424.279 | 1252199.4725
62 | 2611383.07 | 1252187.6748
63 | 2612339.5511 | 1252370.2756
64 | 2612368.0786 | 1252350.2694
65 | 2612319.4418 | 1252379.2298
66 | 2612320.2507 | 1252354.2952
67 | 2612307.0929 | 1252384.7524
68 | 2612401.7291 | 1252330.089
69 | 2612413.2021 | 1252323.299
70 | 2612320.5859 | 1252318.6147
71 | 2612352.7832 | 1252403.7159
72 | 2612406.7123 | 1252318.4322
73 | 2612416.0049 | 1252321.7372
74 | 2612305.3047 | 1252319.3178
75 | 2612343.0872 | 1252318.3674
76 | 2612322.1307 | 1252305.3473
77 | 2612374.2494 | 1252403.7351
78 | 2612329.6996 | 1252438.3737
79 | 2611965.8336 | 1252125.4014
80 | 2611971.309 | 1252139.0765
81 | 2611959.1672 | 1252111.6379
82 | 2611977.7988 | 1252155.2849
83 | 2611952.4404 | 1252098.8097
84 | 2611986.6051 | 1252173.8551
85 | 2611930.09 | 1252098.8042
86 | 2611941.6821 | 1252071.0632
87 | 2611987.6626 | 1252176.0079
88 | 2611915.9023 | 1252098.5363
89 | 2611938.9513 | 1252060.9551
90 | 2611770.9125 | 1252316.7731
91 | 2611888.8403 | 1252110.5245
92 | 2611886.8545 | 1252099.8124
93 | 2611922.6419 | 1252116.9507
94 | 2612130.3224 | 1252325.2878
95 | 2612104.4898 | 1252335.516
96 | 2612158.789 | 1252313.8458
97 | 2612081.826 | 1252344.7204
98 | 2612179.9303 | 1252307.6851
99 | 2612062.7627 | 1252356.4445
100 | 2612074.7494 | 1252331.2024
101 | 2612196.5109 | 1252306.4639
102 | 2612047.1945 | 1252369.1161
103 | 2612074.0972 | 1252329.9566
104 | 2612202.1295 | 1252306.6667
105 | 2612102.5888 | 1252258.6501
106 | 2612095.8904 | 1252260.6656
107 | 2612113.7082 | 1252255.3045
108 | 2612075.0766 | 1252266.9282
109 | 2612045.2546 | 1252275.9013
110 | 2612059.7026 | 1252302.9576
111 | 2612039.5548 | 1252266.0056
112 | 2611999.146 | 1252363.4211
113 | 2611986.3498 | 1252358.8924
114 | 2612012.6106 | 1252358.7759
115 | 2612008.7969 | 1252397.3866
116 | 2612033.1403 | 1252343.8603
117 | 2611986.8796 | 1252401.1698
118 | 2611704.4889 | 1252281.1807
119 | 2611736.299 | 1252276.5844
120 | 2611744.2908 | 1252276.0455
121 | 2612491.6502 | 1252209.6891
122 | 2612495.4624 | 1252192.945
123 | 2612486.9051 | 1252229.7595
124 | 2612455.5093 | 1252032.4512
125 | 2612476.6139 | 1252281.9378
126 | 2612435.8726 | 1251992.9055
127 | 2612437.9767 | 1252012.1138
128 | 2612458.9691 | 1252293.5211
129 | 2612477.6733 | 1252281.3585
130 | 2612496.964 | 1252271.6841
131 | 2612236.8359 | 1252310.4483
132 | 2612250.5095 | 1252312.4505
133 | 2612257.1901 | 1252313.4288
134 | 2611988.8666 | 1252226.0867
135 | 2611977.6611 | 1252229.0754
136 | 2611995.4525 | 1252224.3301
137 | 2611964.3123 | 1252232.8008
138 | 2612012.5934 | 1252220.9995
139 | 2611951.8994 | 1252236.6987
140 | 2612021.1715 | 1252235.3188
141 | 2612038.5766 | 1252212.99
142 | 2611998.5686 | 1252196.8888
143 | 2611935.6343 | 1252241.9946
144 | 2611959.0431 | 1252254.8733
145 | 2612038.1613 | 1252263.6793
146 | 2612056.0295 | 1252207.61
147 | 2612019.6913 | 1252190.5389
148 | 2612062.8948 | 1252308.9356
149 | 2612562.888 | 1252259.7466
150 | 2612555.87 | 1252259.4463
151 | 2612594.082 | 1252263.9734
152 | 2612533.3365 | 1252261.1402
153 | 2612586.2016 | 1252236.5499
154 | 2612598.3422 | 1252264.9027
155 | 2612518.81 | 1252264.4449
156 | 2612613.8973 | 1252268.296
157 | 2612508.3456 | 1252267.4798
158 | 2612657.2938 | 1252277.763
159 | 2611947.9599 | 1252014.2168
160 | 2611968.6514 | 1252015.8372
161 | 2611931.614 | 1252019.1825
162 | 2611959.2042 | 1251729.482
163 | 2611981.0562 | 1252021.093
164 | 2611932.2057 | 1252022.5914
165 | 2611970.8032 | 1251725.8565
166 | 2611977.6285 | 1251721.936
167 | 2611978.0327 | 1251721.7084
168 | 2611995.7115 | 1252027.6128
169 | 2611935.8538 | 1252043.6095
170 | 2612015.6076 | 1252038.2955
171 | 2612559.8989 | 1252330.3984
172 | 2612544.6732 | 1252330.6602
173 | 2612577.6268 | 1252331.137
174 | 2612537.474 | 1252331.0695
175 | 2612588.7279 | 1252332.4622
176 | 2612516.8111 | 1252332.3063
177 | 2612515.6137 | 1252332.4302
178 | 2612650.2934 | 1252337.9623
179 | 2612669.4793 | 1252339.3197
180 | 2612495.1319 | 1252334.5487
181 | 2612042.2872 | 1252336.4794
182 | 2611952.8645 | 1252267.5278
183 | 2611960.7797 | 1252263.6453
184 | 2611950.3316 | 1252268.7703
185 | 2611946.8739 | 1252270.4663
186 | 2612027.2733 | 1252046.6948
187 | 2612047.822 | 1252061.7503
188 | 2612057.9237 | 1252069.1515
189 | 2612071.4308 | 1252079.0478
190 | 2612658.1782 | 1252277.9559
191 | 2612683.3097 | 1252284.1833
192 | 2612702.7957 | 1252289.083
193 | 2612734.4615 | 1252298.3477
194 | 2612675.6031 | 1252339.7612
195 | 2612728.0197 | 1252343.5409
196 | 2612730.9037 | 1252343.7488
197 | 2611923.4169 | 1252420.5989
198 | 2611942.8956 | 1252409.5035
199 | 2611946.7408 | 1252404.4648
200 | 2611936.6459 | 1252403.7744
201 | 2611971.0146 | 1252403.6077
202 | 2611924.434 | 1252402.9392
203 | 2611976.2985 | 1252402.9134
204 | 2611914.9401 | 1252402.3915
205 | 2611872.7749 | 1252401.9104
206 | 2611881.5042 | 1252402.2885
207 | 2611824.5773 | 1252406.1179
208 | 2611801.9016 | 1252410.8976
209 | 2611888.4227 | 1252402.5942
210 | 2611792.0923 | 1252413.511
211 | 2611913.2253 | 1252365.3364
212 | 2611924.8392 | 1252359.4742
213 | 2611898.6782 | 1252402.5307
214 | 2611899.4974 | 1252402.5237
215 | 2612485.378 | 1252335.8277
216 | 2612467.6758 | 1252339.7248
217 | 2612458.7242 | 1252341.6954
218 | 2612442.9257 | 1252343.3243
219 | 2612758.554 | 1252308.981
220 | 2612784.8786 | 1252324.6511
221 | 2612790.6498 | 1252329.324
222 | 2612278.9811 | 1252316.1857
223 | 2612349.785 | 1252318.4126
224 | 2612272.2332 | 1252315.3828
225 | 2612387.5909 | 1252318.6327
226 | 2612753.2329 | 1252345.359
227 | 2612757.2099 | 1252345.6457
228 | 2612764.0445 | 1252346.1386
229 | 2612451.7188 | 1252401.5902
230 | 2612422.5349 | 1252402.3982
231 | 2612464.0815 | 1252448.4263
232 | 2612419.6397 | 1252402.4784
233 | 2612433.6365 | 1252467.6806
234 | 2612464.1354 | 1252464.509
235 | 2612503.1618 | 1252439.3632
236 | 2612402.6226 | 1252402.9495
237 | 2612540.5472 | 1252398.8122
238 | 2612549.0034 | 1252398.5455
239 | 2612575.5489 | 1252397.7084
240 | 2612597.7185 | 1252397.0092
241 | 2612396.0398 | 1252403.1318
242 | 2612776.8736 | 1252345.7052
243 | 2612075.3051 | 1252201.6682
244 | 2612108.0078 | 1252190.0836
245 | 2612086.9339 | 1252149.9119
246 | 2612129.275 | 1252229.465
247 | 2612085.9555 | 1252149.096
248 | 2612056.6208 | 1252133.7428
249 | 2611907.332 | 1252402.4566
250 | 2612611.8905 | 1252396.5622
251 | 2612618.727 | 1252396.3418
252 | 2612630.0457 | 1252395.8983
253 | 2612052.0641 | 1252180.807
254 | 2611816.799 | 1252276.8999
255 | 2611874.8388 | 1252270.9334
256 | 2611793.0668 | 1252275.694
257 | 2611808.6833 | 1252253.7701
258 | 2611892.0146 | 1252262.985
259 | 2611782.4092 | 1252275.2211
260 | 2611793.1964 | 1252222.416
261 | 2611901.8071 | 1252258.148
262 | 2611864.1131 | 1252207.0352
263 | 2611908.6281 | 1252254.7787
264 | 2611767.4507 | 1252170.1829
265 | 2611772.2289 | 1252274.8498
266 | 2612048.4381 | 1252129.7045
267 | 2612032.0281 | 1252121.6059
268 | 2612022.1781 | 1252116.7448
269 | 2611748.669 | 1252275.7503
270 | 2611765.6042 | 1252274.6082
271 | 2611762.0373 | 1252237.9443
272 | 2611762.1808 | 1252231.4811
273 | 2612352.1852 | 1252440.7504
274 | 2612376.7916 | 1252441.6176
275 | 2611762.1902 | 1252231.0593
276 | 2611762.4114 | 1252221.1579
277 | 2611763.0824 | 1252191.6747
278 | 2612387.2178 | 1252441.1221
279 | 2612011.0449 | 1252281.7522
280 | 2612009.4464 | 1252282.635
281 | 2612004.5554 | 1252285.3365
282 | 2612104.4898 | 1252335.516

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9801 | -0.38181 | 0.0030179 | 0.00075636
1 | 0.98012 | -0.38145 | 0.0044412 | 0.0011131
2 | 0.9881 | -0.22672 | 0.0061312 | 0.0015366
3 | 0.98827 | -0.22335 | 0.0039908 | 0.0010002
4 | 0.98028 | -0.3783 | 0.0042626 | 0.0010683
5 | 0.98841 | -0.22057 | 0 | 0
6 | 0.98038 | -0.3763 | 0.0046044 | 0.001154
7 | 0.98686 | -0.25062 | 0.005922 | 0.0014842
8 | 0.98957 | -0.19833 | 0.0020457 | 0.00051271
9 | 0.98063 | -0.37144 | 0.0013952 | 0.00034966
10 | 0.9719 | -0.54113 | 0.0023634 | 0.00059233
11 | 0.97227 | -0.53373 | 0.006612 | 0.0016571
12 | 0.97167 | -0.54567 | 0.0016425 | 0.00041164
13 | 0.97252 | -0.52872 | 0.0026202 | 0.00065667
14 | 0.97131 | -0.55262 | 0.0080142 | 0.0020085
15 | 0.97294 | -0.52046 | 0 | 0
16 | 0.97128 | -0.55326 | 0 | 0
17 | 0.97358 | -0.50782 | 0.0015868 | 0.00039768
18 | 0.97286 | -0.52213 | 0.003428 | 0.00085915
19 | 0.97083 | -0.56221 | 0.0064371 | 0.0016133
20 | 0.97113 | -0.55631 | 0.011497 | 0.0028813
21 | 0.97813 | -0.42078 | 0.0022238 | 0.00055733
22 | 0.97736 | -0.43593 | 0.0013549 | 0.00033956
23 | 0.97919 | -0.39991 | 0.0025889 | 0.00064883
24 | 0.97788 | -0.42578 | 0.001909 | 0.00047844
25 | 0.97673 | -0.44836 | 0 | 0
26 | 0.97965 | -0.39095 | 0.0021132 | 0.00052962
27 | 0.97775 | -0.42826 | 0.0016881 | 0.00042307
28 | 0.97647 | -0.45341 | 0.0029547 | 0.00074051
29 | 0.97634 | -0.45591 | 0.0013344 | 0.00033442
30 | 0.97769 | -0.42934 | 0.0026973 | 0.000676
31 | 0.98024 | -0.37935 | 0 | 0
32 | 0.9762 | -0.45873 | 0 | 0
33 | 0.97617 | -0.45932 | 0.0013153 | 0.00032965
34 | 0.98075 | -0.36947 | 0.0015098 | 0.00037839
35 | 0.97219 | -0.53534 | 0.0013302 | 0.00033338
36 | 0.97226 | -0.53386 | 0.0014451 | 0.00036217
37 | 0.97215 | -0.53616 | 0.0014467 | 0.00036259
38 | 0.97233 | -0.53261 | 0.0014149 | 0.0003546
39 | 0.97211 | -0.53691 | 0.0014197 | 0.0003558
40 | 0.9724 | -0.53119 | 0.0014501 | 0.00036343
41 | 0.97208 | -0.5375 | 0.0014434 | 0.00036174
42 | 0.97244 | -0.53038 | 0.0012913 | 0.00032364
43 | 0.97205 | -0.53813 | 0.0017675 | 0.00044297
44 | 0.9747 | -0.48585 | 0 | 0
45 | 0.97241 | -0.53243 | 0.00092704 | 0.00023234
46 | 0.97242 | -0.53225 | 0.00081123 | 0.00020331
47 | 0.97251 | -0.53041 | 0 | 0
48 | 0.97254 | -0.52981 | 0.0024994 | 0.0006264
49 | 0.97248 | -0.531 | 0.0011966 | 0.0002999
50 | 0.97262 | -0.52829 | 0 | 0
51 | 0.97072 | -0.56434 | 0.0084457 | 0.0021167
52 | 0.97107 | -0.55754 | 0.0019185 | 0.00048082
53 | 0.98091 | -0.36595 | 0.002631 | 0.0006594
54 | 0.98112 | -0.36193 | 0 | 0
55 | 0.98111 | -0.36203 | 0.00042096 | 0.0001055
56 | 0.98158 | -0.35287 | 0.0026489 | 0.00066387
57 | 0.98236 | -0.3376 | 0.0016699 | 0.00041853
58 | 0.98301 | -0.32484 | 0.0011172 | 0.00028001
59 | 0.97614 | -0.46001 | 0.0026219 | 0.00065711
60 | 0.97603 | -0.46212 | 0 | 0
61 | 0.97549 | -0.47279 | 0 | 0
62 | 0.97539 | -0.47468 | 0.0023555 | 0.00059035
63 | 0.98426 | -0.30068 | 0.0014512 | 0.00036369
64 | 0.98421 | -0.30153 | 0.0013544 | 0.00033944
65 | 0.98431 | -0.29956 | 0 | 0
66 | 0.98622 | -0.26271 | 0.00049916 | 0.0001251
67 | 0.98333 | -0.31858 | 0 | 0
68 | 0.98613 | -0.26462 | 0.0023298 | 0.0005839
69 | 0.98616 | -0.26406 | 0 | 0
70 | 0.98885 | -0.21201 | 0 | 0
71 | 0.98097 | -0.36448 | 0.0019075 | 0.00047806
72 | 0.98648 | -0.25774 | 0.0020643 | 0.00051735
73 | 0.98591 | -0.26879 | 0 | 0
74 | 0.98967 | -0.19631 | 0.00088805 | 0.00022257
75 | 0.98822 | -0.22425 | 0.00067953 | 0.00017031
76 | 0.98883 | -0.21241 | 0.001648 | 0.00041302
77 | 0.98001 | -0.3832 | 0.001123 | 0.00028146
78 | 0.97269 | -0.52688 | 0.0036025 | 0.00090287
79 | 0.97733 | -0.43445 | 0.001107 | 0.00027745
80 | 0.97796 | -0.42213 | 0.0015847 | 0.00039716
81 | 0.97669 | -0.44696 | 0.0018587 | 0.00046582
82 | 0.97873 | -0.40704 | 0.001286 | 0.0003223
83 | 0.97611 | -0.45833 | 0 | 0
84 | 0.97966 | -0.38882 | 0.0017616 | 0.0004415
85 | 0.97602 | -0.46012 | 0.0013741 | 0.00034439
86 | 0.97504 | -0.47941 | 0.0027721 | 0.00069476
87 | 0.97978 | -0.38662 | 0.0022186 | 0.00055604
88 | 0.97598 | -0.46091 | 0 | 0
89 | 0.97469 | -0.48627 | 0.001763 | 0.00044185
90 | 0.97201 | -0.53898 | 0.001743 | 0.00043683
91 | 0.97592 | -0.46209 | 0.0016217 | 0.00040643
92 | 0.97594 | -0.46177 | 0 | 0
93 | 0.97595 | -0.46141 | 0.0013958 | 0.00034982
94 | 1 | 0 | -0.58695 | -0.1511
95 | 0.99676 | -0.061037 | 0 | 0
96 | 0.99813 | -0.035193 | 0 | 0
97 | 0.99391 | -0.11497 | 0 | 0
98 | 0.99679 | -0.060556 | 0.0035148 | 0.00088089
99 | 0.99198 | -0.1519 | 0.0011313 | 0.00028354
100 | 0.99257 | -0.14047 | 0.005364 | 0.0013444
101 | 0.9958 | -0.079444 | 0.0014738 | 0.00036937
102 | 0.99028 | -0.18467 | 0.0040187 | 0.0010072
103 | 0.99244 | -0.14278 | 0.0042695 | 0.00107
104 | 0.99546 | -0.085773 | 0.0058034 | 0.0014545
105 | 0.987 | -0.24703 | 0.0016005 | 0.00040112
106 | 0.98702 | -0.24661 | 0.0017413 | 0.00043641
107 | 0.98698 | -0.24738 | 0.0017233 | 0.00043191
108 | 0.98712 | -0.24464 | 0.0028914 | 0.00072464
109 | 0.98735 | -0.24021 | 0 | 0
110 | 0.98985 | -0.19216 | 0.0050236 | 0.001259
111 | 0.98644 | -0.2576 | 0 | 0
112 | 0.97072 | -0.5644 | 0 | 0
113 | 0.97088 | -0.56117 | 0.006154 | 0.0015424
114 | 0.97055 | -0.56779 | 0.0066451 | 0.0016654
115 | 0.98661 | -0.25541 | 0.0045151 | 0.0011316
116 | 0.9704 | -0.57072 | 0.0026494 | 0.000664
117 | 0.98527 | -0.28147 | 0.0027064 | 0.00067829
118 | 0.97161 | -0.5469 | 0.0029185 | 0.00073144
119 | 0.97169 | -0.54517 | 0.0018721 | 0.00046919
120 | 0.97173 | -0.54446 | 0.0018648 | 0.00046737
121 | 0.98158 | -0.35288 | 0.0012539 | 0.00031426
122 | 0.98147 | -0.35489 | 0.0012514 | 0.00031362
123 | 0.98172 | -0.35 | 0.00094829 | 0.00023766
124 | 0.98068 | -0.37052 | 0.0039215 | 0.00098283
125 | 0.98215 | -0.34164 | 0 | 0
126 | 0.98061 | -0.3718 | 0.0012899 | 0.00032328
127 | 0.98064 | -0.37118 | 0 | 0
128 | 0.98322 | -0.32079 | 0.001554 | 0.00038946
129 | 0.9821 | -0.34264 | 0.0013393 | 0.00033565
130 | 0.9812 | -0.36012 | 0.001041 | 0.00026089
131 | 0.99345 | -0.124 | 0.0035728 | 0.00089542
132 | 0.99267 | -0.13887 | 0.002275 | 0.00057017
133 | 0.9923 | -0.14606 | 0.0023382 | 0.000586
134 | 0.98116 | -0.35966 | 0.0017368 | 0.00043529
135 | 0.98056 | -0.37121 | 0.0022075 | 0.00055324
136 | 0.98151 | -0.35282 | 0.00090453 | 0.0002267
137 | 0.97986 | -0.38484 | 0.0027987 | 0.00070142
138 | 0.98243 | -0.33504 | 0 | 0
139 | 0.97922 | -0.39743 | 0 | 0
140 | 0.9837 | -0.31041 | 0.00089357 | 0.00022395
141 | 0.98192 | -0.34503 | 0.0018512 | 0.00046395
142 | 0.98093 | -0.3641 | 0 | 0
143 | 0.97843 | -0.41285 | 0.0022158 | 0.00055534
144 | 0.97901 | -0.4015 | 0.0016859 | 0.00042252
145 | 0.98623 | -0.26164 | 0.0029943 | 0.00075044
146 | 0.98161 | -0.35113 | 0.0011321 | 0.00028374
147 | 0.98083 | -0.36606 | 0.0024793 | 0.00062138
148 | 0.99042 | -0.18138 | 0.0056166 | 0.0014076
149 | 0.97864 | -0.40993 | 0.001226 | 0.00030727
150 | 0.97889 | -0.40512 | 0.0019283 | 0.00048328
151 | 0.97758 | -0.43079 | 0 | 0
152 | 0.97972 | -0.38886 | 0.00096758 | 0.0002425
153 | 0.97752 | -0.43199 | 0.0019032 | 0.00047698
154 | 0.97744 | -0.43353 | 0.0011405 | 0.00028585
155 | 0.98028 | -0.37791 | 0.00099327 | 0.00024894
156 | 0.97694 | -0.44321 | 0.0011937 | 0.00029917
157 | 0.98071 | -0.36971 | 0.0021897 | 0.00054879
158 | 0.97561 | -0.46929 | 0.0016151 | 0.00040479
159 | 0.9729 | -0.52145 | 0.0019992 | 0.00050105
160 | 0.97247 | -0.53003 | 0.00084141 | 0.00021088
161 | 0.97339 | -0.51184 | 0 | 0
162 | 0.97111 | -0.5568 | 0 | 0
163 | 0.9722 | -0.53523 | 0.0016894 | 0.00042341
164 | 0.97349 | -0.5099 | 0.0017324 | 0.00043417
165 | 0.97104 | -0.55834 | 0.0021775 | 0.00054574
166 | 0.971 | -0.559 | 0.0016437 | 0.00041196
167 | 0.971 | -0.55902 | 0.002899 | 0.00072657
168 | 0.97192 | -0.54092 | 0.002154 | 0.00053985
169 | 0.97413 | -0.49726 | 0.001739 | 0.00043583
170 | 0.97155 | -0.54807 | 0.0049277 | 0.001235
171 | 0.98346 | -0.31667 | 0.0026312 | 0.00065944
172 | 0.98354 | -0.31501 | 0.0018571 | 0.00046543
173 | 0.9834 | -0.31777 | 0.0017093 | 0.0004284
174 | 0.98359 | -0.31398 | 0.0012624 | 0.0003164
175 | 0.98338 | -0.31811 | 0.001713 | 0.00042932
176 | 0.98377 | -0.31056 | 0.002423 | 0.00060726
177 | 0.98378 | -0.31031 | 0.0032215 | 0.00080738
178 | 0.97101 | -0.56002 | 0.0018822 | 0.00047173
179 | 0.97105 | -0.55935 | 0.0024377 | 0.00061094
180 | 0.98406 | -0.30482 | 0.0017497 | 0.00043852
181 | 0.97036 | -0.57149 | 0.0035532 | 0.00089051
182 | 0.97887 | -0.40426 | 0.003786 | 0.00094886
183 | 0.97893 | -0.40314 | 0.0027789 | 0.00069647
184 | 0.97886 | -0.40442 | 0.001606 | 0.00040249
185 | 0.97886 | -0.40453 | 0.0015941 | 0.00039952
186 | 0.97139 | -0.5513 | 0.0016432 | 0.00041183
187 | 0.97114 | -0.55625 | 0.0030109 | 0.00075461
188 | 0.97105 | -0.55799 | 0.0034108 | 0.00085482
189 | 0.97099 | -0.55925 | 0.0040909 | 0.0010253
190 | 0.97559 | -0.46979 | 0.0015854 | 0.00039733
191 | 0.97489 | -0.48351 | 0.0027101 | 0.00067921
192 | 0.9744 | -0.49317 | 0.0017365 | 0.00043522
193 | 0.97365 | -0.508 | 0.0019215 | 0.00048158
194 | 0.97107 | -0.55886 | 0.0022063 | 0.00055295
195 | 0.97139 | -0.55252 | 0.0035154 | 0.00088104
196 | 0.97142 | -0.55199 | 0.0015114 | 0.0003788
197 | 0.98215 | -0.34213 | 0.0018417 | 0.00046158
198 | 0.98288 | -0.32798 | 0.0014971 | 0.00037521
199 | 0.98309 | -0.32375 | 0 | 0
200 | 0.98291 | -0.32738 | 0.0063007 | 0.0015791
201 | 0.98436 | -0.29908 | 0.0014133 | 0.00035422
202 | 0.98275 | -0.33038 | 0.001766 | 0.00044259
203 | 0.98465 | -0.29354 | 0.0048989 | 0.0012278
204 | 0.98265 | -0.33242 | 0.0012369 | 0.00031
205 | 0.98242 | -0.33688 | 0.0026504 | 0.00066425
206 | 0.98244 | -0.33646 | 0 | 0
207 | 0.97594 | -0.46383 | 0.0035676 | 0.00089414
208 | 0.97602 | -0.46231 | 0.0011696 | 0.00029313
209 | 0.98246 | -0.33613 | 0.0019683 | 0.0004933
210 | 0.97606 | -0.46143 | 0.0016542 | 0.00041459
211 | 0.97067 | -0.56537 | 0.0021695 | 0.00054372
212 | 0.9707 | -0.56485 | 0.002562 | 0.00064209
213 | 0.9825 | -0.33527 | 0.0013125 | 0.00032894
214 | 0.98251 | -0.33519 | 0.0033523 | 0.00084016
215 | 0.98421 | -0.30188 | 0.0019525 | 0.00048934
216 | 0.98452 | -0.29584 | 0.0024057 | 0.00060292
217 | 0.9847 | -0.29239 | 0.0026324 | 0.00065974
218 | 0.98505 | -0.28566 | 0.0026177 | 0.00065605
219 | 0.97309 | -0.51895 | 0.0020489 | 0.00051349
220 | 0.9725 | -0.53052 | 0.0021185 | 0.00053094
221 | 0.97238 | -0.53303 | 0 | 0
222 | 0.99109 | -0.16907 | 0.0022851 | 0.00057269
223 | 0.98803 | -0.22786 | 0.0023215 | 0.00058182
224 | 0.99146 | -0.16201 | 0.0023458 | 0.00058791
225 | 0.987 | -0.24778 | 0.0015768 | 0.00039518
226 | 0.97166 | -0.54721 | 0.0023796 | 0.00059639
227 | 0.97171 | -0.54619 | 0.0010563 | 0.00026473
228 | 0.97181 | -0.54429 | 0.0010486 | 0.00026279
229 | 0.97698 | -0.44238 | 0.0029229 | 0.00073254
230 | 0.97803 | -0.42194 | 0.0015093 | 0.00037827
231 | 0.97538 | -0.47379 | 0.002549 | 0.00063883
232 | 0.97813 | -0.41984 | 0.0014187 | 0.00035555
233 | 0.97427 | -0.49567 | 0 | 0
234 | 0.9739 | -0.50303 | 0 | 0
235 | 0.97333 | -0.51427 | 0.0022846 | 0.00057258
236 | 0.97879 | -0.40704 | 0.0026323 | 0.00065971
237 | 0.97278 | -0.52518 | 0.0015245 | 0.00038206
238 | 0.9727 | -0.52662 | 0.0014513 | 0.00036372
239 | 0.97251 | -0.53042 | 0.0027198 | 0.00068165
240 | 0.97241 | -0.53248 | 0.0018647 | 0.00046733
241 | 0.97906 | -0.40178 | 0.0029892 | 0.00074917
242 | 0.972 | -0.54048 | 0.0023229 | 0.00058217
243 | 0.98128 | -0.35746 | 0.0017342 | 0.00043463
244 | 0.98078 | -0.36732 | 0 | 0
245 | 0.98015 | -0.37972 | 0.0025009 | 0.00062679
246 | 0.98072 | -0.36844 | 0.0013837 | 0.00034678
247 | 0.98013 | -0.37999 | 0.0021729 | 0.00054459
248 | 0.97984 | -0.38575 | 0.003667 | 0.00091905
249 | 0.98258 | -0.33387 | 0.0013151 | 0.00032959
250 | 0.97236 | -0.53331 | 0.0010468 | 0.00026236
251 | 0.97235 | -0.53358 | 0.0010754 | 0.00026953
252 | 0.97234 | -0.5338 | 0.0010586 | 0.00026532
253 | 0.98076 | -0.36754 | 0.0024256 | 0.00060792
254 | 0.97305 | -0.51839 | 0 | 0
255 | 0.97543 | -0.47145 | 0.00143 | 0.0003584
256 | 0.97244 | -0.53037 | 0.0019489 | 0.00048843
257 | 0.97269 | -0.52538 | 0.01185 | 0.0029699
258 | 0.97624 | -0.4556 | 0 | 0
259 | 0.97219 | -0.53537 | 0.0068789 | 0.001724
260 | 0.97258 | -0.5276 | 0.0014439 | 0.00036188
261 | 0.97673 | -0.44609 | 0.0016072 | 0.00040281
262 | 0.9759 | -0.46222 | 0.005788 | 0.0014506
263 | 0.97707 | -0.43939 | 0.0016043 | 0.00040207
264 | 0.97248 | -0.52973 | 0.0019871 | 0.00049803
265 | 0.97201 | -0.53885 | 0.0016675 | 0.00041792
266 | 0.97979 | -0.38672 | 0.0017934 | 0.00044948
267 | 0.97972 | -0.38808 | 0.0019614 | 0.00049158
268 | 0.9797 | -0.3885 | 0.0021247 | 0.0005325
269 | 0.97176 | -0.54392 | 0.002954 | 0.00074035
270 | 0.97191 | -0.54091 | 0 | 0
271 | 0.97166 | -0.54586 | 0.0014287 | 0.00035807
272 | 0.97162 | -0.54655 | 0.0014295 | 0.00035827
273 | 0.97288 | -0.52311 | 0.0024536 | 0.00061493
274 | 0.97315 | -0.51788 | 0.0024795 | 0.00062143
275 | 0.97162 | -0.54659 | 0.0014217 | 0.00035631
276 | 0.97159 | -0.54713 | 0.0014506 | 0.00036356
277 | 0.97155 | -0.54796 | 0.0015189 | 0.00038067
278 | 0.97328 | -0.5152 | 0.0058868 | 0.0014754
279 | 0.98625 | -0.26122 | 0.0010742 | 0.00026922
280 | 0.98625 | -0.26139 | 0.0014653 | 0.00036723
281 | 0.98623 | -0.26176 | 0.0036639 | 0.00091827
282 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0030179 | -0.00075636 | 0.003018 | 0.00075631 | 5.1906e-08 | -4.9873e-08 | 0.0045819 | 0.0045818 | 0.0045819 | 0.9801 | -0.38181 | 0.98012 | -0.38145 | 1.2588
1 | -0.0074591 | -0.0018694 | 0.0074602 | 0.0018698 | 1.1196e-06 | 4.2309e-07 | 0.011324 | 0.011324 | 0.011324 | 0.98012 | -0.38145 | 0.98028 | -0.3783 | 3.1111
2 | -0.0061312 | -0.0015366 | 0.0061322 | 0.0015369 | 9.8585e-07 | 2.3589e-07 | 0.0092333 | 0.0092332 | 0.0092333 | 0.9881 | -0.22672 | 0.98827 | -0.22335 | 2.5366
3 | -0.010123 | -0.0025371 | 0.010124 | 0.0025377 | 1.3388e-06 | 6.599e-07 | 0.015242 | 0.015242 | 0.015242 | 0.98827 | -0.22335 | 0.98841 | -0.22057 | 4.1874
4 | -0.011723 | -0.0029381 | 0.011724 | 0.0029387 | 1.1164e-06 | 5.9593e-07 | 0.017795 | 0.017795 | 0.017795 | 0.98028 | -0.3783 | 0.98038 | -0.3763 | 4.8887
5 | 0.076272 | 0.019303 | -0.076162 | -0.019233 | 0.00010986 | 7.0025e-05 | 0.11489 | 0.11489 | 0.11489 | 0.98841 | -0.22057 | 0.98686 | -0.25062 | 31.5635
6 | -0.086396 | -0.021841 | 0.086488 | 0.0219 | 9.2267e-05 | 5.8864e-05 | 0.13013 | 0.13013 | 0.13013 | 0.98841 | -0.22057 | 0.98957 | -0.19833 | 35.7508
7 | -0.016328 | -0.0040927 | 0.016332 | 0.0040949 | 3.7767e-06 | 2.2103e-06 | 0.024783 | 0.024783 | 0.024783 | 0.98038 | -0.3763 | 0.98063 | -0.37144 | 6.8086
8 | 0.07024 | 0.017749 | -0.070224 | -0.017739 | 1.6113e-05 | 1.0263e-05 | 0.10596 | 0.10596 | 0.10596 | 0.98686 | -0.25062 | 0.98661 | -0.25541 | 29.1104
9 | -0.088534 | -0.022413 | 0.088592 | 0.02245 | 5.8084e-05 | 3.7062e-05 | 0.13321 | 0.13321 | 0.13321 | 0.98957 | -0.19833 | 0.99028 | -0.18467 | 36.5959
10 | -0.017727 | -0.0044445 | 0.017732 | 0.0044473 | 4.6394e-06 | 2.7535e-06 | 0.0269 | 0.0269 | 0.0269 | 0.98063 | -0.37144 | 0.98091 | -0.36595 | 7.3902
11 | -0.06411 | -0.016087 | 0.064133 | 0.016101 | 2.2629e-05 | 1.3784e-05 | 0.098163 | 0.098162 | 0.098163 | 0.9719 | -0.54113 | 0.97227 | -0.53373 | 8.9892
12 | 0.061747 | 0.015495 | -0.061733 | -0.015487 | 1.3351e-05 | 8.1005e-06 | 0.094544 | 0.094544 | 0.094544 | 0.9719 | -0.54113 | 0.97167 | -0.54567 | 8.6579
13 | -0.070745 | -0.017758 | 0.070762 | 0.017768 | 1.6935e-05 | 1.0408e-05 | 0.10828 | 0.10828 | 0.10828 | 0.97227 | -0.53373 | 0.97252 | -0.52872 | 9.9159
14 | 0.060091 | 0.015075 | -0.060071 | -0.015063 | 1.9897e-05 | 1.2036e-05 | 0.092029 | 0.092029 | 0.092029 | 0.97167 | -0.54567 | 0.97131 | -0.55262 | 8.4276
15 | -0.073382 | -0.018425 | 0.073411 | 0.018443 | 2.8895e-05 | 1.781e-05 | 0.11229 | 0.11229 | 0.11229 | 0.97252 | -0.52872 | 0.97294 | -0.52046 | 10.283
16 | 0.052057 | 0.013054 | -0.052055 | -0.013053 | 1.5992e-06 | 9.488e-07 | 0.079752 | 0.079752 | 0.079752 | 0.97131 | -0.55262 | 0.97128 | -0.55326 | 7.3033
17 | -0.091601 | -0.023004 | 0.091657 | 0.023039 | 5.5295e-05 | 3.4549e-05 | 0.14011 | 0.14011 | 0.14011 | 0.97294 | -0.52046 | 0.97358 | -0.50782 | 12.8307
18 | 0.018191 | 0.0045617 | -0.018189 | -0.0045609 | 1.4447e-06 | 8.6279e-07 | 0.027822 | 0.027822 | 0.027822 | 0.97294 | -0.52046 | 0.97286 | -0.52213 | 7.6433
19 | 0.019624 | 0.0049215 | -0.019616 | -0.0049164 | 8.3698e-06 | 5.0512e-06 | 0.030066 | 0.030066 | 0.030066 | 0.97128 | -0.55326 | 0.97083 | -0.56221 | 8.2598
20 | 0.032431 | 0.0081319 | -0.032426 | -0.0081294 | 4.7129e-06 | 2.4493e-06 | 0.049686 | 0.049686 | 0.049686 | 0.97128 | -0.55326 | 0.97113 | -0.55631 | 4.55
21 | -0.093243 | -0.023437 | 0.093341 | 0.023498 | 9.7915e-05 | 6.1226e-05 | 0.14254 | 0.14254 | 0.14254 | 0.97358 | -0.50782 | 0.9747 | -0.48585 | 13.0528
22 | 0.014761 | 0.0037017 | -0.014755 | -0.0036984 | 5.8044e-06 | 3.338e-06 | 0.022578 | 0.022578 | 0.022578 | 0.97286 | -0.52213 | 0.97244 | -0.53038 | 6.2029
23 | 0.013179 | 0.0033031 | -0.013177 | -0.0033024 | 1.3357e-06 | 7.469e-07 | 0.020199 | 0.020199 | 0.020199 | 0.97083 | -0.56221 | 0.97072 | -0.56434 | 5.5493
24 | 0.02093 | 0.0052481 | -0.020929 | -0.0052475 | 1.2239e-06 | 6.2625e-07 | 0.032071 | 0.032071 | 0.032071 | 0.97113 | -0.55631 | 0.97107 | -0.55754 | 4.4053
25 | 0.018362 | 0.0046071 | -0.018349 | -0.0045992 | 1.3255e-05 | 7.915e-06 | 0.027936 | 0.027936 | 0.027936 | 0.97813 | -0.42078 | 0.97736 | -0.43593 | 7.6748
26 | -0.026882 | -0.0067421 | 0.026909 | 0.0067587 | 2.6765e-05 | 1.6594e-05 | 0.040898 | 0.040897 | 0.040898 | 0.97813 | -0.42078 | 0.97919 | -0.39991 | 11.2356
27 | 0.0062965 | 0.0015777 | -0.006295 | -0.0015773 | 1.5014e-06 | 4.1332e-07 | 0.0095786 | 0.0095788 | 0.0095788 | 0.97813 | -0.42078 | 0.97788 | -0.42578 | 2.6315
28 | 0.016994 | 0.0042596 | -0.016984 | -0.0042537 | 1.0059e-05 | 5.936e-06 | 0.025873 | 0.025874 | 0.025874 | 0.97736 | -0.43593 | 0.97673 | -0.44836 | 7.1081
29 | -0.029498 | -0.0074075 | 0.029511 | 0.0074154 | 1.2612e-05 | 7.861e-06 | 0.044831 | 0.044831 | 0.044831 | 0.97919 | -0.39991 | 0.97965 | -0.39095 | 12.3163
30 | 0.004386 | 0.0010988 | -0.0043855 | -0.0010989 | 5.1745e-07 | -5.7419e-08 | 0.0066739 | 0.0066741 | 0.0066741 | 0.97788 | -0.42578 | 0.97775 | -0.42826 | 1.8335
31 | 0.0079372 | 0.0019857 | -0.0079353 | -0.0019849 | 1.9085e-06 | 7.8584e-07 | 0.012091 | 0.012091 | 0.012091 | 0.97673 | -0.44836 | 0.97647 | -0.45341 | 3.3217
32 | 0.0090467 | 0.002268 | -0.0090435 | -0.0022665 | 3.2559e-06 | 1.512e-06 | 0.013783 | 0.013783 | 0.013783 | 0.97673 | -0.44836 | 0.97634 | -0.45591 | 3.7865
33 | -0.031624 | -0.007945 | 0.031641 | 0.007956 | 1.7528e-05 | 1.0963e-05 | 0.048041 | 0.048041 | 0.048041 | 0.97965 | -0.39095 | 0.98024 | -0.37935 | 13.1981
34 | 0.0026974 | 0.00067581 | -0.0026973 | -0.000676 | 1.3879e-07 | -1.8662e-07 | 0.004105 | 0.0041051 | 0.0041051 | 0.97775 | -0.42826 | 0.97769 | -0.42934 | 1.1278
35 | 0.0049806 | 0.0012444 | -0.0049794 | -0.0012443 | 1.258e-06 | 7.6607e-08 | 0.0075885 | 0.0075887 | 0.0075887 | 0.97647 | -0.45341 | 0.9762 | -0.45873 | 2.0848
36 | 0.0077091 | 0.0019321 | -0.0077079 | -0.0019316 | 1.2522e-06 | 4.9894e-07 | 0.011749 | 0.011749 | 0.011749 | 0.97634 | -0.45591 | 0.97617 | -0.45932 | 3.2278
37 | -0.031641 | -0.007956 | 0.031656 | 0.0079653 | 1.4931e-05 | 9.3385e-06 | 0.048041 | 0.048041 | 0.048041 | 0.98024 | -0.37935 | 0.98075 | -0.36947 | 13.1981
38 | 0.0049794 | 0.0012443 | -0.0049791 | -0.0012443 | 3.0288e-07 | 1.8512e-08 | 0.0075887 | 0.0075888 | 0.0075888 | 0.9762 | -0.45873 | 0.97614 | -0.46001 | 2.0848
39 | 0.0063926 | 0.0016019 | -0.0063919 | -0.0016017 | 6.4238e-07 | 1.8561e-07 | 0.0097443 | 0.0097444 | 0.0097444 | 0.97617 | -0.45932 | 0.97606 | -0.46143 | 2.677
40 | -0.033166 | -0.0083437 | 0.033209 | 0.0083709 | 4.3393e-05 | 2.7194e-05 | 0.050332 | 0.050331 | 0.050332 | 0.98075 | -0.36947 | 0.98215 | -0.34213 | 13.8274
41 | -0.0091513 | -0.0022932 | 0.0091519 | 0.0022935 | 6.4485e-07 | 3.0401e-07 | 0.014007 | 0.014007 | 0.014007 | 0.97219 | -0.53534 | 0.97226 | -0.53386 | 3.848
42 | 0.0078211 | 0.0019598 | -0.0078208 | -0.0019597 | 3.0582e-07 | 1.2516e-07 | 0.011971 | 0.011971 | 0.011971 | 0.97219 | -0.53534 | 0.97215 | -0.53616 | 3.2886
43 | -0.010597 | -0.0026556 | 0.010598 | 0.002656 | 6.3052e-07 | 3.2425e-07 | 0.016218 | 0.016218 | 0.016218 | 0.97226 | -0.53386 | 0.97233 | -0.53261 | 4.4555
44 | 0.006374 | 0.0015971 | -0.0063738 | -0.001597 | 2.2869e-07 | 6.6927e-08 | 0.0097562 | 0.0097562 | 0.0097562 | 0.97215 | -0.53616 | 0.97211 | -0.53691 | 2.6803
45 | -0.012012 | -0.0030106 | 0.012013 | 0.003011 | 8.1152e-07 | 4.3994e-07 | 0.018383 | 0.018383 | 0.018383 | 0.97233 | -0.53261 | 0.9724 | -0.53119 | 5.0504
46 | 0.0049541 | 0.0012412 | -0.004954 | -0.0012412 | 1.38e-07 | 8.983e-09 | 0.0075832 | 0.0075832 | 0.0075832 | 0.97211 | -0.53691 | 0.97208 | -0.5375 | 2.0833
47 | -0.013463 | -0.0033744 | 0.013464 | 0.0033747 | 5.1837e-07 | 2.9136e-07 | 0.020602 | 0.020602 | 0.020602 | 0.9724 | -0.53119 | 0.97244 | -0.53038 | 5.66
48 | 0.0035106 | 0.00087947 | -0.0035105 | -0.00087952 | 1.0567e-07 | -5.3333e-08 | 0.0053738 | 0.0053738 | 0.0053738 | 0.97208 | -0.5375 | 0.97205 | -0.53813 | 1.4763
49 | 0.0017431 | 0.00043655 | -0.001743 | -0.00043683 | 7.047e-08 | -2.8208e-07 | 0.0026682 | 0.0026683 | 0.0026683 | 0.97205 | -0.53813 | 0.97201 | -0.53898 | 0.73305
50 | 0.042738 | 0.010747 | -0.042671 | -0.010705 | 6.6312e-05 | 4.1923e-05 | 0.065258 | 0.065258 | 0.065258 | 0.9747 | -0.48585 | 0.97305 | -0.51839 | 17.928
51 | -0.13608 | -0.034244 | 0.13617 | 0.034304 | 9.3755e-05 | 5.9353e-05 | 0.20779 | 0.20779 | 0.20779 | 0.9747 | -0.48585 | 0.97543 | -0.47145 | 19.0287
52 | -0.00092704 | -0.00023234 | 0.00092705 | 0.00023221 | 7.8738e-09 | -1.244e-07 | 0.0014186 | 0.0014185 | 0.0014186 | 0.97241 | -0.53243 | 0.97242 | -0.53225 | 0.38972
53 | -0.0017383 | -0.00043553 | 0.0017384 | 0.00043491 | 1.5199e-07 | -6.1352e-07 | 0.0026599 | 0.0026597 | 0.0026599 | 0.97242 | -0.53225 | 0.97251 | -0.53041 | 0.73074
54 | -0.0029351 | -0.00073451 | 0.0029352 | 0.00073442 | 8.3198e-08 | -8.3278e-08 | 0.0044905 | 0.0044905 | 0.0044905 | 0.97251 | -0.53041 | 0.97254 | -0.52981 | 1.2337
55 | 0.0011967 | 0.00029959 | -0.0011966 | -0.0002999 | 3.3416e-08 | -3.0843e-07 | 0.0018309 | 0.001831 | 0.001831 | 0.97251 | -0.53041 | 0.97248 | -0.531 | 0.50301
56 | -0.0054345 | -0.0013608 | 0.0054349 | 0.0013609 | 3.9549e-07 | 6.3795e-08 | 0.0083145 | 0.0083145 | 0.0083145 | 0.97254 | -0.52981 | 0.97262 | -0.52829 | 2.2842
57 | -0.0054349 | -0.0013609 | 0.0054353 | 0.0013609 | 3.6513e-07 | 5.8868e-08 | 0.0083145 | 0.0083144 | 0.0083145 | 0.97262 | -0.52829 | 0.97269 | -0.52688 | 2.2842
58 | 0.0047316 | 0.0011857 | -0.0047315 | -0.0011857 | 1.1464e-07 | 1.5313e-09 | 0.007253 | 0.007253 | 0.007253 | 0.97072 | -0.56434 | 0.9707 | -0.56485 | 1.9926
59 | 0.01901 | 0.0047667 | -0.019007 | -0.0047647 | 3.2948e-06 | 1.9806e-06 | 0.029131 | 0.029131 | 0.029131 | 0.97107 | -0.55754 | 0.97088 | -0.56117 | 8.003
60 | -0.020363 | -0.0051067 | 0.020367 | 0.0051091 | 3.9078e-06 | 2.3631e-06 | 0.030891 | 0.030891 | 0.030891 | 0.98091 | -0.36595 | 0.98112 | -0.36193 | 8.4866
61 | 0.00042096 | 0.00010533 | -0.00042096 | -0.0001055 | 2.1217e-09 | -1.7395e-07 | 0.00063839 | 0.00063845 | 0.00063845 | 0.98112 | -0.36193 | 0.98111 | -0.36203 | 0.1754
62 | -0.020788 | -0.0052144 | 0.020797 | 0.0052198 | 8.9797e-06 | 5.4427e-06 | 0.03153 | 0.03153 | 0.03153 | 0.98112 | -0.36193 | 0.98158 | -0.35287 | 8.662
63 | -0.023446 | -0.0058837 | 0.023463 | 0.0058942 | 1.7086e-05 | 1.0479e-05 | 0.035545 | 0.035545 | 0.035545 | 0.98158 | -0.35287 | 0.98236 | -0.3376 | 9.7651
64 | -0.025133 | -0.0063127 | 0.025148 | 0.0063222 | 1.531e-05 | 9.4415e-06 | 0.038074 | 0.038074 | 0.038074 | 0.98236 | -0.3376 | 0.98301 | -0.32484 | 10.46
65 | -0.026265 | -0.0066022 | 0.026273 | 0.006607 | 7.8608e-06 | 4.8628e-06 | 0.039766 | 0.039765 | 0.039766 | 0.98301 | -0.32484 | 0.98333 | -0.31858 | 10.9246
66 | 0.0023572 | 0.00058716 | -0.0023569 | -0.00058762 | 2.36e-07 | -4.586e-07 | 0.003592 | 0.0035922 | 0.0035922 | 0.97614 | -0.46001 | 0.97603 | -0.46212 | 0.98686
67 | 0.0023569 | 0.00058762 | -0.0023557 | -0.00058994 | 1.1949e-06 | -2.3188e-06 | 0.0035922 | 0.0035933 | 0.0035933 | 0.97603 | -0.46212 | 0.97549 | -0.47279 | 0.98717
68 | 0.0023557 | 0.00058994 | -0.0023555 | -0.00059035 | 2.1179e-07 | -4.1044e-07 | 0.0035933 | 0.0035935 | 0.0035935 | 0.97549 | -0.47279 | 0.97539 | -0.47468 | 0.98722
69 | 0.0013544 | 0.00033903 | -0.0013544 | -0.00033944 | 5.4782e-08 | -4.0776e-07 | 0.0020475 | 0.0020477 | 0.0020477 | 0.98426 | -0.30068 | 0.98421 | -0.30153 | 0.56254
70 | -0.0028056 | -0.00070273 | 0.0028057 | 0.00070254 | 1.4919e-07 | -1.8562e-07 | 0.0042414 | 0.0042413 | 0.0042414 | 0.98426 | -0.30068 | 0.98431 | -0.29956 | 1.1652
71 | -0.079491 | -0.020121 | 0.079632 | 0.020211 | 0.0001409 | 8.9844e-05 | 0.12024 | 0.12024 | 0.12024 | 0.98431 | -0.29956 | 0.98622 | -0.26271 | 33.0329
72 | 0.076685 | 0.019418 | -0.076615 | -0.019374 | 6.9956e-05 | 4.4596e-05 | 0.116 | 0.116 | 0.116 | 0.98431 | -0.29956 | 0.98333 | -0.31858 | 31.8677
73 | -0.080131 | -0.020336 | 0.080327 | 0.020461 | 0.00019591 | 0.00012492 | 0.12099 | 0.12099 | 0.12099 | 0.98622 | -0.26271 | 0.98885 | -0.21201 | 33.2397
74 | 0.050342 | 0.012767 | -0.050231 | -0.012697 | 0.00011083 | 7.029e-05 | 0.076233 | 0.076233 | 0.076233 | 0.98333 | -0.31858 | 0.98097 | -0.36448 | 20.9432
75 | -0.0023298 | -0.0005839 | 0.0023298 | 0.00058377 | 6.1785e-08 | -1.3054e-07 | 0.0035155 | 0.0035155 | 0.0035155 | 0.98613 | -0.26462 | 0.98616 | -0.26406 | 0.9658
76 | -0.08534 | -0.021607 | 0.085365 | 0.021623 | 2.5902e-05 | 1.6365e-05 | 0.12885 | 0.12885 | 0.12885 | 0.98616 | -0.26406 | 0.98648 | -0.25774 | 17.6988
77 | 0.08301 | 0.021023 | -0.082991 | -0.021011 | 1.8856e-05 | 1.2027e-05 | 0.12533 | 0.12533 | 0.12533 | 0.98616 | -0.26406 | 0.98591 | -0.26879 | 34.4319
78 | -0.17418 | -0.044284 | 0.17431 | 0.044368 | 0.00013189 | 8.3816e-05 | 0.26233 | 0.26233 | 0.26233 | 0.98885 | -0.21201 | 0.98967 | -0.19631 | 24.0228
79 | 0.092205 | 0.023411 | -0.092151 | -0.023377 | 5.424e-05 | 3.3848e-05 | 0.13886 | 0.13886 | 0.13886 | 0.98885 | -0.21201 | 0.98822 | -0.22425 | 12.7158
80 | 0.001648 | 0.00041287 | -0.001648 | -0.00041302 | 3.0804e-08 | -1.5163e-07 | 0.0024799 | 0.0024799 | 0.0024799 | 0.98885 | -0.21201 | 0.98883 | -0.21241 | 0.6813
81 | 0.048324 | 0.012219 | -0.04828 | -0.012191 | 4.3336e-05 | 2.7464e-05 | 0.07334 | 0.07334 | 0.07334 | 0.98097 | -0.36448 | 0.98001 | -0.3832 | 20.1483
82 | -0.08743 | -0.02214 | 0.087472 | 0.022166 | 4.1842e-05 | 2.6042e-05 | 0.13196 | 0.13196 | 0.13196 | 0.98648 | -0.25774 | 0.987 | -0.24778 | 12.0844
83 | 0.056769 | 0.014423 | -0.056627 | -0.014333 | 0.00014174 | 9.0057e-05 | 0.08575 | 0.085751 | 0.085751 | 0.98591 | -0.26879 | 0.98322 | -0.32079 | 23.5579
84 | 0.026222 | 0.0065875 | -0.026201 | -0.0065745 | 2.1087e-05 | 1.3038e-05 | 0.039582 | 0.039582 | 0.039582 | 0.98591 | -0.26879 | 0.98505 | -0.28566 | 10.8742
85 | -0.1752 | -0.044591 | 0.17543 | 0.044737 | 0.00023036 | 0.00014641 | 0.26366 | 0.26366 | 0.26366 | 0.98967 | -0.19631 | 0.99109 | -0.16907 | 24.145
86 | 0.091471 | 0.023206 | -0.091455 | -0.023196 | 1.5906e-05 | 9.9226e-06 | 0.13783 | 0.13783 | 0.13783 | 0.98822 | -0.22425 | 0.98803 | -0.22786 | 12.6221
87 | 0.047157 | 0.01191 | -0.047115 | -0.011883 | 4.1948e-05 | 2.6572e-05 | 0.071635 | 0.071635 | 0.071635 | 0.98001 | -0.3832 | 0.97906 | -0.40178 | 19.6799
88 | -0.0090378 | -0.0022638 | 0.0090394 | 0.0022646 | 1.6207e-06 | 7.5654e-07 | 0.013825 | 0.013825 | 0.013825 | 0.97269 | -0.52688 | 0.97288 | -0.52311 | 3.7982
89 | -0.04605 | -0.01161 | 0.046077 | 0.011627 | 2.7173e-05 | 1.7206e-05 | 0.070137 | 0.070137 | 0.070137 | 0.97733 | -0.43445 | 0.97796 | -0.42213 | 19.2684
90 | 0.044943 | 0.011332 | -0.044916 | -0.011315 | 2.6901e-05 | 1.7025e-05 | 0.068451 | 0.068452 | 0.068452 | 0.97733 | -0.43445 | 0.97669 | -0.44696 | 18.8054
91 | -0.047662 | -0.012024 | 0.047696 | 0.012046 | 3.446e-05 | 2.1835e-05 | 0.072548 | 0.072548 | 0.072548 | 0.97796 | -0.42213 | 0.97873 | -0.40704 | 19.9308
92 | 0.043057 | 0.01085 | -0.043034 | -0.010835 | 2.3389e-05 | 1.4788e-05 | 0.06562 | 0.06562 | 0.06562 | 0.97669 | -0.44696 | 0.97611 | -0.45833 | 18.0274
93 | -0.048982 | -0.012368 | 0.049025 | 0.012396 | 4.2786e-05 | 2.7125e-05 | 0.074503 | 0.074503 | 0.074503 | 0.97873 | -0.40704 | 0.97966 | -0.38882 | 20.4679
94 | 0.0043922 | 0.0010998 | -0.0043918 | -0.0010999 | 3.7577e-07 | -3.8901e-08 | 0.0066953 | 0.0066954 | 0.0066954 | 0.97611 | -0.45833 | 0.97602 | -0.46012 | 1.8394
95 | 0.038641 | 0.009735 | -0.038603 | -0.0097104 | 3.8918e-05 | 2.4534e-05 | 0.058925 | 0.058925 | 0.058925 | 0.97611 | -0.45833 | 0.97504 | -0.47941 | 16.1881
96 | -0.050786 | -0.012837 | 0.050792 | 0.01284 | 5.3582e-06 | 3.399e-06 | 0.077179 | 0.077179 | 0.077179 | 0.97966 | -0.38882 | 0.97978 | -0.38662 | 21.203
97 | 0.0030177 | 0.00075548 | -0.0030176 | -0.00075558 | 1.1262e-07 | -1.0526e-07 | 0.0046004 | 0.0046005 | 0.0046005 | 0.97602 | -0.46012 | 0.97598 | -0.46091 | 1.2639
98 | 0.03583 | 0.0090157 | -0.035819 | -0.0090083 | 1.1746e-05 | 7.3867e-06 | 0.054694 | 0.054694 | 0.054694 | 0.97504 | -0.47941 | 0.97469 | -0.48627 | 15.0259
99 | -0.05301 | -0.013396 | 0.053068 | 0.013433 | 5.7315e-05 | 3.6385e-05 | 0.080548 | 0.080548 | 0.080548 | 0.97978 | -0.38662 | 0.98093 | -0.3641 | 22.1287
100 | 0.0013958 | 0.00034959 | -0.0013958 | -0.00034982 | 3.3293e-08 | -2.2367e-07 | 0.002128 | 0.0021281 | 0.0021281 | 0.97598 | -0.46091 | 0.97595 | -0.46141 | 0.58465
101 | 0.0016218 | 0.00040599 | -0.0016217 | -0.00040631 | 6.6516e-08 | -3.2e-07 | 0.0024724 | 0.0024726 | 0.0024726 | 0.97598 | -0.46091 | 0.97594 | -0.46177 | 0.67928
102 | 0.034056 | 0.0085664 | -0.034038 | -0.0085552 | 1.7872e-05 | 1.1219e-05 | 0.052003 | 0.052003 | 0.052003 | 0.97469 | -0.48627 | 0.97413 | -0.49726 | 14.2865
103 | -0.0016217 | -0.00040643 | 0.0016217 | 0.00040631 | 2.4977e-08 | -1.2015e-07 | 0.0024726 | 0.0024726 | 0.0024726 | 0.97592 | -0.46209 | 0.97594 | -0.46177 | 0.67929
104 | 0.38469 | 0.099443 | -0.38355 | -0.098713 | 0.0011423 | 0.00072997 | 0.5735 | 0.5735 | 0.5735 | 1 | 0 | 0.99676 | -0.061037 | 52.5185
105 | 0.20061 | 0.051655 | -0.20027 | -0.051437 | 0.00034287 | 0.00021823 | 0.299 | 0.299 | 0.299 | 1 | 0 | 0.99813 | -0.035193 | 27.3814
106 | 0.38355 | 0.098713 | -0.38254 | -0.098072 | 0.0010032 | 0.0006411 | 0.5735 | 0.5735 | 0.5735 | 0.99676 | -0.061037 | 0.99391 | -0.11497 | 52.5185
107 | 0.20027 | 0.051437 | -0.20002 | -0.05128 | 0.0002463 | 0.00015677 | 0.299 | 0.29901 | 0.29901 | 0.99813 | -0.035193 | 0.99679 | -0.060556 | 27.3814
108 | 0.094055 | 0.02394 | -0.093888 | -0.023834 | 0.00016714 | 0.00010668 | 0.14094 | 0.14094 | 0.14094 | 0.99391 | -0.11497 | 0.99198 | -0.1519 | 38.721
109 | 0.28849 | 0.074132 | -0.28813 | -0.073904 | 0.00035687 | 0.0002278 | 0.43256 | 0.43256 | 0.43256 | 0.99391 | -0.11497 | 0.99257 | -0.14047 | 39.6116
110 | 0.19651 | 0.0504 | -0.19633 | -0.050285 | 0.00017984 | 0.00011444 | 0.29376 | 0.29376 | 0.29376 | 0.99679 | -0.060556 | 0.9958 | -0.079444 | 26.901
111 | 0.092757 | 0.02355 | -0.092611 | -0.023457 | 0.000146 | 9.3182e-05 | 0.13925 | 0.13925 | 0.13925 | 0.99198 | -0.1519 | 0.99028 | -0.18467 | 38.2548
112 | 0.28277 | 0.07256 | -0.28273 | -0.07254 | 3.1677e-05 | 2.0219e-05 | 0.42452 | 0.42452 | 0.42452 | 0.99257 | -0.14047 | 0.99244 | -0.14278 | 38.8752
113 | 0.19486 | 0.049916 | -0.1948 | -0.049878 | 5.974e-05 | 3.8015e-05 | 0.29156 | 0.29156 | 0.29156 | 0.9958 | -0.079444 | 0.99546 | -0.085773 | 26.6993
114 | 0.27847 | 0.07147 | -0.27794 | -0.071137 | 0.00052052 | 0.00033221 | 0.41812 | 0.41812 | 0.41812 | 0.99244 | -0.14278 | 0.99042 | -0.18138 | 38.289
115 | 0.18899 | 0.048423 | -0.18864 | -0.048201 | 0.0003494 | 0.00022226 | 0.28288 | 0.28288 | 0.28288 | 0.99546 | -0.085773 | 0.99345 | -0.124 | 25.905
116 | -0.0033238 | -0.00083289 | 0.0033239 | 0.00083285 | 6.5869e-08 | -4.7246e-08 | 0.005011 | 0.005011 | 0.005011 | 0.987 | -0.24703 | 0.98702 | -0.24661 | 1.3767
117 | 0.0017234 | 0.00043178 | -0.0017233 | -0.00043191 | 2.9394e-08 | -1.2959e-07 | 0.0025981 | 0.0025982 | 0.0025982 | 0.987 | -0.24703 | 0.98698 | -0.24738 | 0.71378
118 | -0.0050652 | -0.0012693 | 0.0050657 | 0.0012693 | 4.7527e-07 | 2.6348e-08 | 0.0076361 | 0.007636 | 0.0076361 | 0.98702 | -0.24661 | 0.98712 | -0.24464 | 2.0978
119 | -0.007957 | -0.0019939 | 0.0079587 | 0.0019946 | 1.6802e-06 | 6.771e-07 | 0.011995 | 0.011994 | 0.011995 | 0.98712 | -0.24464 | 0.98735 | -0.24021 | 3.2952
120 | -0.26654 | -0.067984 | 0.26716 | 0.06838 | 0.00061998 | 0.00039561 | 0.40213 | 0.40213 | 0.40213 | 0.98735 | -0.24021 | 0.98985 | -0.19216 | 36.8248
121 | 0.25858 | 0.06599 | -0.25837 | -0.065851 | 0.00021712 | 0.00013852 | 0.39013 | 0.39013 | 0.39013 | 0.98735 | -0.24021 | 0.98644 | -0.2576 | 35.7264
122 | -0.27219 | -0.069639 | 0.27233 | 0.06973 | 0.00014218 | 9.0732e-05 | 0.40968 | 0.40968 | 0.40968 | 0.98985 | -0.19216 | 0.99042 | -0.18138 | 37.5163
123 | 0.0062045 | 0.001555 | -0.0062035 | -0.0015547 | 1.0699e-06 | 2.6903e-07 | 0.0093594 | 0.0093595 | 0.0093595 | 0.98644 | -0.2576 | 0.98625 | -0.26122 | 2.5713
124 | 0.25216 | 0.064296 | -0.25211 | -0.064265 | 4.9145e-05 | 3.1349e-05 | 0.38077 | 0.38077 | 0.38077 | 0.98644 | -0.2576 | 0.98623 | -0.26164 | 34.8693
125 | -0.012851 | -0.0032213 | 0.012853 | 0.0032224 | 1.9753e-06 | 1.0964e-06 | 0.019699 | 0.019699 | 0.019699 | 0.97072 | -0.5644 | 0.97088 | -0.56117 | 5.4119
126 | 0.012851 | 0.0032213 | -0.012849 | -0.0032201 | 2.0727e-06 | 1.1505e-06 | 0.019699 | 0.019699 | 0.019699 | 0.97072 | -0.5644 | 0.97055 | -0.56779 | 5.4119
127 | 0.0062036 | 0.0015547 | -0.0062027 | -0.0015544 | 8.6621e-07 | 2.3887e-07 | 0.0095111 | 0.0095112 | 0.0095112 | 0.97055 | -0.56779 | 0.9704 | -0.57072 | 2.613
128 | 0.065709 | 0.016607 | -0.065627 | -0.016555 | 8.1997e-05 | 5.2195e-05 | 0.099152 | 0.099152 | 0.099152 | 0.98661 | -0.25541 | 0.98527 | -0.28147 | 27.2396
129 | 0.0035533 | 0.00089045 | -0.0035532 | -0.00089051 | 1.3085e-07 | -6.1454e-08 | 0.0054486 | 0.0054487 | 0.0054487 | 0.9704 | -0.57072 | 0.97036 | -0.57149 | 1.4969
130 | 0.06292 | 0.015877 | -0.062884 | -0.015854 | 3.6347e-05 | 2.3126e-05 | 0.095065 | 0.095065 | 0.095065 | 0.98527 | -0.28147 | 0.98465 | -0.29354 | 26.1167
131 | -0.0029185 | -0.00073144 | 0.0029187 | 0.0007312 | 2.41e-07 | -2.4422e-07 | 0.0044697 | 0.0044695 | 0.0044697 | 0.97161 | -0.5469 | 0.97169 | -0.54517 | 1.2279
132 | -0.0047908 | -0.0012004 | 0.004791 | 0.0012004 | 1.6166e-07 | 4.2421e-09 | 0.0073363 | 0.0073363 | 0.0073363 | 0.97169 | -0.54517 | 0.97173 | -0.54446 | 2.0155
133 | -0.0066558 | -0.0016678 | 0.0066559 | 0.0016678 | 1.7094e-07 | 5.5035e-08 | 0.010192 | 0.010192 | 0.010192 | 0.97173 | -0.54446 | 0.97176 | -0.54392 | 2.8
134 | 0.0064674 | 0.0016197 | -0.0064667 | -0.0016195 | 6.1895e-07 | 1.7908e-07 | 0.0098037 | 0.0098038 | 0.0098038 | 0.98158 | -0.35288 | 0.98147 | -0.35489 | 2.6934
135 | -0.0077213 | -0.0019339 | 0.0077223 | 0.0019343 | 1.0596e-06 | 4.174e-07 | 0.011705 | 0.011705 | 0.011705 | 0.98158 | -0.35288 | 0.98172 | -0.35 | 3.2156
136 | 0.0052154 | 0.0013059 | -0.0052115 | -0.0013055 | 3.8777e-06 | 3.9324e-07 | 0.0079066 | 0.0079074 | 0.0079074 | 0.98147 | -0.35489 | 0.98068 | -0.37052 | 2.1724
137 | -0.0086706 | -0.002172 | 0.0086741 | 0.0021735 | 3.456e-06 | 1.5368e-06 | 0.013142 | 0.013142 | 0.013142 | 0.98172 | -0.35 | 0.98215 | -0.34164 | 3.6104
138 | 0.00129 | 0.00032264 | -0.00129 | -0.00032298 | 4.0747e-08 | -3.3181e-07 | 0.0019571 | 0.0019573 | 0.0019573 | 0.98068 | -0.37052 | 0.98064 | -0.37118 | 0.53771
139 | -0.055018 | -0.013909 | 0.055073 | 0.013944 | 5.5053e-05 | 3.4967e-05 | 0.083399 | 0.083399 | 0.083399 | 0.98215 | -0.34164 | 0.98322 | -0.32079 | 22.9118
140 | 0.046344 | 0.011735 | -0.046342 | -0.011734 | 2.2349e-06 | 1.4151e-06 | 0.070257 | 0.070257 | 0.070257 | 0.98215 | -0.34164 | 0.9821 | -0.34264 | 19.3015
141 | -0.0012899 | -0.00032328 | 0.00129 | 0.00032298 | 3.7858e-08 | -3.0821e-07 | 0.0019574 | 0.0019573 | 0.0019574 | 0.98061 | -0.3718 | 0.98064 | -0.37118 | 0.53774
142 | 0.045003 | 0.011398 | -0.044965 | -0.011374 | 3.7736e-05 | 2.3878e-05 | 0.068228 | 0.068228 | 0.068228 | 0.9821 | -0.34264 | 0.9812 | -0.36012 | 18.744
143 | 0.043924 | 0.011113 | -0.043904 | -0.011101 | 2.0223e-05 | 1.279e-05 | 0.06665 | 0.06665 | 0.06665 | 0.9812 | -0.36012 | 0.98071 | -0.36971 | 18.3104
144 | 0.18507 | 0.047306 | -0.18494 | -0.047221 | 0.00013305 | 8.4617e-05 | 0.27753 | 0.27753 | 0.27753 | 0.99345 | -0.124 | 0.99267 | -0.13887 | 25.4149
145 | 0.18266 | 0.046651 | -0.1826 | -0.04661 | 6.3419e-05 | 4.0327e-05 | 0.27412 | 0.27412 | 0.27412 | 0.99267 | -0.13887 | 0.9923 | -0.14606 | 25.1026
146 | 0.18026 | 0.046024 | -0.18012 | -0.045936 | 0.00013887 | 8.8291e-05 | 0.27061 | 0.27061 | 0.27061 | 0.9923 | -0.14606 | 0.99146 | -0.16201 | 24.7816
147 | 0.16609 | 0.042113 | -0.166 | -0.042055 | 9.2107e-05 | 5.8509e-05 | 0.25207 | 0.25207 | 0.25207 | 0.98116 | -0.35966 | 0.98056 | -0.37121 | 23.083
148 | -0.16783 | -0.042549 | 0.16788 | 0.042584 | 5.5273e-05 | 3.5116e-05 | 0.2547 | 0.2547 | 0.2547 | 0.98116 | -0.35966 | 0.98151 | -0.35282 | 23.3242
149 | 0.16379 | 0.041502 | -0.16368 | -0.041434 | 0.00010718 | 6.8073e-05 | 0.24872 | 0.24872 | 0.24872 | 0.98056 | -0.37121 | 0.97986 | -0.38484 | 22.7762
150 | -0.16879 | -0.04281 | 0.16893 | 0.042902 | 0.00014435 | 9.1717e-05 | 0.25607 | 0.25607 | 0.25607 | 0.98151 | -0.35282 | 0.98243 | -0.33504 | 23.4498
151 | 0.16088 | 0.040732 | -0.16079 | -0.04067 | 9.7196e-05 | 6.1714e-05 | 0.24447 | 0.24447 | 0.24447 | 0.97986 | -0.38484 | 0.97922 | -0.39743 | 22.3871
152 | -0.24735 | -0.06273 | 0.24764 | 0.062918 | 0.00029327 | 0.00018706 | 0.3749 | 0.3749 | 0.3749 | 0.98243 | -0.33504 | 0.9837 | -0.31041 | 34.3319
153 | 0.020361 | 0.005115 | -0.020351 | -0.0051091 | 9.7001e-06 | 5.864e-06 | 0.030844 | 0.030844 | 0.030844 | 0.98243 | -0.33504 | 0.98192 | -0.34503 | 8.4736
154 | 0.058054 | 0.014713 | -0.057973 | -0.014662 | 8.0927e-05 | 5.1441e-05 | 0.087989 | 0.087989 | 0.087989 | 0.98243 | -0.33504 | 0.98093 | -0.3641 | 24.1729
155 | 0.14933 | 0.037799 | -0.14922 | -0.037729 | 0.00011041 | 7.0018e-05 | 0.22706 | 0.22706 | 0.22706 | 0.97922 | -0.39743 | 0.97843 | -0.41285 | 20.7931
156 | 0.011454 | 0.0028715 | -0.011452 | -0.0028703 | 2.2198e-06 | 1.1749e-06 | 0.017406 | 0.017406 | 0.017406 | 0.97922 | -0.39743 | 0.97901 | -0.4015 | 4.7819
157 | -0.24853 | -0.063141 | 0.24912 | 0.063515 | 0.00058503 | 0.00037316 | 0.37626 | 0.37626 | 0.37626 | 0.9837 | -0.31041 | 0.98623 | -0.26164 | 34.4556
158 | 0.0185 | 0.0046452 | -0.018495 | -0.004642 | 5.3843e-06 | 3.215e-06 | 0.028039 | 0.028039 | 0.028039 | 0.98192 | -0.34503 | 0.98161 | -0.35113 | 7.703
159 | 0.0049056 | 0.001229 | -0.0049051 | -0.001229 | 4.58e-07 | 1.4716e-08 | 0.0074413 | 0.0074414 | 0.0074414 | 0.98093 | -0.3641 | 0.98083 | -0.36606 | 2.0443
160 | 0.14701 | 0.037174 | -0.14682 | -0.037055 | 0.00018693 | 0.00011851 | 0.22369 | 0.22369 | 0.22369 | 0.97843 | -0.41285 | 0.97707 | -0.43939 | 20.4846
161 | 0.0097662 | 0.0024478 | -0.0097654 | -0.0024474 | 7.6165e-07 | 3.7156e-07 | 0.014844 | 0.014844 | 0.014844 | 0.97901 | -0.4015 | 0.97893 | -0.40314 | 4.078
162 | 0.017363 | 0.0043582 | -0.017357 | -0.0043551 | 5.2409e-06 | 3.0993e-06 | 0.026323 | 0.026323 | 0.026323 | 0.98161 | -0.35113 | 0.98128 | -0.35746 | 7.2315
163 | 0.0024258 | 0.0006076 | -0.0024256 | -0.00060792 | 1.7168e-07 | -3.1674e-07 | 0.00368 | 0.0036802 | 0.0036802 | 0.98083 | -0.36606 | 0.98076 | -0.36754 | 1.011
164 | -0.037747 | -0.0095282 | 0.037756 | 0.0095337 | 8.6972e-06 | 5.4778e-06 | 0.057419 | 0.057419 | 0.057419 | 0.97864 | -0.40993 | 0.97889 | -0.40512 | 15.7745
165 | 0.036521 | 0.009221 | -0.036485 | -0.009198 | 3.6463e-05 | 2.2941e-05 | 0.055555 | 0.055555 | 0.055555 | 0.97864 | -0.40993 | 0.97758 | -0.43079 | 15.2624
166 | -0.039684 | -0.010017 | 0.039715 | 0.010037 | 3.0945e-05 | 1.952e-05 | 0.06035 | 0.06035 | 0.06035 | 0.97889 | -0.40512 | 0.97972 | -0.38886 | 16.5797
167 | 0.0019033 | 0.00047662 | -0.0019032 | -0.00047698 | 1.0835e-07 | -3.6225e-07 | 0.0028969 | 0.0028971 | 0.0028971 | 0.97758 | -0.43079 | 0.97752 | -0.43199 | 0.79591
168 | 0.034582 | 0.0087214 | -0.034577 | -0.0087186 | 4.534e-06 | 2.8471e-06 | 0.052658 | 0.052658 | 0.052658 | 0.97758 | -0.43079 | 0.97744 | -0.43353 | 14.4665
169 | -0.040683 | -0.010279 | 0.040704 | 0.010292 | 2.1371e-05 | 1.3489e-05 | 0.06182 | 0.06182 | 0.06182 | 0.97972 | -0.38886 | 0.98028 | -0.37791 | 16.9834
170 | 0.033437 | 0.0084327 | -0.033421 | -0.008423 | 1.5481e-05 | 9.7086e-06 | 0.050922 | 0.050922 | 0.050922 | 0.97744 | -0.43353 | 0.97694 | -0.44321 | 13.9895
171 | -0.041698 | -0.010541 | 0.041714 | 0.010552 | 1.6386e-05 | 1.035e-05 | 0.063327 | 0.063327 | 0.063327 | 0.98028 | -0.37791 | 0.98071 | -0.36971 | 17.3976
172 | 0.032227 | 0.0081238 | -0.032187 | -0.0080987 | 4.0162e-05 | 2.5148e-05 | 0.049104 | 0.049104 | 0.049104 | 0.97694 | -0.44321 | 0.97561 | -0.46929 | 13.4901
173 | 0.030572 | 0.0076939 | -0.030571 | -0.0076934 | 7.384e-07 | 4.6127e-07 | 0.04664 | 0.04664 | 0.04664 | 0.97561 | -0.46929 | 0.97559 | -0.46979 | 12.8133
174 | 0.021799 | 0.0054733 | -0.02179 | -0.0054679 | 8.9226e-06 | 5.4448e-06 | 0.033344 | 0.033344 | 0.033344 | 0.9729 | -0.52145 | 0.97247 | -0.53003 | 9.1604
175 | -0.03053 | -0.0076625 | 0.030544 | 0.0076713 | 1.3995e-05 | 8.7442e-06 | 0.046699 | 0.046699 | 0.046699 | 0.9729 | -0.52145 | 0.97339 | -0.51184 | 12.8293
176 | 0.0067323 | 0.0016881 | -0.0067209 | -0.0016844 | 1.1332e-05 | 3.7201e-06 | 0.010297 | 0.010298 | 0.010298 | 0.9729 | -0.52145 | 0.97111 | -0.5568 | 2.8292
177 | 0.020948 | 0.005257 | -0.020943 | -0.0052538 | 5.1918e-06 | 3.1557e-06 | 0.032056 | 0.032057 | 0.032057 | 0.97247 | -0.53003 | 0.9722 | -0.53523 | 8.8067
178 | -0.030544 | -0.0076713 | 0.030547 | 0.007673 | 2.8294e-06 | 1.7678e-06 | 0.046699 | 0.046699 | 0.046699 | 0.97339 | -0.51184 | 0.97349 | -0.5099 | 12.8293
179 | 0.0067209 | 0.0016844 | -0.0067204 | -0.0016843 | 4.9218e-07 | 1.6189e-07 | 0.010298 | 0.010298 | 0.010298 | 0.97111 | -0.5568 | 0.97104 | -0.55834 | 2.8292
180 | 0.019254 | 0.0048304 | -0.019248 | -0.0048273 | 5.2242e-06 | 3.1447e-06 | 0.029471 | 0.029471 | 0.029471 | 0.9722 | -0.53523 | 0.97192 | -0.54092 | 8.0964
181 | -0.032279 | -0.0081072 | 0.032299 | 0.0081194 | 1.948e-05 | 1.2202e-05 | 0.049347 | 0.049346 | 0.049347 | 0.97349 | -0.5099 | 0.97413 | -0.49726 | 13.5567
182 | 0.0045429 | 0.0011385 | -0.0045428 | -0.0011385 | 1.4305e-07 | -5.8143e-09 | 0.0069616 | 0.0069616 | 0.0069616 | 0.97104 | -0.55834 | 0.971 | -0.559 | 1.9125
183 | 0.002899 | 0.00072657 | -0.002899 | -0.00072657 | 3.4331e-09 | -3.5402e-09 | 0.0044427 | 0.0044427 | 0.0044427 | 0.971 | -0.559 | 0.971 | -0.55902 | 1.2205
184 | 0.017094 | 0.0042874 | -0.017089 | -0.004284 | 5.8254e-06 | 3.4473e-06 | 0.026173 | 0.026173 | 0.026173 | 0.97192 | -0.54092 | 0.97155 | -0.54807 | 7.1904
185 | 0.012161 | 0.003049 | -0.012159 | -0.003048 | 1.8703e-06 | 1.019e-06 | 0.018626 | 0.018626 | 0.018626 | 0.97155 | -0.54807 | 0.97139 | -0.5513 | 5.117
186 | -0.0060538 | -0.0015169 | 0.0060543 | 0.001517 | 4.7953e-07 | 1.1348e-07 | 0.0091595 | 0.0091595 | 0.0091595 | 0.98346 | -0.31667 | 0.98354 | -0.31501 | 2.5164
187 | 0.0034226 | 0.00085749 | -0.0034224 | -0.0008576 | 1.7852e-07 | -1.1099e-07 | 0.0051784 | 0.0051785 | 0.0051785 | 0.98346 | -0.31667 | 0.9834 | -0.31777 | 1.4227
188 | -0.0079113 | -0.0019825 | 0.0079117 | 0.0019826 | 3.8738e-07 | 1.564e-07 | 0.011969 | 0.011969 | 0.011969 | 0.98354 | -0.31501 | 0.98359 | -0.31398 | 3.2882
189 | 0.001713 | 0.0004292 | -0.001713 | -0.00042932 | 2.8168e-08 | -1.2381e-07 | 0.002592 | 0.0025921 | 0.0025921 | 0.9834 | -0.31777 | 0.98338 | -0.31811 | 0.71211
190 | -0.0091742 | -0.002299 | 0.0091757 | 0.0022997 | 1.4953e-06 | 6.9422e-07 | 0.013879 | 0.013879 | 0.013879 | 0.98359 | -0.31398 | 0.98377 | -0.31056 | 3.8129
191 | -0.011599 | -0.002907 | 0.011599 | 0.0029071 | 1.3893e-07 | 7.3632e-08 | 0.017544 | 0.017544 | 0.017544 | 0.98377 | -0.31056 | 0.98378 | -0.31031 | 4.8197
192 | -0.01482 | -0.0037144 | 0.014824 | 0.0037167 | 3.8801e-06 | 2.2217e-06 | 0.022416 | 0.022416 | 0.022416 | 0.98378 | -0.31031 | 0.98406 | -0.30482 | 6.1584
193 | -0.0018822 | -0.00047173 | 0.0018823 | 0.00047153 | 6.0005e-08 | -1.9952e-07 | 0.0028844 | 0.0028843 | 0.0028844 | 0.97101 | -0.56002 | 0.97105 | -0.55935 | 0.79241
194 | -0.0043199 | -0.0010825 | 0.00432 | 0.0010825 | 1.0089e-07 | -1.1383e-08 | 0.0066197 | 0.0066197 | 0.0066197 | 0.97105 | -0.55935 | 0.97107 | -0.55886 | 1.8186
195 | -0.016574 | -0.0041552 | 0.016576 | 0.0041565 | 2.3198e-06 | 1.3595e-06 | 0.025062 | 0.025062 | 0.025062 | 0.98406 | -0.30482 | 0.98421 | -0.30188 | 6.8852
196 | -0.0069861 | -0.0017508 | 0.0069865 | 0.0017509 | 3.7285e-07 | 1.2779e-07 | 0.01062 | 0.01062 | 0.01062 | 0.97887 | -0.40426 | 0.97893 | -0.40314 | 2.9175
197 | 0.0032001 | 0.00080195 | -0.0032001 | -0.00080197 | 2.5036e-08 | -1.9442e-08 | 0.0048646 | 0.0048646 | 0.0048646 | 0.97887 | -0.40426 | 0.97886 | -0.40442 | 1.3364
198 | 0.0015941 | 0.00039948 | -0.0015941 | -0.00039952 | 8.4809e-09 | -4.2984e-08 | 0.0024233 | 0.0024233 | 0.0024233 | 0.97886 | -0.40442 | 0.97886 | -0.40453 | 0.66574
199 | 0.010516 | 0.0026362 | -0.010513 | -0.0026349 | 2.4789e-06 | 1.2712e-06 | 0.016109 | 0.016109 | 0.016109 | 0.97139 | -0.5513 | 0.97114 | -0.55625 | 4.4256
200 | 0.0075025 | 0.0018803 | -0.0075019 | -0.00188 | 6.2058e-07 | 2.4224e-07 | 0.011496 | 0.011496 | 0.011496 | 0.97114 | -0.55625 | 0.97105 | -0.55799 | 3.1581
201 | 0.0040911 | 0.0010252 | -0.0040909 | -0.0010253 | 2.4678e-07 | -4.9188e-08 | 0.0062691 | 0.0062691 | 0.0062691 | 0.97105 | -0.55799 | 0.97099 | -0.55925 | 1.7223
202 | 0.028986 | 0.0072961 | -0.028967 | -0.0072843 | 1.8989e-05 | 1.183e-05 | 0.044222 | 0.044222 | 0.044222 | 0.97559 | -0.46979 | 0.97489 | -0.48351 | 12.149
203 | 0.026257 | 0.006605 | -0.026245 | -0.0065976 | 1.2107e-05 | 7.4983e-06 | 0.040086 | 0.040086 | 0.040086 | 0.97489 | -0.48351 | 0.9744 | -0.49317 | 11.0126
204 | 0.024508 | 0.0061623 | -0.024491 | -0.0061516 | 1.7351e-05 | 1.0693e-05 | 0.037434 | 0.037434 | 0.037434 | 0.9744 | -0.49317 | 0.97365 | -0.508 | 10.2842
205 | 0.022569 | 0.0056701 | -0.022558 | -0.0056628 | 1.179e-05 | 7.2175e-06 | 0.034498 | 0.034498 | 0.034498 | 0.97365 | -0.508 | 0.97309 | -0.51895 | 9.4774
206 | -0.0065263 | -0.0016354 | 0.0065283 | 0.001636 | 1.9709e-06 | 6.1102e-07 | 0.010001 | 0.01 | 0.010001 | 0.97107 | -0.55886 | 0.97139 | -0.55252 | 2.7474
207 | -0.010044 | -0.0025171 | 0.010044 | 0.0025172 | 2.5666e-07 | 1.2847e-07 | 0.015385 | 0.015385 | 0.015385 | 0.97139 | -0.55252 | 0.97142 | -0.55199 | 4.2267
208 | -0.011555 | -0.002896 | 0.011558 | 0.0028974 | 2.6303e-06 | 1.4061e-06 | 0.0177 | 0.0177 | 0.0177 | 0.97142 | -0.55199 | 0.97166 | -0.54721 | 4.8628
209 | -0.035051 | -0.0088324 | 0.035075 | 0.0088474 | 2.3736e-05 | 1.4907e-05 | 0.053122 | 0.053122 | 0.053122 | 0.98215 | -0.34213 | 0.98288 | -0.32798 | 14.5939
210 | -0.036572 | -0.0092226 | 0.036579 | 0.0092272 | 7.4108e-06 | 4.6612e-06 | 0.055388 | 0.055388 | 0.055388 | 0.98288 | -0.32798 | 0.98309 | -0.32375 | 15.2166
211 | 0.01991 | 0.0049922 | -0.019907 | -0.0049901 | 3.4462e-06 | 2.0773e-06 | 0.030137 | 0.030137 | 0.030137 | 0.98309 | -0.32375 | 0.98291 | -0.32738 | 8.2794
212 | -0.05649 | -0.014219 | 0.056556 | 0.014262 | 6.6697e-05 | 4.2377e-05 | 0.085525 | 0.085525 | 0.085525 | 0.98309 | -0.32375 | 0.98436 | -0.29908 | 23.4959
213 | 0.013606 | 0.003411 | -0.013604 | -0.0034099 | 1.9476e-06 | 1.0913e-06 | 0.020598 | 0.020599 | 0.020599 | 0.98291 | -0.32738 | 0.98275 | -0.33038 | 5.6589
214 | -0.05797 | -0.014616 | 0.057985 | 0.014626 | 1.5358e-05 | 9.7611e-06 | 0.087662 | 0.087661 | 0.087662 | 0.98436 | -0.29908 | 0.98465 | -0.29354 | 24.0828
215 | 0.011838 | 0.0029673 | -0.011837 | -0.0029667 | 1.1462e-06 | 6.1303e-07 | 0.017925 | 0.017925 | 0.017925 | 0.98275 | -0.33038 | 0.98265 | -0.33242 | 4.9244
216 | 0.0106 | 0.0026567 | -0.010599 | -0.0026564 | 7.3513e-07 | 3.7411e-07 | 0.016052 | 0.016052 | 0.016052 | 0.98265 | -0.33242 | 0.98258 | -0.33387 | 4.4098
217 | -0.0026504 | -0.00066425 | 0.0026504 | 0.00066417 | 5.2802e-08 | -7.6845e-08 | 0.0040144 | 0.0040143 | 0.0040144 | 0.98242 | -0.33688 | 0.98244 | -0.33646 | 1.1028
218 | -0.0026504 | -0.00066417 | 0.0026505 | 0.00066411 | 4.185e-08 | -6.091e-08 | 0.0040143 | 0.0040143 | 0.0040143 | 0.98244 | -0.33646 | 0.98246 | -0.33613 | 1.1028
219 | -0.0035676 | -0.00089414 | 0.0035679 | 0.00089401 | 2.5719e-07 | -1.2506e-07 | 0.0054396 | 0.0054395 | 0.0054396 | 0.97594 | -0.46383 | 0.97602 | -0.46231 | 1.4944
220 | -0.0047375 | -0.0011871 | 0.0047377 | 0.0011871 | 1.9859e-07 | 2.1918e-10 | 0.0072226 | 0.0072226 | 0.0072226 | 0.97602 | -0.46231 | 0.97606 | -0.46143 | 1.9842
221 | -0.0046187 | -0.0011574 | 0.0046189 | 0.0011574 | 1.8821e-07 | -9.4275e-09 | 0.0069954 | 0.0069954 | 0.0069954 | 0.98246 | -0.33613 | 0.9825 | -0.33527 | 1.9218
222 | -0.0021695 | -0.00054372 | 0.0021695 | 0.0005436 | 5.396e-08 | -1.2628e-07 | 0.0033258 | 0.0033257 | 0.0033258 | 0.97067 | -0.56537 | 0.9707 | -0.56485 | 0.91367
223 | -0.0059314 | -0.0014863 | 0.0059314 | 0.0014863 | 2.4789e-08 | 5.4909e-09 | 0.0089831 | 0.0089831 | 0.0089831 | 0.9825 | -0.33527 | 0.98251 | -0.33519 | 2.4679
224 | -0.0092837 | -0.0023265 | 0.0092843 | 0.0023268 | 5.8083e-07 | 2.725e-07 | 0.01406 | 0.01406 | 0.01406 | 0.98251 | -0.33519 | 0.98258 | -0.33387 | 3.8627
225 | -0.018529 | -0.0046459 | 0.018534 | 0.0046491 | 5.3344e-06 | 3.1836e-06 | 0.028014 | 0.028014 | 0.028014 | 0.98421 | -0.30188 | 0.98452 | -0.29584 | 7.6961
226 | -0.02094 | -0.005252 | 0.020943 | 0.0052541 | 3.4431e-06 | 2.087e-06 | 0.03165 | 0.03165 | 0.03165 | 0.98452 | -0.29584 | 0.9847 | -0.29239 | 8.695
227 | -0.023576 | -0.0059138 | 0.023583 | 0.0059185 | 7.5707e-06 | 4.6429e-06 | 0.035628 | 0.035628 | 0.035628 | 0.9847 | -0.29239 | 0.98505 | -0.28566 | 9.7878
228 | 0.020509 | 0.0051494 | -0.020497 | -0.0051425 | 1.1307e-05 | 6.8557e-06 | 0.031365 | 0.031365 | 0.031365 | 0.97309 | -0.51895 | 0.9725 | -0.53052 | 8.6167
229 | 0.018379 | 0.0046116 | -0.018377 | -0.0046102 | 2.2031e-06 | 1.3179e-06 | 0.028123 | 0.028123 | 0.028123 | 0.9725 | -0.53052 | 0.97238 | -0.53303 | 7.7262
230 | 0.018377 | 0.0046102 | -0.01837 | -0.0046063 | 6.5252e-06 | 3.9033e-06 | 0.028123 | 0.028124 | 0.028124 | 0.97238 | -0.53303 | 0.972 | -0.54048 | 7.7263
231 | -0.17771 | -0.04531 | 0.17778 | 0.045348 | 6.0599e-05 | 3.852e-05 | 0.26709 | 0.26709 | 0.26709 | 0.99109 | -0.16907 | 0.99146 | -0.16201 | 24.4592
232 | 0.089134 | 0.022615 | -0.089048 | -0.022561 | 8.5285e-05 | 5.3131e-05 | 0.13434 | 0.13434 | 0.13434 | 0.98803 | -0.22786 | 0.987 | -0.24778 | 12.302
233 | -0.013938 | -0.0034938 | 0.013938 | 0.0034942 | 6.8122e-07 | 3.8659e-07 | 0.021345 | 0.021345 | 0.021345 | 0.97166 | -0.54721 | 0.97171 | -0.54619 | 5.8639
234 | -0.014995 | -0.0037589 | 0.014996 | 0.0037597 | 1.3549e-06 | 7.8221e-07 | 0.022962 | 0.022962 | 0.022962 | 0.97171 | -0.54619 | 0.97181 | -0.54429 | 6.3083
235 | -0.016044 | -0.0040225 | 0.016047 | 0.0040242 | 2.9124e-06 | 1.7045e-06 | 0.024568 | 0.024567 | 0.024568 | 0.97181 | -0.54429 | 0.972 | -0.54048 | 6.7493
236 | -0.038488 | -0.009691 | 0.038525 | 0.0097147 | 3.7641e-05 | 2.3724e-05 | 0.058636 | 0.058636 | 0.058636 | 0.97698 | -0.44238 | 0.97803 | -0.42194 | 16.1087
237 | 0.035565 | 0.0089584 | -0.035511 | -0.0089249 | 5.3331e-05 | 3.3526e-05 | 0.054184 | 0.054184 | 0.054184 | 0.97698 | -0.44238 | 0.97538 | -0.47379 | 14.8858
238 | -0.040035 | -0.010093 | 0.040039 | 0.010096 | 4.0324e-06 | 2.5444e-06 | 0.060932 | 0.060932 | 0.060932 | 0.97803 | -0.42194 | 0.97813 | -0.41984 | 16.7395
239 | 0.032962 | 0.0082861 | -0.032928 | -0.0082645 | 3.4411e-05 | 2.1571e-05 | 0.050296 | 0.050296 | 0.050296 | 0.97538 | -0.47379 | 0.97427 | -0.49567 | 13.8175
240 | -0.041457 | -0.010451 | 0.041483 | 0.010467 | 2.541e-05 | 1.6049e-05 | 0.06309 | 0.06309 | 0.06309 | 0.97813 | -0.41984 | 0.97879 | -0.40704 | 17.3324
241 | 0.019882 | 0.00499 | -0.019864 | -0.0049788 | 1.8497e-05 | 1.1172e-05 | 0.030369 | 0.030369 | 0.030369 | 0.97427 | -0.49567 | 0.97328 | -0.5152 | 8.3433
242 | 0.013046 | 0.0032745 | -0.013041 | -0.0032719 | 4.5726e-06 | 2.5442e-06 | 0.019926 | 0.019927 | 0.019927 | 0.97427 | -0.49567 | 0.9739 | -0.50303 | 5.4743
243 | 0.013041 | 0.0032719 | -0.013034 | -0.0032681 | 6.9883e-06 | 3.8888e-06 | 0.019927 | 0.019927 | 0.019927 | 0.9739 | -0.50303 | 0.97333 | -0.51427 | 5.4744
244 | 0.010749 | 0.0026955 | -0.010744 | -0.0026926 | 5.5861e-06 | 2.89e-06 | 0.016434 | 0.016434 | 0.016434 | 0.97333 | -0.51427 | 0.97278 | -0.52518 | 4.5149
245 | -0.044115 | -0.011127 | 0.044126 | 0.011134 | 1.1116e-05 | 7.0314e-06 | 0.067092 | 0.067092 | 0.067092 | 0.97879 | -0.40704 | 0.97906 | -0.40178 | 18.4318
246 | 0.0092193 | 0.0023105 | -0.0092187 | -0.0023102 | 6.3098e-07 | 2.988e-07 | 0.014102 | 0.014102 | 0.014102 | 0.97278 | -0.52518 | 0.9727 | -0.52662 | 3.8743
247 | 0.0077674 | 0.0019465 | -0.007766 | -0.0019459 | 1.4062e-06 | 5.7037e-07 | 0.011882 | 0.011882 | 0.011882 | 0.9727 | -0.52662 | 0.97251 | -0.53042 | 3.2644
248 | 0.0050462 | 0.0012643 | -0.0050457 | -0.0012642 | 4.9585e-07 | 4.2159e-08 | 0.0077209 | 0.007721 | 0.007721 | 0.97251 | -0.53042 | 0.97241 | -0.53248 | 2.1212
249 | 0.0031811 | 0.00079691 | -0.0031809 | -0.00079701 | 1.2599e-07 | -9.5256e-08 | 0.0048677 | 0.0048677 | 0.0048677 | 0.97241 | -0.53248 | 0.97236 | -0.53331 | 1.3373
250 | 0.015623 | 0.0039205 | -0.015616 | -0.0039162 | 7.3371e-06 | 4.2557e-06 | 0.023693 | 0.023693 | 0.023693 | 0.98128 | -0.35746 | 0.98078 | -0.36732 | 6.5091
251 | 0.014232 | 0.00357 | -0.014224 | -0.0035652 | 8.4116e-06 | 4.7767e-06 | 0.021594 | 0.021594 | 0.021594 | 0.98078 | -0.36732 | 0.98015 | -0.37972 | 5.9324
252 | 0.0013838 | 0.00034626 | -0.0013837 | -0.00034678 | 7.4171e-08 | -5.1887e-07 | 0.0020992 | 0.0020994 | 0.0020994 | 0.98078 | -0.36732 | 0.98072 | -0.36844 | 0.57676
253 | 0.011723 | 0.0029384 | -0.011723 | -0.0029383 | 1.5132e-07 | 8.0786e-08 | 0.017797 | 0.017797 | 0.017797 | 0.98015 | -0.37972 | 0.98013 | -0.37999 | 4.8894
254 | 0.0095498 | 0.0023938 | -0.0095472 | -0.0023925 | 2.6166e-06 | 1.2564e-06 | 0.014498 | 0.014499 | 0.014499 | 0.98013 | -0.37999 | 0.97984 | -0.38575 | 3.9831
255 | 0.0058801 | 0.0014734 | -0.0058799 | -0.0014734 | 2.7286e-07 | 5.9701e-08 | 0.0089297 | 0.0089297 | 0.0089297 | 0.97984 | -0.38575 | 0.97979 | -0.38672 | 2.4532
256 | 0.0021341 | 0.00053465 | -0.0021341 | -0.00053471 | 2.7357e-08 | -6.7336e-08 | 0.0032658 | 0.0032658 | 0.0032658 | 0.97236 | -0.53331 | 0.97235 | -0.53358 | 0.89719
257 | 0.0010586 | 0.00026519 | -0.0010586 | -0.00026532 | 1.1149e-08 | -1.3337e-07 | 0.00162 | 0.0016201 | 0.0016201 | 0.97235 | -0.53358 | 0.97234 | -0.5338 | 0.44508
258 | 0.027385 | 0.0068726 | -0.027369 | -0.0068629 | 1.563e-05 | 9.7082e-06 | 0.041881 | 0.041881 | 0.041881 | 0.97305 | -0.51839 | 0.97244 | -0.53037 | 11.5057
259 | 0.015287 | 0.003832 | -0.015282 | -0.003829 | 5.0893e-06 | 2.9488e-06 | 0.023377 | 0.023377 | 0.023377 | 0.97305 | -0.51839 | 0.97269 | -0.52538 | 6.4223
260 | -0.1376 | -0.034662 | 0.13771 | 0.034728 | 0.00010436 | 6.6081e-05 | 0.20998 | 0.20997 | 0.20998 | 0.97543 | -0.47145 | 0.97624 | -0.4556 | 19.2285
261 | 0.02542 | 0.0063745 | -0.025414 | -0.0063707 | 6.0534e-06 | 3.7418e-06 | 0.038899 | 0.038899 | 0.038899 | 0.97244 | -0.53037 | 0.97219 | -0.53537 | 10.6865
262 | 0.0034316 | 0.00085911 | -0.0034313 | -0.00085931 | 3.6137e-07 | -2.0275e-07 | 0.0052493 | 0.0052495 | 0.0052495 | 0.97269 | -0.52538 | 0.97258 | -0.5276 | 1.4422
263 | -0.1435 | -0.036179 | 0.14356 | 0.036221 | 6.5359e-05 | 4.142e-05 | 0.2188 | 0.2188 | 0.2188 | 0.97624 | -0.4556 | 0.97673 | -0.44609 | 20.0366
264 | 0.0057898 | 0.001451 | -0.005788 | -0.0014506 | 1.826e-06 | 3.8719e-07 | 0.008825 | 0.0088253 | 0.0088253 | 0.97624 | -0.4556 | 0.9759 | -0.46222 | 2.4245
265 | 0.018535 | 0.0046467 | -0.018532 | -0.0046449 | 3.0747e-06 | 1.8415e-06 | 0.02837 | 0.02837 | 0.02837 | 0.97219 | -0.53537 | 0.97201 | -0.53885 | 7.794
266 | 0.0019874 | 0.00049743 | -0.0019871 | -0.00049803 | 2.0188e-07 | -5.9338e-07 | 0.0030403 | 0.0030406 | 0.0030406 | 0.97258 | -0.5276 | 0.97248 | -0.52973 | 0.83533
267 | -0.14517 | -0.036623 | 0.14522 | 0.036653 | 4.655e-05 | 2.9507e-05 | 0.22125 | 0.22125 | 0.22125 | 0.97673 | -0.44609 | 0.97707 | -0.43939 | 20.2608
268 | 0.016864 | 0.004227 | -0.016863 | -0.004226 | 1.6569e-06 | 9.7828e-07 | 0.025817 | 0.025817 | 0.025817 | 0.97201 | -0.53885 | 0.97191 | -0.54091 | 7.0927
269 | 0.0040864 | 0.0010239 | -0.0040862 | -0.001024 | 2.643e-07 | -6.13e-08 | 0.006206 | 0.0062061 | 0.0062061 | 0.97979 | -0.38672 | 0.97972 | -0.38808 | 1.705
270 | 0.0021247 | 0.00053239 | -0.0021247 | -0.0005325 | 4.2896e-08 | -1.1086e-07 | 0.0032271 | 0.0032271 | 0.0032271 | 0.97972 | -0.38808 | 0.9797 | -0.3885 | 0.88657
271 | -0.00961 | -0.0024082 | 0.0096113 | 0.0024088 | 1.3783e-06 | 6.7179e-07 | 0.014715 | 0.014715 | 0.014715 | 0.97176 | -0.54392 | 0.97191 | -0.54091 | 4.0427
272 | 0.0072515 | 0.0018172 | -0.0072498 | -0.0018165 | 1.7074e-06 | 6.3508e-07 | 0.011102 | 0.011102 | 0.011102 | 0.97191 | -0.54091 | 0.97166 | -0.54586 | 3.0501
273 | 0.0058211 | 0.0014585 | -0.0058209 | -0.0014584 | 1.9265e-07 | 4.3223e-08 | 0.0089143 | 0.0089144 | 0.0089144 | 0.97166 | -0.54586 | 0.97162 | -0.54655 | 2.449
274 | 0.0043914 | 0.0011001 | -0.0043914 | -0.0011001 | 7.1568e-09 | -6.4607e-10 | 0.0067251 | 0.0067251 | 0.0067251 | 0.97162 | -0.54655 | 0.97162 | -0.54659 | 1.8476
275 | -0.011493 | -0.0028795 | 0.011496 | 0.002881 | 2.8612e-06 | 1.5245e-06 | 0.017578 | 0.017578 | 0.017578 | 0.97288 | -0.52311 | 0.97315 | -0.51788 | 4.8292
276 | -0.013975 | -0.0035025 | 0.013977 | 0.0035035 | 1.7874e-06 | 1.0143e-06 | 0.021369 | 0.021369 | 0.021369 | 0.97315 | -0.51788 | 0.97328 | -0.5152 | 5.8707
277 | 0.0029697 | 0.00074384 | -0.0029696 | -0.00074391 | 7.6815e-08 | -7.3496e-08 | 0.0045478 | 0.0045479 | 0.0045479 | 0.97162 | -0.54659 | 0.97159 | -0.54713 | 1.2494
278 | 0.001519 | 0.00038035 | -0.0015189 | -0.00038067 | 5.9847e-08 | -3.2691e-07 | 0.0023262 | 0.0023263 | 0.0023263 | 0.97159 | -0.54713 | 0.97155 | -0.54796 | 0.6391
279 | 0.0051293 | 0.0012855 | -0.0051292 | -0.0012855 | 4.1011e-08 | 2.9445e-09 | 0.0077388 | 0.0077388 | 0.0077388 | 0.98625 | -0.26122 | 0.98625 | -0.26139 | 2.1261
280 | 0.003664 | 0.00091824 | -0.0036639 | -0.00091827 | 6.4032e-08 | -3.0319e-08 | 0.0055281 | 0.0055281 | 0.0055281 | 0.98625 | -0.26139 | 0.98623 | -0.26176 | 1.5187

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.59167 | 0.15228

## res_load
| p_mw | q_mvar
0 | 0.0030179 | 0.00075636
1 | 0.0044412 | 0.0011131
2 | 0.0061312 | 0.0015366
3 | 0.0039908 | 0.0010002
4 | 0.0042626 | 0.0010683
5 | 0.0046044 | 0.001154
6 | 0.005922 | 0.0014842
7 | 0.0020457 | 0.00051271
8 | 0.0013952 | 0.00034966
9 | 0.0023634 | 0.00059233
10 | 0.006612 | 0.0016571
11 | 0.0016425 | 0.00041164
12 | 0.0026202 | 0.00065667
13 | 0.0080142 | 0.0020085
14 | 0.0015868 | 0.00039768
15 | 0.003428 | 0.00085915
16 | 0.0064371 | 0.0016133
17 | 0.011497 | 0.0028813
18 | 0.0022238 | 0.00055733
19 | 0.0013549 | 0.00033956
20 | 0.0025889 | 0.00064883
21 | 0.001909 | 0.00047844
22 | 0.0021132 | 0.00052962
23 | 0.0016881 | 0.00042307
24 | 0.0029547 | 0.00074051
25 | 0.0013344 | 0.00033442
26 | 0.0026973 | 0.000676
27 | 0.0013153 | 0.00032965
28 | 0.0015098 | 0.00037839
29 | 0.0013302 | 0.00033338
30 | 0.0014451 | 0.00036217
31 | 0.0014467 | 0.00036259
32 | 0.0014149 | 0.0003546
33 | 0.0014197 | 0.0003558
34 | 0.0014501 | 0.00036343
35 | 0.0014434 | 0.00036174
36 | 0.0012913 | 0.00032364
37 | 0.0017675 | 0.00044297
38 | 0.00092704 | 0.00023234
39 | 0.00081123 | 0.00020331
40 | 0.0024994 | 0.0006264
41 | 0.0011966 | 0.0002999
42 | 0.0084457 | 0.0021167
43 | 0.0019185 | 0.00048082
44 | 0.002631 | 0.0006594
45 | 0.00042096 | 0.0001055
46 | 0.0026489 | 0.00066387
47 | 0.0016699 | 0.00041853
48 | 0.0011172 | 0.00028001
49 | 0.0026219 | 0.00065711
50 | 0.0023555 | 0.00059035
51 | 0.0014512 | 0.00036369
52 | 0.0013544 | 0.00033944
53 | 0.00049916 | 0.0001251
54 | 0.0023298 | 0.0005839
55 | 0.0019075 | 0.00047806
56 | 0.0020643 | 0.00051735
57 | 0.00088805 | 0.00022257
58 | 0.00067953 | 0.00017031
59 | 0.001648 | 0.00041302
60 | 0.001123 | 0.00028146
61 | 0.0036025 | 0.00090287
62 | 0.001107 | 0.00027745
63 | 0.0015847 | 0.00039716
64 | 0.0018587 | 0.00046582
65 | 0.001286 | 0.0003223
66 | 0.0017616 | 0.0004415
67 | 0.0013741 | 0.00034439
68 | 0.0027721 | 0.00069476
69 | 0.0022186 | 0.00055604
70 | 0.001763 | 0.00044185
71 | 0.001743 | 0.00043683
72 | 0.0016217 | 0.00040643
73 | 0.0013958 | 0.00034982
74 | 0.0047199 | 0.0011829
75 | 0.0035148 | 0.00088089
76 | 0.0011313 | 0.00028354
77 | 0.005364 | 0.0013444
78 | 0.0014738 | 0.00036937
79 | 0.0040187 | 0.0010072
80 | 0.0042695 | 0.00107
81 | 0.0058034 | 0.0014545
82 | 0.0016005 | 0.00040112
83 | 0.0017413 | 0.00043641
84 | 0.0017233 | 0.00043191
85 | 0.0028914 | 0.00072464
86 | 0.0050236 | 0.001259
87 | 0.006154 | 0.0015424
88 | 0.0066451 | 0.0016654
89 | 0.0045151 | 0.0011316
90 | 0.0026494 | 0.000664
91 | 0.0027064 | 0.00067829
92 | 0.0029185 | 0.00073144
93 | 0.0018721 | 0.00046919
94 | 0.0018648 | 0.00046737
95 | 0.0012539 | 0.00031426
96 | 0.0012514 | 0.00031362
97 | 0.00094829 | 0.00023766
98 | 0.0039215 | 0.00098283
99 | 0.0012899 | 0.00032328
100 | 0.001554 | 0.00038946
101 | 0.0013393 | 0.00033565
102 | 0.001041 | 0.00026089
103 | 0.0035728 | 0.00089542
104 | 0.002275 | 0.00057017
105 | 0.0023382 | 0.000586
106 | 0.0017368 | 0.00043529
107 | 0.0022075 | 0.00055324
108 | 0.00090453 | 0.0002267
109 | 0.0027987 | 0.00070142
110 | 0.00089357 | 0.00022395
111 | 0.0018512 | 0.00046395
112 | 0.0022158 | 0.00055534
113 | 0.0016859 | 0.00042252
114 | 0.0029943 | 0.00075044
115 | 0.0011321 | 0.00028374
116 | 0.0024793 | 0.00062138
117 | 0.0056166 | 0.0014076
118 | 0.001226 | 0.00030727
119 | 0.0019283 | 0.00048328
120 | 0.00096758 | 0.0002425
121 | 0.0019032 | 0.00047698
122 | 0.0011405 | 0.00028585
123 | 0.00099327 | 0.00024894
124 | 0.0011937 | 0.00029917
125 | 0.0021897 | 0.00054879
126 | 0.0016151 | 0.00040479
127 | 0.0019992 | 0.00050105
128 | 0.00084141 | 0.00021088
129 | 0.0016894 | 0.00042341
130 | 0.0017324 | 0.00043417
131 | 0.0021775 | 0.00054574
132 | 0.0016437 | 0.00041196
133 | 0.002899 | 0.00072657
134 | 0.002154 | 0.00053985
135 | 0.001739 | 0.00043583
136 | 0.0049277 | 0.001235
137 | 0.0026312 | 0.00065944
138 | 0.0018571 | 0.00046543
139 | 0.0017093 | 0.0004284
140 | 0.0012624 | 0.0003164
141 | 0.001713 | 0.00042932
142 | 0.002423 | 0.00060726
143 | 0.0032215 | 0.00080738
144 | 0.0018822 | 0.00047173
145 | 0.0024377 | 0.00061094
146 | 0.0017497 | 0.00043852
147 | 0.0035532 | 0.00089051
148 | 0.003786 | 0.00094886
149 | 0.0027789 | 0.00069647
150 | 0.001606 | 0.00040249
151 | 0.0015941 | 0.00039952
152 | 0.0016432 | 0.00041183
153 | 0.0030109 | 0.00075461
154 | 0.0034108 | 0.00085482
155 | 0.0040909 | 0.0010253
156 | 0.0015854 | 0.00039733
157 | 0.0027101 | 0.00067921
158 | 0.0017365 | 0.00043522
159 | 0.0019215 | 0.00048158
160 | 0.0022063 | 0.00055295
161 | 0.0035154 | 0.00088104
162 | 0.0015114 | 0.0003788
163 | 0.0018417 | 0.00046158
164 | 0.0014971 | 0.00037521
165 | 0.0063007 | 0.0015791
166 | 0.0014133 | 0.00035422
167 | 0.001766 | 0.00044259
168 | 0.0048989 | 0.0012278
169 | 0.0012369 | 0.00031
170 | 0.0026504 | 0.00066425
171 | 0.0035676 | 0.00089414
172 | 0.0011696 | 0.00029313
173 | 0.0019683 | 0.0004933
174 | 0.0016542 | 0.00041459
175 | 0.0021695 | 0.00054372
176 | 0.002562 | 0.00064209
177 | 0.0013125 | 0.00032894
178 | 0.0033523 | 0.00084016
179 | 0.0019525 | 0.00048934
180 | 0.0024057 | 0.00060292
181 | 0.0026324 | 0.00065974
182 | 0.0026177 | 0.00065605
183 | 0.0020489 | 0.00051349
184 | 0.0021185 | 0.00053094
185 | 0.0022851 | 0.00057269
186 | 0.0023215 | 0.00058182
187 | 0.0023458 | 0.00058791
188 | 0.0015768 | 0.00039518
189 | 0.0023796 | 0.00059639
190 | 0.0010563 | 0.00026473
191 | 0.0010486 | 0.00026279
192 | 0.0029229 | 0.00073254
193 | 0.0015093 | 0.00037827
194 | 0.002549 | 0.00063883
195 | 0.0014187 | 0.00035555
196 | 0.0022846 | 0.00057258
197 | 0.0026323 | 0.00065971
198 | 0.0015245 | 0.00038206
199 | 0.0014513 | 0.00036372
200 | 0.0027198 | 0.00068165
201 | 0.0018647 | 0.00046733
202 | 0.0029892 | 0.00074917
203 | 0.0023229 | 0.00058217
204 | 0.0017342 | 0.00043463
205 | 0.0025009 | 0.00062679
206 | 0.0013837 | 0.00034678
207 | 0.0021729 | 0.00054459
208 | 0.003667 | 0.00091905
209 | 0.0013151 | 0.00032959
210 | 0.0010468 | 0.00026236
211 | 0.0010754 | 0.00026953
212 | 0.0010586 | 0.00026532
213 | 0.0024256 | 0.00060792
214 | 0.00143 | 0.0003584
215 | 0.0019489 | 0.00048843
216 | 0.01185 | 0.0029699
217 | 0.0068789 | 0.001724
218 | 0.0014439 | 0.00036188
219 | 0.0016072 | 0.00040281
220 | 0.005788 | 0.0014506
221 | 0.0016043 | 0.00040207
222 | 0.0019871 | 0.00049803
223 | 0.0016675 | 0.00041792
224 | 0.0017934 | 0.00044948
225 | 0.0019614 | 0.00049158
226 | 0.0021247 | 0.0005325
227 | 0.002954 | 0.00074035
228 | 0.0014287 | 0.00035807
229 | 0.0014295 | 0.00035827
230 | 0.0024536 | 0.00061493
231 | 0.0024795 | 0.00062143
232 | 0.0014217 | 0.00035631
233 | 0.0014506 | 0.00036356
234 | 0.0015189 | 0.00038067
235 | 0.0058868 | 0.0014754
236 | 0.0010742 | 0.00026922
237 | 0.0014653 | 0.00036723
238 | 0.0036639 | 0.00091827

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1