## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2619-2_1_4_node_10 | 0.4 | n |  | TRUE
1 | bus_LV_2619-2_1_4_node_11 | 0.4 | n |  | TRUE
2 | bus_LV_2619-2_1_4_node_12 | 0.4 | n |  | TRUE
3 | bus_LV_2619-2_1_4_node_13 | 0.4 | n |  | TRUE
4 | bus_LV_2619-2_1_4_node_14 | 0.4 | n |  | TRUE
5 | bus_LV_2619-2_1_4_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_2619-2_1_4_node_100 | 0.4 | n |  | TRUE
7 | bus_LV_2619-2_1_4_node_136 | 0.4 | n |  | TRUE
8 | bus_LV_2619-2_1_4_node_97 | 0.4 | n |  | TRUE
9 | bus_LV_2619-2_1_4_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_2619-2_1_4_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_2619-2_1_4_node_23 | 0.4 | n |  | TRUE
12 | bus_LV_2619-2_1_4_node_101 | 0.4 | n |  | TRUE
13 | bus_LV_2619-2_1_4_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_2619-2_1_4_node_102 | 0.4 | n |  | TRUE
15 | bus_LV_2619-2_1_4_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_2619-2_1_4_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_2619-2_1_4_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_2619-2_1_4_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_2619-2_1_4_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_2619-2_1_4_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_2619-2_1_4_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_2619-2_1_4_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_2619-2_1_4_node_52 | 0.4 | n |  | TRUE
24 | bus_LV_2619-2_1_4_node_53 | 0.4 | n |  | TRUE
25 | bus_LV_2619-2_1_4_node_55 | 0.4 | n |  | TRUE
26 | bus_LV_2619-2_1_4_node_62 | 0.4 | n |  | TRUE
27 | bus_LV_2619-2_1_4_node_63 | 0.4 | n |  | TRUE
28 | bus_LV_2619-2_1_4_node_56 | 0.4 | n |  | TRUE
29 | bus_LV_2619-2_1_4_node_140 | 0.4 | n |  | TRUE
30 | bus_LV_2619-2_1_4_node_126 | 0.4 | n |  | TRUE
31 | bus_LV_2619-2_1_4_node_221 | 0.4 | n |  | TRUE
32 | bus_LV_2619-2_1_4_node_130 | 0.4 | n |  | TRUE
33 | bus_LV_2619-2_1_4_node_57 | 0.4 | n |  | TRUE
34 | bus_LV_2619-2_1_4_node_58 | 0.4 | n |  | TRUE
35 | bus_LV_2619-2_1_4_node_59 | 0.4 | n |  | TRUE
36 | bus_LV_2619-2_1_4_node_60 | 0.4 | n |  | TRUE
37 | bus_LV_2619-2_1_4_node_61 | 0.4 | n |  | TRUE
38 | bus_LV_2619-2_1_4_node_194 | 0.4 | n |  | TRUE
39 | bus_LV_2619-2_1_4_node_115 | 0.4 | n |  | TRUE
40 | bus_LV_2619-2_1_4_node_108 | 0.4 | n |  | TRUE
41 | bus_LV_2619-2_1_4_node_200 | 0.4 | n |  | TRUE
42 | bus_LV_2619-2_1_4_node_193 | 0.4 | n |  | TRUE
43 | bus_LV_2619-2_1_4_node_114 | 0.4 | n |  | TRUE
44 | bus_LV_2619-2_1_4_node_107 | 0.4 | n |  | TRUE
45 | bus_LV_2619-2_1_4_node_125 | 0.4 | n |  | TRUE
46 | bus_LV_2619-2_1_4_node_69 | 0.4 | n |  | TRUE
47 | bus_LV_2619-2_1_4_node_70 | 0.4 | n |  | TRUE
48 | bus_LV_2619-2_1_4_node_71 | 0.4 | n |  | TRUE
49 | bus_LV_2619-2_1_4_node_72 | 0.4 | n |  | TRUE
50 | bus_LV_2619-2_1_4_node_73 | 0.4 | n |  | TRUE
51 | bus_LV_2619-2_1_4_node_74 | 0.4 | n |  | TRUE
52 | bus_LV_2619-2_1_4_node_120 | 0.4 | n |  | TRUE
53 | bus_LV_2619-2_1_4_node_118 | 0.4 | n |  | TRUE
54 | bus_LV_2619-2_1_4_node_160 | 0.4 | n |  | TRUE
55 | bus_LV_2619-2_1_4_node_159 | 0.4 | n |  | TRUE
56 | bus_LV_2619-2_1_4_node_217 | 0.4 | n |  | TRUE
57 | bus_LV_2619-2_1_4_node_119 | 0.4 | n |  | TRUE
58 | bus_LV_2619-2_1_4_node_197 | 0.4 | n |  | TRUE
59 | bus_LV_2619-2_1_4_node_128 | 0.4 | n |  | TRUE
60 | bus_LV_2619-2_1_4_node_75 | 0.4 | n |  | TRUE
61 | bus_LV_2619-2_1_4_node_76 | 0.4 | n |  | TRUE
62 | bus_LV_2619-2_1_4_node_77 | 0.4 | n |  | TRUE
63 | bus_LV_2619-2_1_4_node_78 | 0.4 | n |  | TRUE
64 | bus_LV_2619-2_1_4_node_79 | 0.4 | n |  | TRUE
65 | bus_LV_2619-2_1_4_node_153 | 0.4 | n |  | TRUE
66 | bus_LV_2619-2_1_4_node_124 | 0.4 | n |  | TRUE
67 | bus_LV_2619-2_1_4_node_109 | 0.4 | n |  | TRUE
68 | bus_LV_2619-2_1_4_node_169 | 0.4 | n |  | TRUE
69 | bus_LV_2619-2_1_4_node_208 | 0.4 | n |  | TRUE
70 | bus_LV_2619-2_1_4_node_123 | 0.4 | n |  | TRUE
71 | bus_LV_2619-2_1_4_node_110 | 0.4 | n |  | TRUE
72 | bus_LV_2619-2_1_4_node_168 | 0.4 | n |  | TRUE
73 | bus_LV_2619-2_1_4_node_82 | 0.4 | n |  | TRUE
74 | bus_LV_2619-2_1_4_node_83 | 0.4 | n |  | TRUE
75 | bus_LV_2619-2_1_4_node_84 | 0.4 | n |  | TRUE
76 | bus_LV_2619-2_1_4_node_85 | 0.4 | n |  | TRUE
77 | bus_LV_2619-2_1_4_node_86 | 0.4 | n |  | TRUE
78 | bus_LV_2619-2_1_4_node_87 | 0.4 | n |  | TRUE
79 | bus_LV_2619-2_1_4_node_88 | 0.4 | n |  | TRUE
80 | bus_LV_2619-2_1_4_node_158 | 0.4 | n |  | TRUE
81 | bus_LV_2619-2_1_4_node_111 | 0.4 | n |  | TRUE
82 | bus_LV_2619-2_1_4_node_183 | 0.4 | n |  | TRUE
83 | bus_LV_2619-2_1_4_node_182 | 0.4 | n |  | TRUE
84 | bus_LV_2619-2_1_4_node_155 | 0.4 | n |  | TRUE
85 | bus_LV_2619-2_1_4_node_112 | 0.4 | n |  | TRUE
86 | bus_LV_2619-2_1_4_node_187 | 0.4 | n |  | TRUE
87 | bus_LV_2619-2_1_4_node_181 | 0.4 | n |  | TRUE
88 | bus_LV_2619-2_1_4_node_95 | 0.4 | n |  | TRUE
89 | bus_LV_2619-2_1_4_node_96 | 0.4 | n |  | TRUE
90 | bus_LV_2619-2_1_4_node_98 | 0.4 | n |  | TRUE
91 | bus_LV_2619-2_1_4_node_99 | 0.4 | n |  | TRUE
92 | bus_LV_2619-2_1_4_node_148 | 0.4 | n |  | TRUE
93 | bus_LV_2619-2_1_4_node_149 | 0.4 | n |  | TRUE
94 | bus_LV_2619-2_1_4_node_186 | 0.4 | n |  | TRUE
95 | bus_LV_2619-2_1_4_node_172 | 0.4 | n |  | TRUE
96 | bus_LV_2619-2_1_4_node_185 | 0.4 | n |  | TRUE
97 | bus_LV_2619-2_1_4_node_171 | 0.4 | n |  | TRUE
98 | bus_LV_2619-2_1_4_node_113 | 0.4 | n |  | TRUE
99 | bus_LV_2619-2_1_4_node_121 | 0.4 | n |  | TRUE
100 | bus_LV_2619-2_1_4_node_122 | 0.4 | n |  | TRUE
101 | bus_LV_2619-2_1_4_node_190 | 0.4 | n |  | TRUE
102 | bus_LV_2619-2_1_4_node_156 | 0.4 | n |  | TRUE
103 | bus_LV_2619-2_1_4_node_188 | 0.4 | n |  | TRUE
104 | bus_LV_2619-2_1_4_node_150 | 0.4 | n |  | TRUE
105 | bus_LV_2619-2_1_4_node_216 | 0.4 | n |  | TRUE
106 | bus_LV_2619-2_1_4_node_202 | 0.4 | n |  | TRUE
107 | bus_LV_2619-2_1_4_node_164 | 0.4 | n |  | TRUE
108 | bus_LV_2619-2_1_4_node_189 | 0.4 | n |  | TRUE
109 | bus_LV_2619-2_1_4_node_151 | 0.4 | n |  | TRUE
110 | bus_LV_2619-2_1_4_node_127 | 0.4 | n |  | TRUE
111 | bus_LV_2619-2_1_4_node_129 | 0.4 | n |  | TRUE
112 | bus_LV_2619-2_1_4_node_131 | 0.4 | n |  | TRUE
113 | bus_LV_2619-2_1_4_node_132 | 0.4 | n |  | TRUE
114 | bus_LV_2619-2_1_4_node_133 | 0.4 | n |  | TRUE
115 | bus_LV_2619-2_1_4_node_134 | 0.4 | n |  | TRUE
116 | bus_LV_2619-2_1_4_node_135 | 0.4 | n |  | TRUE
117 | bus_LV_2619-2_1_4_node_161 | 0.4 | n |  | TRUE
118 | bus_LV_2619-2_1_4_node_137 | 0.4 | n |  | TRUE
119 | bus_LV_2619-2_1_4_node_138 | 0.4 | n |  | TRUE
120 | bus_LV_2619-2_1_4_node_139 | 0.4 | n |  | TRUE
121 | bus_LV_2619-2_1_4_node_152 | 0.4 | n |  | TRUE
122 | bus_LV_2619-2_1_4_node_203 | 0.4 | n |  | TRUE
123 | bus_LV_2619-2_1_4_node_207 | 0.4 | n |  | TRUE
124 | bus_LV_2619-2_1_4_node_154 | 0.4 | n |  | TRUE
125 | bus_LV_2619-2_1_4_node_157 | 0.4 | n |  | TRUE
126 | bus_LV_2619-2_1_4_node_167 | 0.4 | n |  | TRUE
127 | bus_LV_2619-2_1_4_node_165 | 0.4 | n |  | TRUE
128 | bus_LV_2619-2_1_4_node_180 | 0.4 | n |  | TRUE
129 | bus_LV_2619-2_1_4_node_210 | 0.4 | n |  | TRUE
130 | bus_LV_2619-2_1_4_node_211 | 0.4 | n |  | TRUE
131 | bus_LV_2619-2_1_4_node_173 | 0.4 | n |  | TRUE
132 | bus_LV_2619-2_1_4_node_174 | 0.4 | n |  | TRUE
133 | bus_LV_2619-2_1_4_node_175 | 0.4 | n |  | TRUE
134 | bus_LV_2619-2_1_4_node_195 | 0.4 | n |  | TRUE
135 | bus_LV_2619-2_1_4_node_196 | 0.4 | n |  | TRUE
136 | bus_LV_2619-2_1_4_node_176 | 0.4 | n |  | TRUE
137 | bus_LV_2619-2_1_4_node_177 | 0.4 | n |  | TRUE
138 | bus_LV_2619-2_1_4_node_178 | 0.4 | n |  | TRUE
139 | bus_LV_2619-2_1_4_node_179 | 0.4 | n |  | TRUE
140 | bus_LV_2619-2_1_4_node_232 | 0.4 | n |  | TRUE
141 | bus_LV_2619-2_1_4_node_213 | 0.4 | n |  | TRUE
142 | bus_LV_2619-2_1_4_node_218 | 0.4 | n |  | TRUE
143 | bus_LV_2619-2_1_4_node_212 | 0.4 | n |  | TRUE
144 | bus_LV_2619-2_1_4_node_222 | 0.4 | n |  | TRUE
145 | bus_LV_2619-2_1_4_node_191 | 0.4 | n |  | TRUE
146 | bus_LV_2619-2_1_4_node_192 | 0.4 | n |  | TRUE
147 | bus_LV_2619-2_1_4_node_198 | 0.4 | n |  | TRUE
148 | bus_LV_2619-2_1_4_node_199 | 0.4 | n |  | TRUE
149 | bus_MV_293_0_node_129 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2619-2_1_4_load_10 | 0 | 0.00048775 | 0.00012224 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2619-2_1_4_load_11 | 1 | 0.00032659 | 8.1852e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2619-2_1_4_load_13 | 3 | 0.00040846 | 0.00010237 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2619-2_1_4_load_14 | 4 | 0.00061273 | 0.00015357 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2619-2_1_4_load_100 | 6 | 0.00049251 | 0.00012344 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2619-2_1_4_load_136 | 7 | 0.0013231 | 0.00033161 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2619-2_1_4_load_17 | 9 | 0.0002396 | 6.0049e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2619-2_1_4_load_35 | 10 | 0.00021548 | 5.4005e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2619-2_1_4_load_23 | 11 | 0.00059254 | 0.0001485 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2619-2_1_4_load_102 | 14 | 0.00010124 | 2.5372e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2619-2_1_4_load_18 | 15 | 0.00064924 | 0.00016271 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2619-2_1_4_load_19 | 16 | 0.00014272 | 3.5769e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2619-2_1_4_load_21 | 17 | 0.0012681 | 0.00031781 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2619-2_1_4_load_22 | 18 | 0.00016462 | 4.1258e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2619-2_1_4_load_24 | 20 | 0.00016168 | 4.0522e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2619-2_1_4_load_26 | 21 | 0.00041217 | 0.0001033 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2619-2_1_4_load_25 | 22 | 0.00036096 | 9.0466e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2619-2_1_4_load_52 | 23 | 0.0038058 | 0.00095383 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2619-2_1_4_load_53 | 24 | 0.001647 | 0.00041279 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2619-2_1_4_load_62 | 26 | 0.0018396 | 0.00046103 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2619-2_1_4_load_63 | 27 | 0.0021653 | 0.00054268 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2619-2_1_4_load_126 | 30 | 0.0019314 | 0.00048405 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2619-2_1_4_load_221 | 31 | 0.0015477 | 0.00038789 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2619-2_1_4_load_57 | 33 | 0.0013434 | 0.00033668 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2619-2_1_4_load_58 | 34 | 0.002332 | 0.00058445 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2619-2_1_4_load_59 | 35 | 0.0021219 | 0.00053181 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2619-2_1_4_load_61 | 37 | 0.0013526 | 0.00033898 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2619-2_1_4_load_108 | 40 | 0.0014898 | 0.00037337 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2619-2_1_4_load_193 | 42 | 0.0010264 | 0.00025725 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2619-2_1_4_load_114 | 43 | 0.0010262 | 0.0002572 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2619-2_1_4_load_107 | 44 | 0.00090219 | 0.00022611 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2619-2_1_4_load_125 | 45 | 0.002366 | 0.00059296 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2619-2_1_4_load_69 | 46 | 0.00031457 | 7.8838e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2619-2_1_4_load_70 | 47 | 0.00069181 | 0.00017339 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2619-2_1_4_load_72 | 49 | 0.00033248 | 8.3327e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2619-2_1_4_load_118 | 53 | 0.0034766 | 0.00087133 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2619-2_1_4_load_160 | 54 | 0.0004851 | 0.00012158 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2619-2_1_4_load_159 | 55 | 0.00052359 | 0.00013123 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2619-2_1_4_load_217 | 56 | 0.00088873 | 0.00022274 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2619-2_1_4_load_197 | 58 | 0.00020793 | 5.2112e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2619-2_1_4_load_128 | 59 | 0.0013486 | 0.000338 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2619-2_1_4_load_75 | 60 | 0.00041008 | 0.00010278 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2619-2_1_4_load_76 | 61 | 0.00051663 | 0.00012948 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2619-2_1_4_load_153 | 65 | 0.044759 | 0.011218 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2619-2_1_4_load_124 | 66 | 0.00069033 | 0.00017301 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2619-2_1_4_load_169 | 68 | 0.001372 | 0.00034386 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2619-2_1_4_load_208 | 69 | 0.00080059 | 0.00020065 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2619-2_1_4_load_123 | 70 | 0.0015415 | 0.00038635 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2619-2_1_4_load_168 | 72 | 0.0011261 | 0.00028222 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2619-2_1_4_load_82 | 73 | 0.0023397 | 0.0005864 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2619-2_1_4_load_85 | 76 | 0.0011098 | 0.00027814 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2619-2_1_4_load_86 | 77 | 0.0011026 | 0.00027633 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2619-2_1_4_load_87 | 78 | 0.001143 | 0.00028647 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2619-2_1_4_load_88 | 79 | 0.00096523 | 0.00024191 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2619-2_1_4_load_111 | 81 | 0.00054146 | 0.0001357 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2619-2_1_4_load_182 | 83 | 0.0014101 | 0.00035341 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2619-2_1_4_load_112 | 85 | 0.00083501 | 0.00020927 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2619-2_1_4_load_187 | 86 | 0.00088408 | 0.00022157 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2619-2_1_4_load_181 | 87 | 0.00093002 | 0.00023309 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2619-2_1_4_load_95 | 88 | 0.00080935 | 0.00020284 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2619-2_1_4_load_96 | 89 | 0.001401 | 0.00035112 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2619-2_1_4_load_98 | 90 | 0.0011859 | 0.00029721 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2619-2_1_4_load_99 | 91 | 0.0015424 | 0.00038656 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2619-2_1_4_load_148 | 92 | 0.00095784 | 0.00024006 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2619-2_1_4_load_149 | 93 | 0.0026914 | 0.00067453 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2619-2_1_4_load_186 | 94 | 0.0020174 | 0.00050561 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2619-2_1_4_load_172 | 95 | 0.0014981 | 0.00037546 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2619-2_1_4_load_185 | 96 | 0.0013835 | 0.00034674 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2619-2_1_4_load_171 | 97 | 0.0013213 | 0.00033116 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2619-2_1_4_load_113 | 98 | 0.001128 | 0.00028272 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2619-2_1_4_load_122 | 100 | 0.00096656 | 0.00024224 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2619-2_1_4_load_190 | 101 | 0.0017656 | 0.0004425 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2619-2_1_4_load_188 | 103 | 0.0021347 | 0.00053502 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2619-2_1_4_load_150 | 104 | 0.012339 | 0.0030926 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2619-2_1_4_load_216 | 105 | 0.0014756 | 0.00036982 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2619-2_1_4_load_202 | 106 | 0.0022745 | 0.00057004 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2619-2_1_4_load_164 | 107 | 0.0020629 | 0.00051701 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2619-2_1_4_load_189 | 108 | 0.001479 | 0.00037067 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2619-2_1_4_load_151 | 109 | 0.019834 | 0.0049708 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2619-2_1_4_load_127 | 110 | 0.00044037 | 0.00011037 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2619-2_1_4_load_129 | 111 | 0.0015912 | 0.00039878 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2619-2_1_4_load_131 | 112 | 0.0012929 | 0.00032403 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2619-2_1_4_load_132 | 113 | 0.001455 | 0.00036466 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2619-2_1_4_load_133 | 114 | 0.0016955 | 0.00042492 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2619-2_1_4_load_134 | 115 | 0.0014151 | 0.00035466 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2619-2_1_4_load_135 | 116 | 0.0016432 | 0.00041184 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2619-2_1_4_load_161 | 117 | 0.0016555 | 0.0004149 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2619-2_1_4_load_137 | 118 | 0.00034946 | 8.7582e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2619-2_1_4_load_138 | 119 | 0.00038307 | 9.6005e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2619-2_1_4_load_139 | 120 | 0.00041889 | 0.00010498 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2619-2_1_4_load_152 | 121 | 0.0077187 | 0.0019345 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2619-2_1_4_load_203 | 122 | 0.003749 | 0.00093959 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2619-2_1_4_load_207 | 123 | 0.070762 | 0.017735 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2619-2_1_4_load_154 | 124 | 0.0011656 | 0.00029213 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2619-2_1_4_load_157 | 125 | 0.001584 | 0.00039698 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2619-2_1_4_load_167 | 126 | 0.0015588 | 0.00039068 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2619-2_1_4_load_165 | 127 | 0.0018802 | 0.00047123 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2619-2_1_4_load_180 | 128 | 0.0015069 | 0.00037768 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2619-2_1_4_load_210 | 129 | 0.0024084 | 0.00060361 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2619-2_1_4_load_211 | 130 | 0.0014498 | 0.00036335 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2619-2_1_4_load_174 | 132 | 0.0021263 | 0.00053289 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2619-2_1_4_load_175 | 133 | 0.0010047 | 0.00025181 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2619-2_1_4_load_196 | 135 | 0.0020065 | 0.00050287 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2619-2_1_4_load_176 | 136 | 0.001598 | 0.0004005 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2619-2_1_4_load_232 | 140 | 0.0019962 | 0.00050029 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2619-2_1_4_load_218 | 142 | 0.0015417 | 0.00038639 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2619-2_1_4_load_212 | 143 | 0.0020289 | 0.00050848 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2619-2_1_4_load_222 | 144 | 0.0035259 | 0.00088368 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2619-2_1_4_load_191 | 145 | 0.0029595 | 0.00074172 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2619-2_1_4_load_192 | 146 | 0.0024813 | 0.00062186 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2619-2_1_4_load_198 | 147 | 0.0011011 | 0.00027597 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2619-2_1_4_load_199 | 148 | 0.0013067 | 0.00032748 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 122 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2619-2_1_4_line_0 |  | 0 | 1 | 0.0073907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_2619-2_1_4_line_1 |  | 0 | 2 | 0.048796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_2619-2_1_4_line_2 |  | 1 | 3 | 0.0047681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_2619-2_1_4_line_3 |  | 2 | 4 | 0.08836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2619-2_1_4_line_4 |  | 2 | 5 | 0.090085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2619-2_1_4_line_5 |  | 3 | 9 | 0.063384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2619-2_1_4_line_6 |  | 4 | 10 | 0.055173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2619-2_1_4_line_7 |  | 5 | 11 | 0.11372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2619-2_1_4_line_8 |  | 6 | 7 | 0.38623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_2619-2_1_4_line_9 |  | 6 | 8 | 0.07913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_2619-2_1_4_line_10 |  | 7 | 14 | 0.031377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2619-2_1_4_line_11 |  | 8 | 91 | 0.13445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2619-2_1_4_line_12 |  | 8 | 88 | 0.0238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_2619-2_1_4_line_13 |  | 9 | 12 | 0.0099703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_2619-2_1_4_line_14 |  | 11 | 13 | 0.019384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2619-2_1_4_line_15 |  | 12 | 14 | 0.011078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2619-2_1_4_line_16 |  | 13 | 18 | 0.035228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2619-2_1_4_line_17 |  | 13 | 15 | 0.00282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2619-2_1_4_line_18 |  | 15 | 16 | 0.015285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2619-2_1_4_line_19 |  | 16 | 17 | 0.040679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2619-2_1_4_line_20 |  | 17 | 19 | 0.047662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2619-2_1_4_line_21 |  | 18 | 20 | 0.0065085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2619-2_1_4_line_22 |  | 19 | 21 | 0.086723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2619-2_1_4_line_23 |  | 20 | 22 | 0.016258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2619-2_1_4_line_24 |  | 23 | 24 | 0.026742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2619-2_1_4_line_25 |  | 24 | 25 | 0.037681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2619-2_1_4_line_26 |  | 25 | 26 | 0.013334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2619-2_1_4_line_27 |  | 25 | 27 | 0.020254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2619-2_1_4_line_28 |  | 26 | 30 | 0.020006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2619-2_1_4_line_29 |  | 27 | 28 | 0.068006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2619-2_1_4_line_30 |  | 28 | 29 | 0.032131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2619-2_1_4_line_31 |  | 29 | 31 | 0.061378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2619-2_1_4_line_32 |  | 29 | 32 | 0.02824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2619-2_1_4_line_33 |  | 30 | 45 | 0.0055163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2619-2_1_4_line_34 |  | 32 | 59 | 0.077623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2619-2_1_4_line_35 |  | 32 | 51 | 0.18193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2619-2_1_4_line_36 |  | 33 | 34 | 0.039333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2619-2_1_4_line_37 |  | 33 | 35 | 0.014599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2619-2_1_4_line_38 |  | 34 | 36 | 0.009294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2619-2_1_4_line_39 |  | 35 | 37 | 0.025242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2619-2_1_4_line_40 |  | 36 | 38 | 0.026024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2619-2_1_4_line_41 |  | 36 | 39 | 0.006458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2619-2_1_4_line_42 |  | 37 | 40 | 0.025851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2619-2_1_4_line_43 |  | 38 | 41 | 0.004358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2619-2_1_4_line_44 |  | 38 | 42 | 0.010366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2619-2_1_4_line_45 |  | 39 | 43 | 0.021058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2619-2_1_4_line_46 |  | 40 | 44 | 0.021752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2619-2_1_4_line_47 |  | 41 | 147 | 0.014903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2619-2_1_4_line_48 |  | 42 | 145 | 0.019152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2619-2_1_4_line_49 |  | 44 | 67 | 0.019628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2619-2_1_4_line_50 |  | 46 | 47 | 0.041285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2619-2_1_4_line_51 |  | 46 | 48 | 0.023369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2619-2_1_4_line_52 |  | 47 | 49 | 0.0071643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2619-2_1_4_line_53 |  | 48 | 50 | 0.007059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2619-2_1_4_line_54 |  | 48 | 51 | 0.16453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2619-2_1_4_line_55 |  | 50 | 52 | 0.006144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2619-2_1_4_line_56 |  | 50 | 53 | 0.0678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2619-2_1_4_line_57 |  | 51 | 54 | 0.027588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2619-2_1_4_line_58 |  | 51 | 55 | 0.018609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2619-2_1_4_line_59 |  | 52 | 56 | 0.018305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2619-2_1_4_line_60 |  | 53 | 57 | 0.0028063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2619-2_1_4_line_61 |  | 54 | 58 | 0.01297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2619-2_1_4_line_62 |  | 56 | 105 | 0.025584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2619-2_1_4_line_63 |  | 57 | 99 | 0.037974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_2619-2_1_4_line_64 |  | 57 | 100 | 0.033203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_2619-2_1_4_line_65 |  | 58 | 120 | 0.0090153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2619-2_1_4_line_66 |  | 59 | 110 | 0.0085015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2619-2_1_4_line_67 |  | 60 | 61 | 0.023383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_2619-2_1_4_line_68 |  | 60 | 62 | 0.044861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_2619-2_1_4_line_69 |  | 61 | 63 | 0.016327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_2619-2_1_4_line_70 |  | 62 | 64 | 0.039394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_2619-2_1_4_line_71 |  | 63 | 65 | 0.058226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_2619-2_1_4_line_72 |  | 63 | 66 | 0.012764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_2619-2_1_4_line_73 |  | 64 | 67 | 0.041549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_2619-2_1_4_line_74 |  | 64 | 68 | 0.021599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2619-2_1_4_line_75 |  | 65 | 69 | 0.0013365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2619-2_1_4_line_76 |  | 66 | 70 | 0.066019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_2619-2_1_4_line_77 |  | 67 | 71 | 0.030534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_2619-2_1_4_line_78 |  | 68 | 72 | 0.0039003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2619-2_1_4_line_79 |  | 69 | 123 | 0.048445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2619-2_1_4_line_80 |  | 70 | 76 | 0.038405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_2619-2_1_4_line_81 |  | 71 | 94 | 0.016971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_2619-2_1_4_line_82 |  | 71 | 95 | 0.027884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2619-2_1_4_line_83 |  | 73 | 74 | 0.0070566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2619-2_1_4_line_84 |  | 73 | 75 | 0.032109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2619-2_1_4_line_85 |  | 74 | 76 | 0.01328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_2619-2_1_4_line_86 |  | 74 | 77 | 0.063601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_2619-2_1_4_line_87 |  | 75 | 78 | 0.019432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2619-2_1_4_line_88 |  | 75 | 79 | 0.026789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2619-2_1_4_line_89 |  | 77 | 80 | 0.050537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_2619-2_1_4_line_90 |  | 78 | 81 | 0.013375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2619-2_1_4_line_91 |  | 79 | 82 | 0.055867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2619-2_1_4_line_92 |  | 80 | 83 | 0.012236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2619-2_1_4_line_93 |  | 80 | 84 | 0.019381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_2619-2_1_4_line_94 |  | 81 | 85 | 0.021211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2619-2_1_4_line_95 |  | 82 | 86 | 0.008997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2619-2_1_4_line_96 |  | 82 | 87 | 0.010935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2619-2_1_4_line_97 |  | 83 | 128 | 0.013455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2619-2_1_4_line_98 |  | 84 | 125 | 0.015731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2619-2_1_4_line_99 |  | 84 | 102 | 0.027249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_2619-2_1_4_line_100 |  | 84 | 124 | 0.02657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2619-2_1_4_line_101 |  | 85 | 98 | 0.0030874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2619-2_1_4_line_102 |  | 88 | 89 | 0.12292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_2619-2_1_4_line_103 |  | 89 | 90 | 0.00034876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_2619-2_1_4_line_104 |  | 90 | 92 | 0.033189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_2619-2_1_4_line_105 |  | 92 | 93 | 0.028286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_2619-2_1_4_line_106 |  | 93 | 117 | 0.0075507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_2619-2_1_4_line_107 |  | 94 | 96 | 0.024331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_2619-2_1_4_line_108 |  | 95 | 97 | 0.026546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2619-2_1_4_line_109 |  | 96 | 116 | 0.018134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_2619-2_1_4_line_110 |  | 97 | 131 | 0.012992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2619-2_1_4_line_111 |  | 99 | 101 | 0.012452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2619-2_1_4_line_112 |  | 99 | 102 | 0.022201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_2619-2_1_4_line_113 |  | 99 | 103 | 0.024301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2619-2_1_4_line_114 |  | 100 | 104 | 0.012098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_2619-2_1_4_line_115 |  | 101 | 106 | 0.028309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2619-2_1_4_line_116 |  | 102 | 107 | 0.020517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2619-2_1_4_line_117 |  | 103 | 108 | 0.031632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2619-2_1_4_line_118 |  | 104 | 109 | 0.012753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_2619-2_1_4_line_119 |  | 105 | 139 | 0.046802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2619-2_1_4_line_120 |  | 107 | 127 | 0.032646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2619-2_1_4_line_121 |  | 109 | 121 | 0.046726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_2619-2_1_4_line_122 |  | 110 | 111 | 0.026583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2619-2_1_4_line_123 |  | 112 | 113 | 0.026425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_2619-2_1_4_line_124 |  | 112 | 114 | 0.014926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_2619-2_1_4_line_125 |  | 113 | 115 | 0.013251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_2619-2_1_4_line_126 |  | 114 | 116 | 0.01068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_2619-2_1_4_line_127 |  | 115 | 117 | 0.019942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_2619-2_1_4_line_128 |  | 118 | 119 | 0.0041023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2619-2_1_4_line_129 |  | 119 | 120 | 0.015793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2619-2_1_4_line_130 |  | 121 | 122 | 0.028022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_2619-2_1_4_line_131 |  | 125 | 126 | 0.030207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2619-2_1_4_line_132 |  | 129 | 130 | 0.058078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2619-2_1_4_line_133 |  | 130 | 143 | 0.023546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2619-2_1_4_line_134 |  | 131 | 132 | 0.030481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2619-2_1_4_line_135 |  | 131 | 133 | 0.02767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2619-2_1_4_line_136 |  | 132 | 134 | 0.0091131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2619-2_1_4_line_137 |  | 134 | 135 | 0.032261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2619-2_1_4_line_138 |  | 136 | 137 | 0.061289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2619-2_1_4_line_139 |  | 137 | 138 | 0.018696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2619-2_1_4_line_140 |  | 137 | 139 | 0.041531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2619-2_1_4_line_141 |  | 138 | 140 | 0.043237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2619-2_1_4_line_142 |  | 138 | 141 | 0.028449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2619-2_1_4_line_143 |  | 139 | 142 | 0.035516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2619-2_1_4_line_144 |  | 141 | 143 | 0.035287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2619-2_1_4_line_145 |  | 142 | 144 | 0.026648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2619-2_1_4_line_146 |  | 145 | 146 | 0.026651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2619-2_1_4_line_147 |  | 147 | 148 | 0.027315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2619-2_1_4_trafo_203 | 0.63 MVA 20/0.4 kV | 149 | 122 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2598185.9755 | 1251734.8091 | 2598186.2731 | 1251736.5331 | 2598185.6512 | 1251742.1399
1 | 2598178.2205 | 1251688.2821 | 2598176.9348 | 1251703.359 | 2598177.5196 | 1251714.8107 | 2598180.2018 | 1251724.783 | 2598185.3809 | 1251731.3634 | 2598185.9755 | 1251734.8091
2 | 2598184.7491 | 1251746.8058 | 2598185.3851 | 1251744.5386 | 2598185.6512 | 1251742.1399
3 | 2598178.2205 | 1251688.2821 | 2598161.4386 | 1251694.1691 | 2598139.474 | 1251705.7393 | 2598098.8828 | 1251726.8443
4 | 2598148.3687 | 1251604.2815 | 2598156.2309 | 1251622.7688 | 2598166.5993 | 1251643.6012 | 2598174.8235 | 1251661.7548 | 2598177.5072 | 1251676.1744 | 2598178.2205 | 1251688.2821
5 | 2598184.7491 | 1251746.8058 | 2598181.6387 | 1251757.8929 | 2598178.9638 | 1251770.7133 | 2598172.583 | 1251808.9572
6 | 2598098.8828 | 1251726.8443 | 2598088.7618 | 1251732.1066 | 2598083.608 | 1251733.5537 | 2598077.8875 | 1251733.1998 | 2598073.7813 | 1251730.5328 | 2598070.5634 | 1251721.806 | 2598072.3487 | 1251712.0101 | 2598076.8065 | 1251705.2487 | 2598077.1037 | 1251704.9406
7 | 2598148.3687 | 1251604.2815 | 2598142.9026 | 1251597.5344 | 2598129.8515 | 1251566.3851 | 2598113.2246 | 1251517.0696 | 2598110.7228 | 1251505.6742 | 2598110.1172 | 1251498.149
8 | 2598392.8127 | 1252149.3176 | 2598145.5226 | 1251852.6293
9 | 2598464.1534 | 1252177.3716 | 2598458.2823 | 1252176.1057 | 2598449.9655 | 1252172.4389 | 2598431.7154 | 1252158.8907 | 2598422.1906 | 1252152.8894 | 2598411.8741 | 1252149.3122 | 2598402.7507 | 1252148.5142 | 2598392.8127 | 1252149.3176
10 | 2598145.5226 | 1251852.6293 | 2598150.3942 | 1251845.7491 | 2598158.1333 | 1251834.5504 | 2598162.5004 | 1251827.5778 | 2598163.2672 | 1251826.7797
11 | 2598464.1534 | 1252177.3716 | 2598471.8808 | 1252178.1811 | 2598482.2864 | 1252176.5773 | 2598507.0813 | 1252171.1449 | 2598519.5019 | 1252170.6858 | 2598531.7496 | 1252172.3281 | 2598541.2509 | 1252175.5166 | 2598549.9979 | 1252179.8727 | 2598560.3156 | 1252188.6091 | 2598578.3177 | 1252207.6169 | 2598583.4424 | 1252211.596
12 | 2598464.1534 | 1252177.3716 | 2598460.7984 | 1252188.0684 | 2598456.4469 | 1252199.8823
13 | 2598170.9421 | 1251818.7916 | 2598172.583 | 1251808.9572
14 | 2598118.088 | 1251480.9557 | 2598114.9648 | 1251484.6369 | 2598112.5059 | 1251488.7515 | 2598110.9449 | 1251492.6434 | 2598110.109 | 1251498.0472 | 2598110.1172 | 1251498.149
15 | 2598170.9421 | 1251818.7916 | 2598163.2672 | 1251826.7797
16 | 2598118.088 | 1251480.9557 | 2598108.3269 | 1251472.1087 | 2598099.6317 | 1251468.6872 | 2598087.0821 | 1251466.6768
17 | 2598118.088 | 1251480.9557 | 2598120.0698 | 1251478.9495
18 | 2598120.0698 | 1251478.9495 | 2598121.9885 | 1251477.0074 | 2598126.0101 | 1251474.2821 | 2598129.8056 | 1251472.3351 | 2598133.0269 | 1251471.1539
19 | 2598168.7758 | 1251452.7991 | 2598167.6099 | 1251454.0998 | 2598164.6826 | 1251456.8581 | 2598160.3818 | 1251459.9171 | 2598156.9787 | 1251461.9195 | 2598152.2928 | 1251464.0891 | 2598133.0269 | 1251471.1539
20 | 2598197.1665 | 1251415.0317 | 2598195.289 | 1251420.2134 | 2598192.634 | 1251425.1286 | 2598187.1647 | 1251432.4239 | 2598173.7208 | 1251447.2823 | 2598168.7758 | 1251452.7991
21 | 2598087.0821 | 1251466.6768 | 2598080.6555 | 1251465.6473
22 | 2598197.1665 | 1251415.0317 | 2598195.5584 | 1251413.131 | 2598193.3693 | 1251411.4973 | 2598189.8744 | 1251409.6527 | 2598179.1872 | 1251407.5992 | 2598148.9375 | 1251403.8955 | 2598122.6274 | 1251400.4018 | 2598112.9913 | 1251399.8657
23 | 2598080.6555 | 1251465.6473 | 2598072.6197 | 1251464.3601 | 2598064.5302 | 1251463.6598
24 | 2598425.6553 | 1252644.4092 | 2598412.5331 | 1252642.0224 | 2598399.1357 | 1252642.4612
25 | 2598361.9199 | 1252648.0408 | 2598393.0132 | 1252642.6617 | 2598399.1357 | 1252642.4612
26 | 2598361.9199 | 1252648.0408 | 2598359.9406 | 1252634.8547
27 | 2598361.9199 | 1252648.0408 | 2598365.1717 | 1252668.0317
28 | 2598356.9709 | 1252615.0705 | 2598359.9406 | 1252634.8547
29 | 2598377.7826 | 1252734.7151 | 2598374.5809 | 1252725.8769 | 2598365.1717 | 1252668.0317
30 | 2598377.7826 | 1252734.7151 | 2598359.3968 | 1252742.2142 | 2598348.0878 | 1252746.9872
31 | 2598348.0878 | 1252746.9872 | 2598339.18 | 1252686.2595
32 | 2598323.2677 | 1252760.559 | 2598345.4774 | 1252748.0887 | 2598348.0878 | 1252746.9872
33 | 2598356.1521 | 1252609.6153 | 2598356.9709 | 1252615.0705
34 | 2598323.2677 | 1252760.559 | 2598319.6282 | 1252751.732 | 2598308.2451 | 1252710.275 | 2598304.0674 | 1252693.1539 | 2598302.8095 | 1252685.7999
35 | 2598258.0492 | 1252721.6754 | 2598246.9374 | 1252729.6507 | 2598230.9433 | 1252736.1488 | 2598240.5297 | 1252748.6318 | 2598248.6835 | 1252764.195 | 2598254.4527 | 1252779.1919 | 2598260.4483 | 1252794.2554 | 2598262.0415 | 1252798.2465 | 2598263.8535 | 1252801.7371 | 2598268.6609 | 1252805.3602 | 2598279.0699 | 1252794.1608 | 2598290.7237 | 1252782.0939 | 2598309.5904 | 1252768.3237 | 2598323.2677 | 1252760.559
36 | 2598564.9765 | 1252500.7662 | 2598570.0611 | 1252499.8208 | 2598578.8133 | 1252496.9723 | 2598590.5299 | 1252489.6646 | 2598599.179 | 1252482.6297
37 | 2598550.4671 | 1252501.658 | 2598559.7618 | 1252501.7358 | 2598564.9765 | 1252500.7662
38 | 2598605.4367 | 1252475.7851 | 2598600.375 | 1252481.6569 | 2598599.179 | 1252482.6297
39 | 2598525.3501 | 1252499.3051 | 2598546.8663 | 1252501.6279 | 2598550.4671 | 1252501.658
40 | 2598616.3192 | 1252452.2115 | 2598610.0979 | 1252467.8899 | 2598605.4367 | 1252475.7851
41 | 2598605.4367 | 1252475.7851 | 2598611.8733 | 1252476.5062
42 | 2598525.3501 | 1252499.3051 | 2598516.6603 | 1252498.367 | 2598509.1902 | 1252498.8248 | 2598499.804 | 1252500.962
43 | 2598617.2463 | 1252447.9529 | 2598616.3192 | 1252452.2115
44 | 2598616.3192 | 1252452.2115 | 2598626.6687 | 1252451.6251
45 | 2598611.8733 | 1252476.5062 | 2598613.2323 | 1252497.52
46 | 2598482.5998 | 1252513.6277 | 2598485.7789 | 1252509.3157 | 2598491.8821 | 1252504.8 | 2598499.804 | 1252500.962 | 2598499.804 | 1252500.962
47 | 2598617.2463 | 1252447.9529 | 2598602.3692 | 1252448.8377
48 | 2598626.6687 | 1252451.6251 | 2598645.7901 | 1252450.5417
49 | 2598472.6628 | 1252530.5219 | 2598480.1218 | 1252516.9889 | 2598482.5998 | 1252513.6277
50 | 2598215.8086 | 1252609.2801 | 2598229.9901 | 1252607.0759 | 2598232.0728 | 1252607.4199 | 2598233.6733 | 1252610.4436 | 2598237.6313 | 1252631.4751
51 | 2598192.7172 | 1252612.8691 | 2598215.8086 | 1252609.2801
52 | 2598238.9563 | 1252638.5158 | 2598237.6313 | 1252631.4751
53 | 2598192.7172 | 1252612.8691 | 2598191.8397 | 1252605.8648
54 | 2598192.7172 | 1252612.8691 | 2598196.0397 | 1252644.4332 | 2598197.7447 | 1252667.5588 | 2598199.0015 | 1252680.9894 | 2598200.1282 | 1252688.7497 | 2598202.5076 | 1252696.8765 | 2598205.5654 | 1252703.0796 | 2598209.2952 | 1252710.4054 | 2598214.8436 | 1252718.6424 | 2598224.2334 | 1252729.4576 | 2598230.9433 | 1252736.1488 | 2598246.9374 | 1252729.6507 | 2598258.0492 | 1252721.6754
55 | 2598188.7669 | 1252600.5401 | 2598191.8397 | 1252605.8648
56 | 2598191.8397 | 1252605.8648 | 2598195.6094 | 1252596.3908 | 2598221.0059 | 1252544.688
57 | 2598258.0492 | 1252721.6754 | 2598255.4597 | 1252716.8175 | 2598250.9951 | 1252695.1901
58 | 2598258.0492 | 1252721.6754 | 2598272.7134 | 1252710.2191
59 | 2598188.7669 | 1252600.5401 | 2598178.1397 | 1252585.6363
60 | 2598222.2432 | 1252542.1692 | 2598221.0059 | 1252544.688
61 | 2598248.373 | 1252682.4878 | 2598250.9951 | 1252695.1901
62 | 2598160.9335 | 1252566.8355 | 2598173.0652 | 1252578.5196 | 2598178.1397 | 1252585.6363
63 | 2598222.2432 | 1252542.1692 | 2598239.1423 | 1252508.1417
64 | 2598222.2432 | 1252542.1692 | 2598255.2321 | 1252538.4047
65 | 2598246.5504 | 1252673.6587 | 2598246.5504 | 1252673.6587 | 2598248.373 | 1252682.4878
66 | 2598301.3761 | 1252677.4201 | 2598302.8095 | 1252685.7999
67 | 2598476.011 | 1252566.3344 | 2598462.8831 | 1252546.9845
68 | 2598500.7368 | 1252603.7511 | 2598496.0037 | 1252595.8028 | 2598476.011 | 1252566.3344
69 | 2598453.7166 | 1252533.4735 | 2598462.8831 | 1252546.9845
70 | 2598500.7368 | 1252603.7511 | 2598502.9769 | 1252600.4039 | 2598503.6172 | 1252596.4234 | 2598489.9674 | 1252568.1975
71 | 2598453.7166 | 1252533.4735 | 2598426.7841 | 1252552.2487 | 2598418.2212 | 1252556.9875 | 2598407.6284 | 1252561.2822 | 2598403.7026 | 1252562.711
72 | 2598453.7166 | 1252533.4735 | 2598446.5561 | 1252522.9077
73 | 2598489.9674 | 1252568.1975 | 2598484.4038 | 1252558.7817 | 2598477.3748 | 1252543.5959 | 2598472.6628 | 1252530.5219
74 | 2598489.9674 | 1252568.1975 | 2598500.206 | 1252565.3151 | 2598511.1606 | 1252564.8952
75 | 2598402.4467 | 1252563.1681 | 2598403.7026 | 1252562.711
76 | 2598446.5561 | 1252522.9077 | 2598423.4765 | 1252488.8527 | 2598409.5183 | 1252468.2565
77 | 2598461.5178 | 1252502.0842 | 2598472.6628 | 1252530.5219
78 | 2598511.1606 | 1252564.8952 | 2598515.0581 | 1252564.7458
79 | 2598355.9681 | 1252576.4538 | 2598381.2745 | 1252570.8737 | 2598402.4467 | 1252563.1681
80 | 2598409.5183 | 1252468.2565 | 2598408.4998 | 1252466.7536 | 2598389.2357 | 1252435.646
81 | 2598461.5178 | 1252502.0842 | 2598459.1919 | 1252495.5583 | 2598456.6802 | 1252485.8345
82 | 2598461.5178 | 1252502.0842 | 2598464.0753 | 1252500.4824 | 2598470.1541 | 1252489.3179 | 2598477.5209 | 1252479.6509
83 | 2598382.2438 | 1252424.3555 | 2598378.8402 | 1252418.174
84 | 2598364.1089 | 1252389.6714 | 2598368.2089 | 1252398.8651 | 2598378.8402 | 1252418.174
85 | 2598382.2438 | 1252424.3555 | 2598389.2357 | 1252435.646
86 | 2598382.2438 | 1252424.3555 | 2598372.4959 | 1252428.7279 | 2598348.0197 | 1252435.7617 | 2598326.5839 | 1252441.3495 | 2598321.3652 | 1252442.2632
87 | 2598364.1089 | 1252389.6714 | 2598359.6645 | 1252370.7544
88 | 2598364.1089 | 1252389.6714 | 2598347.3782 | 1252383.7724 | 2598338.9708 | 1252380.4274
89 | 2598271.1172 | 1252447.1476 | 2598279.2287 | 1252446.945 | 2598311.0632 | 1252444.0669 | 2598321.3652 | 1252442.2632
90 | 2598359.6645 | 1252370.7544 | 2598356.6053 | 1252357.7335
91 | 2598302.6559 | 1252338.6451 | 2598327.4081 | 1252370.2361 | 2598335.1752 | 1252378.9173 | 2598338.9708 | 1252380.4274
92 | 2598271.1172 | 1252447.1476 | 2598276.7178 | 1252436.269
93 | 2598261.894 | 1252464.206 | 2598271.1172 | 1252447.1476
94 | 2598356.6053 | 1252357.7335 | 2598356.312 | 1252356.4854 | 2598353.0322 | 1252336.8286
95 | 2598302.6559 | 1252338.6451 | 2598303.6719 | 1252329.7056
96 | 2598302.6559 | 1252338.6451 | 2598300.8397 | 1252349.4285
97 | 2598276.7178 | 1252436.269 | 2598277.844 | 1252434.0815 | 2598281.2725 | 1252423.6353
98 | 2598261.894 | 1252464.206 | 2598246.2012 | 1252465.2959
99 | 2598261.894 | 1252464.206 | 2598249.353 | 1252488.4146
100 | 2598261.894 | 1252464.206 | 2598288.4123 | 1252462.5423
101 | 2598352.524 | 1252333.7833 | 2598353.0322 | 1252336.8286
102 | 2598456.4469 | 1252199.8823 | 2598452.1646 | 1252211.5082 | 2598442.0589 | 1252233.2696 | 2598436.8086 | 1252239.4307 | 2598429.136 | 1252245.1699 | 2598412.6582 | 1252254.2693 | 2598407.3776 | 1252260.019 | 2598397.3018 | 1252279.6346 | 2598394.4298 | 1252290.1645 | 2598394.4171 | 1252298.6589 | 2598394.5573 | 1252299.4107
103 | 2598394.5573 | 1252299.4107 | 2598394.6212 | 1252299.7536
104 | 2598394.6212 | 1252299.7536 | 2598398.5812 | 1252320.9946 | 2598403.2289 | 1252331.603
105 | 2598414.5797 | 1252357.5116 | 2598403.2289 | 1252331.603
106 | 2598414.5797 | 1252357.5116 | 2598417.6097 | 1252364.4277
107 | 2598456.6802 | 1252485.8345 | 2598454.063 | 1252475.7023 | 2598450.7369 | 1252462.2404
108 | 2598493.231 | 1252458.2839 | 2598491.4253 | 1252461.4051 | 2598477.5209 | 1252479.6509
109 | 2598450.7369 | 1252462.2404 | 2598446.3871 | 1252444.6358
110 | 2598499.7369 | 1252447.038 | 2598493.231 | 1252458.2839
111 | 2598239.1423 | 1252508.1417 | 2598226.7173 | 1252508.9569
112 | 2598249.353 | 1252488.4146 | 2598239.1423 | 1252508.1417
113 | 2598239.1423 | 1252508.1417 | 2598263.3547 | 1252506.068
114 | 2598255.2321 | 1252538.4047 | 2598267.252 | 1252537.033
115 | 2598198.4692 | 1252510.8102 | 2598226.7173 | 1252508.9569
116 | 2598249.353 | 1252488.4146 | 2598228.8713 | 1252489.6137
117 | 2598293.8228 | 1252499.2303 | 2598281.7438 | 1252504.493 | 2598263.3547 | 1252506.068
118 | 2598279.8963 | 1252535.4258 | 2598278.32 | 1252535.77 | 2598267.252 | 1252537.033
119 | 2598118.2975 | 1252548.8403 | 2598130.5902 | 1252551.7937 | 2598144.2491 | 1252556.27 | 2598159.713 | 1252565.66 | 2598160.9335 | 1252566.8355
120 | 2598196.2995 | 1252491.8093 | 2598222.242 | 1252490.0018 | 2598228.8713 | 1252489.6137
121 | 2598324.9065 | 1252522.9576 | 2598290.3544 | 1252533.1424 | 2598279.8963 | 1252535.4258
122 | 2598296.8942 | 1252651.2176 | 2598301.3761 | 1252677.4201
123 | 2598429.0467 | 1252395.5812 | 2598434.0638 | 1252409.5535 | 2598437.9119 | 1252420.4747
124 | 2598442.8725 | 1252434.5528 | 2598437.9119 | 1252420.4747
125 | 2598424.5684 | 1252383.1094 | 2598429.0467 | 1252395.5812
126 | 2598442.8725 | 1252434.5528 | 2598446.2974 | 1252444.2728 | 2598446.3871 | 1252444.6358
127 | 2598424.5684 | 1252383.1094 | 2598418.9983 | 1252367.597 | 2598417.6097 | 1252364.4277
128 | 2598231.4554 | 1252674.5296 | 2598227.4322 | 1252675.3314
129 | 2598246.5504 | 1252673.6587 | 2598243.909 | 1252672.0473 | 2598231.4554 | 1252674.5296
130 | 2598351.7854 | 1252515.0346 | 2598324.9065 | 1252522.9576
131 | 2598216.0667 | 1252467.3888 | 2598246.2012 | 1252465.2959
132 | 2598189.8071 | 1252452.1787 | 2598170.2639 | 1252455.0955 | 2598152.7743 | 1252459.3484 | 2598133.3295 | 1252465.243
133 | 2598133.3295 | 1252465.243 | 2598110.7962 | 1252472.0738
134 | 2598499.7369 | 1252447.038 | 2598506.2977 | 1252432.2043 | 2598510.1981 | 1252418.4869
135 | 2598526.5526 | 1252440.4488 | 2598517.2716 | 1252441.4074 | 2598506.716 | 1252444.7568 | 2598499.7369 | 1252447.038
136 | 2598512.6905 | 1252409.7213 | 2598510.1981 | 1252418.4869
137 | 2598544.6255 | 1252414.9163 | 2598512.6905 | 1252409.7213
138 | 2598091.05 | 1252525.0672 | 2598149.1955 | 1252505.6905
139 | 2598085.0453 | 1252507.3576 | 2598091.05 | 1252525.0672
140 | 2598091.05 | 1252525.0672 | 2598095.9745 | 1252539.4305 | 2598096.3153 | 1252543.0216 | 2598118.2975 | 1252548.8403
141 | 2598126.3759 | 1252494.2687 | 2598085.0453 | 1252507.3576
142 | 2598085.0453 | 1252507.3576 | 2598084.1238 | 1252504.5783 | 2598076.4718 | 1252480.2317
143 | 2598118.2975 | 1252548.8403 | 2598122.3017 | 1252541.2563 | 2598147.6647 | 1252532.1763
144 | 2598076.4718 | 1252480.2317 | 2598107.9801 | 1252472.9275 | 2598110.7962 | 1252472.0738
145 | 2598172.7532 | 1252523.1947 | 2598147.6647 | 1252532.1763
146 | 2598645.7901 | 1252450.5417 | 2598672.3987 | 1252449.034
147 | 2598575.1023 | 1252450.4592 | 2598602.3692 | 1252448.8377

## bus_geodata
| x | y | coords
0 | 2598185.9755 | 1251734.8091
1 | 2598185.6512 | 1251742.1399
2 | 2598178.2205 | 1251688.2821
3 | 2598184.7491 | 1251746.8058
4 | 2598098.8828 | 1251726.8443
5 | 2598148.3687 | 1251604.2815
6 | 2598392.8127 | 1252149.3176
7 | 2598145.5226 | 1251852.6293
8 | 2598464.1534 | 1252177.3716
9 | 2598172.583 | 1251808.9572
10 | 2598077.1037 | 1251704.9406
11 | 2598110.1172 | 1251498.149
12 | 2598170.9421 | 1251818.7916
13 | 2598118.088 | 1251480.9557
14 | 2598163.2672 | 1251826.7797
15 | 2598120.0698 | 1251478.9495
16 | 2598133.0269 | 1251471.1539
17 | 2598168.7758 | 1251452.7991
18 | 2598087.0821 | 1251466.6768
19 | 2598197.1665 | 1251415.0317
20 | 2598080.6555 | 1251465.6473
21 | 2598112.9913 | 1251399.8657
22 | 2598064.5302 | 1251463.6598
23 | 2598425.6553 | 1252644.4092
24 | 2598399.1357 | 1252642.4612
25 | 2598361.9199 | 1252648.0408
26 | 2598359.9406 | 1252634.8547
27 | 2598365.1717 | 1252668.0317
28 | 2598377.7826 | 1252734.7151
29 | 2598348.0878 | 1252746.9872
30 | 2598356.9709 | 1252615.0705
31 | 2598339.18 | 1252686.2595
32 | 2598323.2677 | 1252760.559
33 | 2598564.9765 | 1252500.7662
34 | 2598599.179 | 1252482.6297
35 | 2598550.4671 | 1252501.658
36 | 2598605.4367 | 1252475.7851
37 | 2598525.3501 | 1252499.3051
38 | 2598616.3192 | 1252452.2115
39 | 2598611.8733 | 1252476.5062
40 | 2598499.804 | 1252500.962
41 | 2598617.2463 | 1252447.9529
42 | 2598626.6687 | 1252451.6251
43 | 2598613.2323 | 1252497.52
44 | 2598482.5998 | 1252513.6277
45 | 2598356.1521 | 1252609.6153
46 | 2598215.8086 | 1252609.2801
47 | 2598237.6313 | 1252631.4751
48 | 2598192.7172 | 1252612.8691
49 | 2598238.9563 | 1252638.5158
50 | 2598191.8397 | 1252605.8648
51 | 2598258.0492 | 1252721.6754
52 | 2598188.7669 | 1252600.5401
53 | 2598221.0059 | 1252544.688
54 | 2598250.9951 | 1252695.1901
55 | 2598272.7134 | 1252710.2191
56 | 2598178.1397 | 1252585.6363
57 | 2598222.2432 | 1252542.1692
58 | 2598248.373 | 1252682.4878
59 | 2598302.8095 | 1252685.7999
60 | 2598476.011 | 1252566.3344
61 | 2598462.8831 | 1252546.9845
62 | 2598500.7368 | 1252603.7511
63 | 2598453.7166 | 1252533.4735
64 | 2598489.9674 | 1252568.1975
65 | 2598403.7026 | 1252562.711
66 | 2598446.5561 | 1252522.9077
67 | 2598472.6628 | 1252530.5219
68 | 2598511.1606 | 1252564.8952
69 | 2598402.4467 | 1252563.1681
70 | 2598409.5183 | 1252468.2565
71 | 2598461.5178 | 1252502.0842
72 | 2598515.0581 | 1252564.7458
73 | 2598378.8402 | 1252418.174
74 | 2598382.2438 | 1252424.3555
75 | 2598364.1089 | 1252389.6714
76 | 2598389.2357 | 1252435.646
77 | 2598321.3652 | 1252442.2632
78 | 2598359.6645 | 1252370.7544
79 | 2598338.9708 | 1252380.4274
80 | 2598271.1172 | 1252447.1476
81 | 2598356.6053 | 1252357.7335
82 | 2598302.6559 | 1252338.6451
83 | 2598276.7178 | 1252436.269
84 | 2598261.894 | 1252464.206
85 | 2598353.0322 | 1252336.8286
86 | 2598303.6719 | 1252329.7056
87 | 2598300.8397 | 1252349.4285
88 | 2598456.4469 | 1252199.8823
89 | 2598394.5573 | 1252299.4107
90 | 2598394.6212 | 1252299.7536
91 | 2598583.4424 | 1252211.596
92 | 2598403.2289 | 1252331.603
93 | 2598414.5797 | 1252357.5116
94 | 2598456.6802 | 1252485.8345
95 | 2598477.5209 | 1252479.6509
96 | 2598450.7369 | 1252462.2404
97 | 2598493.231 | 1252458.2839
98 | 2598352.524 | 1252333.7833
99 | 2598239.1423 | 1252508.1417
100 | 2598255.2321 | 1252538.4047
101 | 2598226.7173 | 1252508.9569
102 | 2598249.353 | 1252488.4146
103 | 2598263.3547 | 1252506.068
104 | 2598267.252 | 1252537.033
105 | 2598160.9335 | 1252566.8355
106 | 2598198.4692 | 1252510.8102
107 | 2598228.8713 | 1252489.6137
108 | 2598293.8228 | 1252499.2303
109 | 2598279.8963 | 1252535.4258
110 | 2598301.3761 | 1252677.4201
111 | 2598296.8942 | 1252651.2176
112 | 2598437.9119 | 1252420.4747
113 | 2598429.0467 | 1252395.5812
114 | 2598442.8725 | 1252434.5528
115 | 2598424.5684 | 1252383.1094
116 | 2598446.3871 | 1252444.6358
117 | 2598417.6097 | 1252364.4277
118 | 2598227.4322 | 1252675.3314
119 | 2598231.4554 | 1252674.5296
120 | 2598246.5504 | 1252673.6587
121 | 2598324.9065 | 1252522.9576
122 | 2598351.7854 | 1252515.0346
123 | 2598355.9681 | 1252576.4538
124 | 2598288.4123 | 1252462.5423
125 | 2598246.2012 | 1252465.2959
126 | 2598216.0667 | 1252467.3888
127 | 2598196.2995 | 1252491.8093
128 | 2598281.2725 | 1252423.6353
129 | 2598189.8071 | 1252452.1787
130 | 2598133.3295 | 1252465.243
131 | 2598499.7369 | 1252447.038
132 | 2598510.1981 | 1252418.4869
133 | 2598526.5526 | 1252440.4488
134 | 2598512.6905 | 1252409.7213
135 | 2598544.6255 | 1252414.9163
136 | 2598149.1955 | 1252505.6905
137 | 2598091.05 | 1252525.0672
138 | 2598085.0453 | 1252507.3576
139 | 2598118.2975 | 1252548.8403
140 | 2598126.3759 | 1252494.2687
141 | 2598076.4718 | 1252480.2317
142 | 2598147.6647 | 1252532.1763
143 | 2598110.7962 | 1252472.0738
144 | 2598172.7532 | 1252523.1947
145 | 2598645.7901 | 1252450.5417
146 | 2598672.3987 | 1252449.034
147 | 2598602.3693 | 1252448.8377
148 | 2598575.1023 | 1252450.4592
149 | 2598222.2432 | 1252542.1692

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97129 | -0.55425 | 0.00048775 | 0.00012224
1 | 0.9713 | -0.55407 | 0.00032659 | 8.1852e-05
2 | 0.97119 | -0.55632 | 0 | 0
3 | 0.97131 | -0.55395 | 0.00040846 | 0.00010237
4 | 0.97112 | -0.55768 | 0.00061273 | 0.00015357
5 | 0.97087 | -0.56259 | 0 | 0
6 | 0.97214 | -0.53734 | 0.00049251 | 0.00012344
7 | 0.97147 | -0.55076 | 0.0013231 | 0.00033161
8 | 0.97228 | -0.5344 | 0 | 0
9 | 0.97139 | -0.55225 | 0.0002396 | 6.0049e-05
10 | 0.97111 | -0.5579 | 0.00021548 | 5.4005e-05
11 | 0.97047 | -0.57051 | 0.00059254 | 0.0001485
12 | 0.97141 | -0.55197 | 0 | 0
13 | 0.97042 | -0.57164 | 0 | 0
14 | 0.97142 | -0.55166 | 0.00010124 | 2.5372e-05
15 | 0.97041 | -0.57177 | 0.00064924 | 0.00016271
16 | 0.97038 | -0.57229 | 0.00014272 | 3.5769e-05
17 | 0.97032 | -0.57356 | 0.0012681 | 0.00031781
18 | 0.97039 | -0.57209 | 0.00016462 | 4.1258e-05
19 | 0.9703 | -0.57393 | 0 | 0
20 | 0.97039 | -0.57216 | 0.00016168 | 4.0522e-05
21 | 0.97027 | -0.57459 | 0.00041217 | 0.0001033
22 | 0.97038 | -0.57226 | 0.00036096 | 9.0466e-05
23 | 0.98036 | -0.37751 | 0.0038058 | 0.00095383
24 | 0.98046 | -0.37566 | 0.001647 | 0.00041279
25 | 0.98065 | -0.37194 | 0 | 0
26 | 0.98057 | -0.37342 | 0.0018396 | 0.00046103
27 | 0.98086 | -0.36768 | 0.0021653 | 0.00054268
28 | 0.98173 | -0.35074 | 0 | 0
29 | 0.98214 | -0.34275 | 0 | 0
30 | 0.98049 | -0.37498 | 0.0019314 | 0.00048405
31 | 0.98205 | -0.34447 | 0.0015477 | 0.00038789
32 | 0.98254 | -0.33494 | 0 | 0
33 | 0.97221 | -0.53565 | 0.0013434 | 0.00033668
34 | 0.97176 | -0.54453 | 0.002332 | 0.00058445
35 | 0.97239 | -0.53199 | 0.0021219 | 0.00053181
36 | 0.97167 | -0.54623 | 0 | 0
37 | 0.97276 | -0.52469 | 0.0013526 | 0.00033898
38 | 0.97146 | -0.5505 | 0 | 0
39 | 0.97167 | -0.54635 | 0 | 0
40 | 0.97317 | -0.51657 | 0.0014898 | 0.00037337
41 | 0.97145 | -0.55069 | 0 | 0
42 | 0.9714 | -0.55174 | 0.0010264 | 0.00025725
43 | 0.97165 | -0.54675 | 0.0010262 | 0.0002572
44 | 0.97355 | -0.50915 | 0.00090219 | 0.00022611
45 | 0.98048 | -0.37521 | 0.002366 | 0.00059296
46 | 0.98885 | -0.21226 | 0.00031457 | 7.8838e-05
47 | 0.98881 | -0.21302 | 0.00069181 | 0.00017339
48 | 0.98888 | -0.2117 | 0 | 0
49 | 0.98881 | -0.21306 | 0.00033248 | 8.3327e-05
50 | 0.98902 | -0.20888 | 0 | 0
51 | 0.98568 | -0.27371 | 0 | 0
52 | 0.98893 | -0.21074 | 0 | 0
53 | 0.99148 | -0.16146 | 0.0034766 | 0.00087133
54 | 0.98563 | -0.27463 | 0.0004851 | 0.00012158
55 | 0.98567 | -0.27389 | 0.00052359 | 0.00013123
56 | 0.98864 | -0.21626 | 0.00088873 | 0.00022274
57 | 0.99159 | -0.15933 | 0 | 0
58 | 0.98561 | -0.27494 | 0.00020793 | 5.2112e-05
59 | 0.98229 | -0.33968 | 0.0013486 | 0.000338
60 | 0.97561 | -0.46846 | 0.00041008 | 0.00010278
61 | 0.97594 | -0.46208 | 0.00051663 | 0.00012948
62 | 0.97499 | -0.48062 | 0 | 0
63 | 0.97616 | -0.45759 | 0 | 0
64 | 0.97445 | -0.49132 | 0 | 0
65 | 0.97458 | -0.48862 | 0.044759 | 0.011218
66 | 0.97669 | -0.4473 | 0.00069033 | 0.00017301
67 | 0.97391 | -0.50213 | 0 | 0
68 | 0.9744 | -0.49231 | 0.001372 | 0.00034386
69 | 0.9745 | -0.49037 | 0.00080059 | 0.00020065
70 | 0.97941 | -0.39403 | 0.0015415 | 0.00038635
71 | 0.97364 | -0.50735 | 0 | 0
72 | 0.9744 | -0.49239 | 0.0011261 | 0.00028222
73 | 0.98151 | -0.35322 | 0.0023397 | 0.0005864
74 | 0.98157 | -0.3521 | 0 | 0
75 | 0.98132 | -0.35696 | 0 | 0
76 | 0.98101 | -0.36291 | 0.0011098 | 0.00027814
77 | 0.98436 | -0.29801 | 0.0011026 | 0.00027633
78 | 0.98125 | -0.35824 | 0.001143 | 0.00028647
79 | 0.98125 | -0.35831 | 0.00096523 | 0.00024191
80 | 0.98659 | -0.255 | 0 | 0
81 | 0.98122 | -0.35885 | 0.00054146 | 0.0001357
82 | 0.98116 | -0.36014 | 0 | 0
83 | 0.98656 | -0.25564 | 0.0014101 | 0.00035341
84 | 0.98746 | -0.2383 | 0 | 0
85 | 0.98118 | -0.3596 | 0.00083501 | 0.00020927
86 | 0.98115 | -0.36029 | 0.00088408 | 0.00022157
87 | 0.98115 | -0.36033 | 0.00093002 | 0.00023309
88 | 0.97234 | -0.53335 | 0.00080935 | 0.00020284
89 | 0.97263 | -0.52745 | 0.001401 | 0.00035112
90 | 0.97263 | -0.52743 | 0.0011859 | 0.00029721
91 | 0.97209 | -0.53823 | 0.0015424 | 0.00038656
92 | 0.97273 | -0.52544 | 0.00095784 | 0.00024006
93 | 0.97282 | -0.52362 | 0.0026914 | 0.00067453
94 | 0.97353 | -0.50963 | 0.0020174 | 0.00050561
95 | 0.97344 | -0.51143 | 0.0014981 | 0.00037546
96 | 0.97337 | -0.51268 | 0.0013835 | 0.00034674
97 | 0.97328 | -0.51459 | 0.0013213 | 0.00033116
98 | 0.98118 | -0.35966 | 0.001128 | 0.00028272
99 | 0.98975 | -0.19449 | 0 | 0
100 | 0.99353 | -0.12242 | 0.00096656 | 0.00024224
101 | 0.9897 | -0.19539 | 0.0017656 | 0.0004425
102 | 0.98871 | -0.21435 | 0 | 0
103 | 0.98967 | -0.19605 | 0.0021347 | 0.00053502
104 | 0.99424 | -0.10895 | 0.012339 | 0.0030926
105 | 0.98827 | -0.22358 | 0.0014756 | 0.00036982
106 | 0.98964 | -0.19653 | 0.0022745 | 0.00057004
107 | 0.98863 | -0.21579 | 0.0020629 | 0.00051701
108 | 0.98962 | -0.19689 | 0.001479 | 0.00037067
109 | 0.99502 | -0.094082 | 0.019834 | 0.0049708
110 | 0.98228 | -0.33999 | 0.00044037 | 0.00011037
111 | 0.98224 | -0.34076 | 0.0015912 | 0.00039878
112 | 0.97313 | -0.51757 | 0.0012929 | 0.00032403
113 | 0.973 | -0.52015 | 0.001455 | 0.00036466
114 | 0.97321 | -0.51602 | 0.0016955 | 0.00042492
115 | 0.97294 | -0.52135 | 0.0014151 | 0.00035466
116 | 0.97327 | -0.51484 | 0.0016432 | 0.00041184
117 | 0.97285 | -0.52304 | 0.0016555 | 0.0004149
118 | 0.98559 | -0.27536 | 0.00034946 | 8.7582e-05
119 | 0.98559 | -0.27534 | 0.00038307 | 9.6005e-05
120 | 0.9856 | -0.27513 | 0.00041889 | 0.00010498
121 | 0.9981 | -0.035752 | 0.0077187 | 0.0019345
122 | 1 | 0 | -0.29934 | -0.076726
123 | 0.9713 | -0.5535 | 0.070762 | 0.017735
124 | 0.98743 | -0.23885 | 0.0011656 | 0.00029213
125 | 0.98741 | -0.23918 | 0.001584 | 0.00039698
126 | 0.98737 | -0.24003 | 0.0015588 | 0.00039068
127 | 0.98858 | -0.21689 | 0.0018802 | 0.00047123
128 | 0.98654 | -0.256 | 0.0015069 | 0.00037768
129 | 0.98659 | -0.25628 | 0.0024084 | 0.00060361
130 | 0.98672 | -0.25378 | 0.0014498 | 0.00036335
131 | 0.97321 | -0.51582 | 0 | 0
132 | 0.9731 | -0.51814 | 0.0021263 | 0.00053289
133 | 0.97319 | -0.51633 | 0.0010047 | 0.00025181
134 | 0.97308 | -0.51847 | 0 | 0
135 | 0.97302 | -0.51967 | 0.0020065 | 0.00050287
136 | 0.98719 | -0.24455 | 0.001598 | 0.0004005
137 | 0.98728 | -0.2428 | 0 | 0
138 | 0.98714 | -0.24543 | 0 | 0
139 | 0.98764 | -0.23575 | 0 | 0
140 | 0.98707 | -0.24698 | 0.0019962 | 0.00050029
141 | 0.98699 | -0.24843 | 0 | 0
142 | 0.98748 | -0.23897 | 0.0015417 | 0.00038639
143 | 0.9868 | -0.25215 | 0.0020289 | 0.00050848
144 | 0.98739 | -0.24065 | 0.0035259 | 0.00088368
145 | 0.9713 | -0.55366 | 0.0029595 | 0.00074172
146 | 0.97124 | -0.55488 | 0.0024813 | 0.00062186
147 | 0.97141 | -0.55135 | 0.0011011 | 0.00027597
148 | 0.97138 | -0.55201 | 0.0013067 | 0.00032748
149 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0050714 | -0.0012635 | 0.0050714 | 0.0012631 | 4.1794e-08 | -3.3915e-07 | 0.0077666 | 0.0077665 | 0.0077666 | 0.97129 | -0.55425 | 0.9713 | -0.55407 | 0.53342
1 | 0.0045836 | 0.0011412 | -0.0045832 | -0.0011422 | 4.5083e-07 | -9.1921e-07 | 0.0070194 | 0.0070198 | 0.0070198 | 0.97129 | -0.55425 | 0.97119 | -0.55632 | 0.96426
2 | -0.005398 | -0.001345 | 0.005398 | 0.0013448 | 3.0549e-08 | -2.1651e-07 | 0.0082668 | 0.0082667 | 0.0082668 | 0.9713 | -0.55407 | 0.97131 | -0.55395 | 0.56778
3 | 0.00082827 | 0.00020583 | -0.00082822 | -0.00020689 | 5.3327e-08 | -1.0592e-06 | 0.0012684 | 0.0012688 | 0.0012688 | 0.97119 | -0.55632 | 0.97112 | -0.55768 | 0.34857
4 | 0.0037549 | 0.00093633 | -0.0037538 | -0.00093673 | 1.1175e-06 | -3.9914e-07 | 0.0057514 | 0.0057518 | 0.0057518 | 0.97119 | -0.55632 | 0.97087 | -0.56259 | 1.5802
5 | -0.0058065 | -0.0014472 | 0.005807 | 0.0014443 | 4.6983e-07 | -2.8377e-06 | 0.0088925 | 0.0088914 | 0.0088925 | 0.97131 | -0.55395 | 0.97139 | -0.55225 | 0.61075
6 | 0.00021549 | 5.3324e-05 | -0.00021548 | -5.4005e-05 | 2.254e-09 | -6.8118e-07 | 0.00032994 | 0.00033018 | 0.00033018 | 0.97112 | -0.55768 | 0.97111 | -0.5579 | 0.090709
7 | 0.0037538 | 0.00093673 | -0.0037524 | -0.00093724 | 1.4109e-06 | -5.0266e-07 | 0.0057518 | 0.0057523 | 0.0057523 | 0.97087 | -0.56259 | 0.97047 | -0.57051 | 1.5803
8 | 0.0074761 | 0.0018429 | -0.0074714 | -0.001859 | 4.7354e-06 | -1.6111e-05 | 0.011432 | 0.011439 | 0.011439 | 0.97214 | -0.53734 | 0.97147 | -0.55076 | 0.78566
9 | -0.0079686 | -0.0019663 | 0.0079697 | 0.0019631 | 1.1015e-06 | -3.22e-06 | 0.012186 | 0.012185 | 0.012186 | 0.97214 | -0.53734 | 0.97228 | -0.5344 | 0.83697
10 | 0.0061482 | 0.0015274 | -0.006148 | -0.0015288 | 2.6063e-07 | -1.3871e-06 | 0.0094125 | 0.0094131 | 0.0094131 | 0.97147 | -0.55076 | 0.97142 | -0.55166 | 0.6465
11 | 0.0015427 | 0.00038507 | -0.0015424 | -0.00038656 | 2.8097e-07 | -1.4873e-06 | 0.0023604 | 0.002361 | 0.002361 | 0.97228 | -0.5344 | 0.97209 | -0.53823 | 0.64862
12 | -0.0095124 | -0.0023482 | 0.0095129 | 0.0023473 | 4.7205e-07 | -8.7866e-07 | 0.014545 | 0.014545 | 0.014545 | 0.97228 | -0.5344 | 0.97234 | -0.53335 | 0.99898
13 | -0.0060466 | -0.0015044 | 0.0060466 | 0.0015039 | 8.012e-08 | -4.4243e-07 | 0.0092584 | 0.0092582 | 0.0092584 | 0.97139 | -0.55225 | 0.97141 | -0.55197 | 0.63588
14 | 0.0031598 | 0.00078873 | -0.0031597 | -0.00078886 | 1.7055e-07 | -1.3034e-07 | 0.0048438 | 0.0048439 | 0.0048439 | 0.97047 | -0.57051 | 0.97042 | -0.57164 | 1.3307
15 | -0.0060466 | -0.0015039 | 0.0060467 | 0.0015034 | 8.9015e-08 | -4.9159e-07 | 0.0092582 | 0.009258 | 0.0092582 | 0.97141 | -0.55197 | 0.97142 | -0.55166 | 0.63587
16 | 0.00068729 | 0.00017154 | -0.00068727 | -0.00017197 | 1.4667e-08 | -4.2582e-07 | 0.0010536 | 0.0010538 | 0.0010538 | 0.97042 | -0.57164 | 0.97039 | -0.57209 | 0.2895
17 | 0.0024724 | 0.00061732 | -0.0024724 | -0.00061735 | 1.5192e-08 | -2.5116e-08 | 0.0037903 | 0.0037903 | 0.0037903 | 0.97042 | -0.57164 | 0.97041 | -0.57177 | 1.0413
18 | 0.0018231 | 0.00045463 | -0.0018231 | -0.00045479 | 4.477e-08 | -1.6018e-07 | 0.0027947 | 0.0027948 | 0.0027948 | 0.97041 | -0.57177 | 0.97038 | -0.57229 | 0.7678
19 | 0.0016804 | 0.00041902 | -0.0016803 | -0.00041946 | 1.0123e-07 | -4.3772e-07 | 0.002576 | 0.0025761 | 0.0025761 | 0.97038 | -0.57229 | 0.97032 | -0.57356 | 0.70773
20 | 0.00041219 | 0.00010165 | -0.00041218 | -0.00010224 | 7.1304e-09 | -5.8415e-07 | 0.00063151 | 0.00063172 | 0.00063172 | 0.97032 | -0.57356 | 0.9703 | -0.57393 | 0.17355
21 | 0.00052265 | 0.00013071 | -0.00052265 | -0.00013079 | 1.5674e-09 | -7.9403e-08 | 0.00080134 | 0.00080137 | 0.00080137 | 0.97039 | -0.57209 | 0.97039 | -0.57216 | 0.22016
22 | 0.00041218 | 0.00010224 | -0.00041217 | -0.0001033 | 1.2986e-08 | -1.0628e-06 | 0.00063172 | 0.00063211 | 0.00063211 | 0.9703 | -0.57393 | 0.97027 | -0.57459 | 0.17366
23 | 0.00036097 | 9.0266e-05 | -0.00036096 | -9.0466e-05 | 1.8677e-09 | -1.9965e-07 | 0.00055344 | 0.00055351 | 0.00055351 | 0.97039 | -0.57216 | 0.97038 | -0.57226 | 0.15206
24 | -0.0038058 | -0.00095383 | 0.0038061 | 0.0009537 | 3.3462e-07 | -1.2307e-07 | 0.0057766 | 0.0057764 | 0.0057766 | 0.98036 | -0.37751 | 0.98046 | -0.37566 | 1.587
25 | -0.0054532 | -0.0013665 | 0.0054541 | 0.0013666 | 9.6782e-07 | 1.441e-07 | 0.0082761 | 0.0082759 | 0.0082761 | 0.98046 | -0.37566 | 0.98065 | -0.37194 | 2.2737
26 | 0.0061376 | 0.0015381 | -0.0061372 | -0.0015379 | 4.3369e-07 | 1.0935e-07 | 0.0093131 | 0.0093132 | 0.0093132 | 0.98065 | -0.37194 | 0.98057 | -0.37342 | 2.5586
27 | -0.011592 | -0.0029047 | 0.011594 | 0.0029059 | 2.3497e-06 | 1.2482e-06 | 0.017589 | 0.017589 | 0.017589 | 0.98065 | -0.37194 | 0.98086 | -0.36768 | 4.8322
28 | 0.0042977 | 0.0010769 | -0.0042973 | -0.001077 | 3.1909e-07 | -4.8127e-08 | 0.0065216 | 0.0065217 | 0.0065217 | 0.98057 | -0.37342 | 0.98049 | -0.37498 | 1.7917
29 | -0.013759 | -0.0034486 | 0.013771 | 0.0034549 | 1.1112e-05 | 6.2523e-06 | 0.020874 | 0.020874 | 0.020874 | 0.98086 | -0.36768 | 0.98173 | -0.35074 | 5.7346
30 | -0.013771 | -0.0034549 | 0.013776 | 0.0034578 | 5.2499e-06 | 2.9535e-06 | 0.020874 | 0.020873 | 0.020874 | 0.98173 | -0.35074 | 0.98214 | -0.34275 | 5.7345
31 | 0.0015478 | 0.00038719 | -0.0015477 | -0.00038789 | 1.2656e-07 | -6.9565e-07 | 0.0023448 | 0.0023451 | 0.0023451 | 0.98214 | -0.34275 | 0.98205 | -0.34447 | 0.64425
32 | -0.015324 | -0.003845 | 0.015329 | 0.0038483 | 5.7089e-06 | 3.2962e-06 | 0.023218 | 0.023218 | 0.023218 | 0.98214 | -0.34275 | 0.98254 | -0.33494 | 6.3786
33 | 0.002366 | 0.00059291 | -0.002366 | -0.00059296 | 2.667e-08 | -5.2504e-08 | 0.0035906 | 0.0035907 | 0.0035907 | 0.98049 | -0.37498 | 0.98048 | -0.37521 | 0.98645
34 | 0.003381 | 0.00084627 | -0.0033803 | -0.00084676 | 7.6314e-07 | -4.9445e-07 | 0.00512 | 0.0051204 | 0.0051204 | 0.98254 | -0.33494 | 0.98229 | -0.33968 | 1.4067
35 | -0.01871 | -0.0046946 | 0.018765 | 0.0047273 | 5.4786e-05 | 3.2751e-05 | 0.028338 | 0.028337 | 0.028338 | 0.98254 | -0.33494 | 0.98568 | -0.27371 | 7.7852
36 | 0.012242 | 0.0030691 | -0.012237 | -0.0030663 | 5.1788e-06 | 2.8269e-06 | 0.018738 | 0.018738 | 0.018738 | 0.97221 | -0.53565 | 0.97176 | -0.54453 | 5.1478
37 | -0.013586 | -0.0034058 | 0.013588 | 0.0034072 | 2.3671e-06 | 1.3339e-06 | 0.020794 | 0.020794 | 0.020794 | 0.97221 | -0.53565 | 0.97239 | -0.53199 | 5.7126
38 | 0.009905 | 0.0024819 | -0.0099042 | -0.0024815 | 8.0174e-07 | 3.9798e-07 | 0.015167 | 0.015167 | 0.015167 | 0.97176 | -0.54453 | 0.97167 | -0.54623 | 4.1668
39 | -0.01571 | -0.003939 | 0.015715 | 0.0039422 | 5.4708e-06 | 3.1881e-06 | 0.024041 | 0.024041 | 0.024041 | 0.97239 | -0.53199 | 0.97276 | -0.52469 | 6.6046
40 | 0.008878 | 0.0022246 | -0.0088762 | -0.0022238 | 1.8039e-06 | 8.3219e-07 | 0.013596 | 0.013596 | 0.013596 | 0.97167 | -0.54623 | 0.97146 | -0.5505 | 3.7351
41 | 0.0010263 | 0.00025687 | -0.0010263 | -0.00025695 | 5.9808e-09 | -7.6164e-08 | 0.0015715 | 0.0015715 | 0.0015715 | 0.97167 | -0.54623 | 0.97167 | -0.54635 | 0.43174
42 | -0.017068 | -0.0042811 | 0.017075 | 0.004285 | 6.6086e-06 | 3.9084e-06 | 0.02611 | 0.02611 | 0.02611 | 0.97276 | -0.52469 | 0.97317 | -0.51657 | 7.173
43 | 0.0024079 | 0.00060296 | -0.0024079 | -0.000603 | 2.2229e-08 | -3.9729e-08 | 0.0036881 | 0.0036881 | 0.0036881 | 0.97146 | -0.5505 | 0.97145 | -0.55069 | 1.0132
44 | 0.0064682 | 0.0016208 | -0.0064679 | -0.0016207 | 3.8157e-07 | 1.1587e-07 | 0.0099075 | 0.0099076 | 0.0099076 | 0.97146 | -0.5505 | 0.9714 | -0.55174 | 2.7219
45 | 0.0010263 | 0.00025695 | -0.0010262 | -0.0002572 | 1.9503e-08 | -2.4834e-07 | 0.0015715 | 0.0015716 | 0.0015716 | 0.97167 | -0.54635 | 0.97165 | -0.54675 | 0.43176
46 | -0.018564 | -0.0046584 | 0.018571 | 0.0046623 | 6.5733e-06 | 3.9365e-06 | 0.028387 | 0.028387 | 0.028387 | 0.97317 | -0.51657 | 0.97355 | -0.50915 | 7.7988
47 | 0.0024079 | 0.000603 | -0.0024078 | -0.00060314 | 7.6021e-08 | -1.3586e-07 | 0.0036881 | 0.0036882 | 0.0036882 | 0.97145 | -0.55069 | 0.97141 | -0.55135 | 1.0132
48 | 0.0054414 | 0.0013634 | -0.0054409 | -0.0013633 | 4.9899e-07 | 8.2282e-08 | 0.0083352 | 0.0083353 | 0.0083353 | 0.9714 | -0.55174 | 0.9713 | -0.55366 | 2.2899
49 | -0.019473 | -0.0048885 | 0.01948 | 0.0048924 | 6.5218e-06 | 3.9298e-06 | 0.029766 | 0.029766 | 0.029766 | 0.97355 | -0.50915 | 0.97391 | -0.50213 | 8.1776
50 | 0.0010243 | 0.00025611 | -0.0010243 | -0.00025662 | 3.6778e-08 | -5.0605e-07 | 0.0015412 | 0.0015414 | 0.0015414 | 0.98885 | -0.21226 | 0.98881 | -0.21302 | 0.42346
51 | -0.0013389 | -0.00033495 | 0.0013389 | 0.00033467 | 3.5563e-08 | -2.7703e-07 | 0.0020146 | 0.0020144 | 0.0020146 | 0.98885 | -0.21226 | 0.98888 | -0.2117 | 0.55345
52 | 0.00033248 | 8.3235e-05 | -0.00033248 | -8.3327e-05 | 6.7251e-10 | -9.1469e-08 | 0.0005003 | 0.00050033 | 0.00050033 | 0.98881 | -0.21302 | 0.98881 | -0.21306 | 0.13745
53 | -0.022535 | -0.0056925 | 0.022538 | 0.0056944 | 3.0467e-06 | 1.8593e-06 | 0.033926 | 0.033926 | 0.033926 | 0.98888 | -0.2117 | 0.98902 | -0.20888 | 9.3202
54 | 0.021196 | 0.0053579 | -0.021133 | -0.0053198 | 6.2832e-05 | 3.8109e-05 | 0.031911 | 0.031912 | 0.031912 | 0.98888 | -0.2117 | 0.98568 | -0.27371 | 8.767
55 | 0.016941 | 0.0042508 | -0.01694 | -0.0042499 | 1.497e-06 | 8.7926e-07 | 0.02549 | 0.02549 | 0.02549 | 0.98902 | -0.20888 | 0.98893 | -0.21074 | 7.0028
56 | -0.039479 | -0.0099452 | 0.039569 | 0.010002 | 8.9756e-05 | 5.6572e-05 | 0.059416 | 0.059416 | 0.059416 | 0.98902 | -0.20888 | 0.99148 | -0.16146 | 16.323
57 | 0.0018446 | 0.00046145 | -0.0018445 | -0.00046175 | 8.0208e-08 | -3.003e-07 | 0.0027843 | 0.0027844 | 0.0027844 | 0.98568 | -0.27371 | 0.98563 | -0.27463 | 0.76496
58 | 0.0005236 | 0.00013099 | -0.00052359 | -0.00013123 | 4.3596e-09 | -2.344e-07 | 0.00079036 | 0.00079045 | 0.00079045 | 0.98568 | -0.27371 | 0.98567 | -0.27389 | 0.21716
59 | 0.01694 | 0.0042499 | -0.016935 | -0.0042473 | 4.4601e-06 | 2.6197e-06 | 0.02549 | 0.02549 | 0.02549 | 0.98893 | -0.21074 | 0.98864 | -0.21626 | 7.0029
60 | -0.043046 | -0.010873 | 0.04305 | 0.010876 | 4.3962e-06 | 2.7774e-06 | 0.064633 | 0.064633 | 0.064633 | 0.99148 | -0.16146 | 0.99159 | -0.15933 | 17.7564
61 | 0.0013594 | 0.00034017 | -0.0013594 | -0.00034033 | 2.0482e-08 | -1.5219e-07 | 0.0020521 | 0.0020521 | 0.0020521 | 0.98563 | -0.27463 | 0.98561 | -0.27494 | 0.56378
62 | 0.016046 | 0.0040245 | -0.016041 | -0.0040213 | 5.5967e-06 | 3.2539e-06 | 0.024153 | 0.024153 | 0.024153 | 0.98864 | -0.21626 | 0.98827 | -0.22358 | 6.6354
63 | 0.21163 | 0.05424 | -0.21127 | -0.054011 | 0.00036002 | 0.00022846 | 0.31801 | 0.31801 | 0.31801 | 0.99159 | -0.15933 | 0.98975 | -0.19449 | 21.8411
64 | -0.25468 | -0.065115 | 0.25513 | 0.065405 | 0.00045575 | 0.00028996 | 0.38264 | 0.38264 | 0.38264 | 0.99159 | -0.15933 | 0.99353 | -0.12242 | 26.2801
65 | 0.0011514 | 0.00028821 | -0.0011514 | -0.00028832 | 1.0215e-08 | -1.0836e-07 | 0.0017382 | 0.0017383 | 0.0017383 | 0.98561 | -0.27494 | 0.9856 | -0.27513 | 0.47755
66 | 0.0020316 | 0.00050877 | -0.0020316 | -0.00050885 | 3.0194e-08 | -8.8294e-08 | 0.0030774 | 0.0030775 | 0.0030775 | 0.98229 | -0.33968 | 0.98228 | -0.33999 | 0.84546
67 | -0.059591 | -0.014932 | 0.059609 | 0.014942 | 1.8108e-05 | 1.0421e-05 | 0.090888 | 0.090887 | 0.090888 | 0.97561 | -0.46846 | 0.97594 | -0.46208 | 6.2423
68 | 0.059181 | 0.014829 | -0.059147 | -0.01481 | 3.4266e-05 | 1.9691e-05 | 0.090262 | 0.090263 | 0.090263 | 0.97561 | -0.46846 | 0.97499 | -0.48062 | 6.1994
69 | -0.060126 | -0.015072 | 0.060139 | 0.015079 | 1.2864e-05 | 7.4168e-06 | 0.091675 | 0.091675 | 0.091675 | 0.97594 | -0.46208 | 0.97616 | -0.45759 | 6.2964
70 | 0.059147 | 0.01481 | -0.059117 | -0.014792 | 3.009e-05 | 1.7294e-05 | 0.090263 | 0.090264 | 0.090264 | 0.97499 | -0.48062 | 0.97445 | -0.49132 | 6.1994
71 | 0.11671 | 0.0294 | -0.11654 | -0.029293 | 0.00017289 | 0.00010774 | 0.17797 | 0.17797 | 0.17797 | 0.97616 | -0.45759 | 0.97458 | -0.48862 | 12.223
72 | -0.17685 | -0.04448 | 0.17694 | 0.044535 | 8.6999e-05 | 5.5041e-05 | 0.26964 | 0.26964 | 0.26964 | 0.97616 | -0.45759 | 0.97669 | -0.4473 | 18.5193
73 | 0.056618 | 0.014166 | -0.056589 | -0.01415 | 2.9111e-05 | 1.6562e-05 | 0.086449 | 0.08645 | 0.08645 | 0.97445 | -0.49132 | 0.97391 | -0.50213 | 5.9375
74 | 0.0024982 | 0.00062583 | -0.0024981 | -0.00062603 | 1.1787e-07 | -1.9362e-07 | 0.0038147 | 0.0038148 | 0.0038148 | 0.97445 | -0.49132 | 0.9744 | -0.49231 | 1.048
75 | 0.071782 | 0.018075 | -0.071776 | -0.018071 | 6.0236e-06 | 3.8385e-06 | 0.10963 | 0.10963 | 0.10963 | 0.97458 | -0.48862 | 0.9745 | -0.49037 | 30.1178
76 | -0.17763 | -0.044708 | 0.17808 | 0.044995 | 0.00045352 | 0.00028694 | 0.27069 | 0.27069 | 0.27069 | 0.97669 | -0.4473 | 0.97941 | -0.39403 | 18.5915
77 | 0.03711 | 0.0092575 | -0.0371 | -0.0092531 | 9.1976e-06 | 4.3671e-06 | 0.056684 | 0.056684 | 0.056684 | 0.97391 | -0.50213 | 0.97364 | -0.50735 | 3.8932
78 | 0.0011261 | 0.00028217 | -0.0011261 | -0.00028222 | 4.325e-09 | -4.5815e-08 | 0.0017196 | 0.0017196 | 0.0017196 | 0.9744 | -0.49231 | 0.9744 | -0.49239 | 0.47242
79 | 0.070975 | 0.017871 | -0.070762 | -0.017735 | 0.0002135 | 0.00013604 | 0.10841 | 0.10841 | 0.10841 | 0.9745 | -0.49037 | 0.9713 | -0.5535 | 29.782
80 | -0.17962 | -0.045381 | 0.17989 | 0.045551 | 0.0002684 | 0.00016984 | 0.27303 | 0.27303 | 0.27303 | 0.97941 | -0.39403 | 0.98101 | -0.36291 | 18.7523
81 | 0.02914 | 0.0072588 | -0.029137 | -0.0072576 | 3.1533e-06 | 1.174e-06 | 0.044519 | 0.044519 | 0.044519 | 0.97364 | -0.50735 | 0.97353 | -0.50963 | 3.0576
82 | 0.0079604 | 0.0019943 | -0.0079588 | -0.0019937 | 1.5476e-06 | 6.4374e-07 | 0.012166 | 0.012166 | 0.012166 | 0.97364 | -0.50735 | 0.97344 | -0.51143 | 3.3422
83 | -0.0087685 | -0.0021959 | 0.0087689 | 0.0021961 | 4.6759e-07 | 2.1006e-07 | 0.013293 | 0.013293 | 0.013293 | 0.98151 | -0.35322 | 0.98157 | -0.3521 | 3.6519
84 | 0.0064287 | 0.0016095 | -0.0064276 | -0.0016092 | 1.1436e-06 | 3.2619e-07 | 0.0097457 | 0.0097458 | 0.0097458 | 0.98151 | -0.35322 | 0.98132 | -0.35696 | 2.6774
85 | 0.1811 | 0.045889 | -0.181 | -0.045829 | 9.396e-05 | 5.9463e-05 | 0.27472 | 0.27472 | 0.27472 | 0.98157 | -0.3521 | 0.98101 | -0.36291 | 18.8679
86 | -0.18987 | -0.048085 | 0.19036 | 0.048398 | 0.00049459 | 0.00031331 | 0.28801 | 0.28801 | 0.28801 | 0.98157 | -0.3521 | 0.98436 | -0.29801 | 19.7808
87 | 0.0036479 | 0.00091367 | -0.0036477 | -0.00091378 | 2.2295e-07 | -1.0279e-07 | 0.0055313 | 0.0055314 | 0.0055314 | 0.98132 | -0.35696 | 0.98125 | -0.35824 | 1.5196
88 | 0.0027797 | 0.00069549 | -0.0027795 | -0.00069572 | 1.7844e-07 | -2.2421e-07 | 0.0042145 | 0.0042147 | 0.0042147 | 0.98132 | -0.35696 | 0.98125 | -0.35831 | 1.1579
89 | -0.19146 | -0.048674 | 0.19186 | 0.048926 | 0.00039756 | 0.00025186 | 0.28967 | 0.28967 | 0.28967 | 0.98436 | -0.29801 | 0.98659 | -0.255 | 19.8952
90 | 0.0025047 | 0.00062731 | -0.0025046 | -0.00062743 | 7.2354e-08 | -1.2265e-07 | 0.003798 | 0.0037981 | 0.0037981 | 0.98125 | -0.35824 | 0.98122 | -0.35885 | 1.0434
91 | 0.0018143 | 0.00045381 | -0.0018141 | -0.00045441 | 1.5856e-07 | -6.0416e-07 | 0.0027509 | 0.0027512 | 0.0027512 | 0.98125 | -0.35831 | 0.98116 | -0.36014 | 0.75582
92 | 0.0029172 | 0.00073083 | -0.0029171 | -0.00073093 | 8.882e-08 | -9.9398e-08 | 0.0043997 | 0.0043997 | 0.0043997 | 0.98659 | -0.255 | 0.98656 | -0.25564 | 1.2087
93 | -0.19478 | -0.049657 | 0.19493 | 0.049757 | 0.00015713 | 9.9572e-05 | 0.29407 | 0.29407 | 0.29407 | 0.98659 | -0.255 | 0.98746 | -0.2383 | 20.1973
94 | 0.0019631 | 0.00049173 | -0.0019631 | -0.00049195 | 7.0494e-08 | -2.2279e-07 | 0.002977 | 0.0029771 | 0.0029771 | 0.98122 | -0.35885 | 0.98118 | -0.3596 | 0.81788
95 | 0.00088408 | 0.00022146 | -0.00088408 | -0.00022157 | 6.0652e-09 | -1.0975e-07 | 0.0013408 | 0.0013408 | 0.0013408 | 0.98116 | -0.36014 | 0.98115 | -0.36029 | 0.36835
96 | 0.00093003 | 0.00023295 | -0.00093002 | -0.00023309 | 8.1579e-09 | -1.3288e-07 | 0.0014104 | 0.0014105 | 0.0014105 | 0.98116 | -0.36014 | 0.98115 | -0.36033 | 0.38749
97 | 0.001507 | 0.00037752 | -0.0015069 | -0.00037768 | 2.6066e-08 | -1.5512e-07 | 0.0022729 | 0.002273 | 0.002273 | 0.98656 | -0.25564 | 0.98654 | -0.256 | 0.62444
98 | 0.003143 | 0.0007872 | -0.0031429 | -0.00078732 | 1.3232e-07 | -1.1654e-07 | 0.0047361 | 0.0047361 | 0.0047361 | 0.98746 | -0.2383 | 0.98741 | -0.23918 | 1.3011
99 | -0.19924 | -0.050836 | 0.19947 | 0.050982 | 0.00023078 | 0.0001463 | 0.30056 | 0.30056 | 0.30056 | 0.98746 | -0.2383 | 0.98871 | -0.21435 | 20.6432
100 | 0.0011656 | 0.00029181 | -0.0011656 | -0.00029213 | 3.074e-08 | -3.2021e-07 | 0.0017564 | 0.0017565 | 0.0017565 | 0.98746 | -0.2383 | 0.98743 | -0.23885 | 0.48256
101 | 0.0011281 | 0.00028268 | -0.001128 | -0.00028272 | 3.3884e-09 | -3.6826e-08 | 0.0017107 | 0.0017108 | 0.0017108 | 0.98118 | -0.3596 | 0.98118 | -0.35966 | 0.46999
102 | -0.010322 | -0.0025502 | 0.010325 | 0.0025459 | 2.8702e-06 | -4.2632e-06 | 0.015783 | 0.015781 | 0.015783 | 0.97234 | -0.53335 | 0.97263 | -0.52745 | 1.084
103 | -0.011726 | -0.002897 | 0.011726 | 0.002897 | 1.0505e-08 | -1.0591e-08 | 0.017925 | 0.017925 | 0.017925 | 0.97263 | -0.52745 | 0.97263 | -0.52743 | 1.2311
104 | -0.012912 | -0.0031942 | 0.012913 | 0.0031933 | 1.2122e-06 | -8.7197e-07 | 0.019739 | 0.019738 | 0.019739 | 0.97263 | -0.52743 | 0.97273 | -0.52544 | 1.3557
105 | -0.013871 | -0.0034334 | 0.013872 | 0.0034328 | 1.1922e-06 | -6.4165e-07 | 0.021203 | 0.021203 | 0.021203 | 0.97273 | -0.52544 | 0.97282 | -0.52362 | 1.4563
106 | -0.016564 | -0.0041073 | 0.016564 | 0.0041072 | 4.5381e-07 | -8.4571e-08 | 0.02532 | 0.02532 | 0.02532 | 0.97282 | -0.52362 | 0.97285 | -0.52304 | 1.739
107 | 0.02712 | 0.006752 | -0.027116 | -0.0067507 | 3.9164e-06 | 1.2966e-06 | 0.041435 | 0.041436 | 0.041436 | 0.97353 | -0.50963 | 0.97337 | -0.51268 | 2.8459
108 | 0.0064607 | 0.0016182 | -0.0064597 | -0.0016179 | 9.7087e-07 | 2.9141e-07 | 0.0098756 | 0.0098758 | 0.0098758 | 0.97344 | -0.51143 | 0.97328 | -0.51459 | 2.7131
109 | 0.025732 | 0.006404 | -0.025729 | -0.0064032 | 2.6286e-06 | 7.8076e-07 | 0.039321 | 0.039321 | 0.039321 | 0.97337 | -0.51268 | 0.97327 | -0.51484 | 2.7006
110 | 0.0051384 | 0.0012868 | -0.0051381 | -0.0012867 | 3.0066e-07 | 3.0972e-08 | 0.0078556 | 0.0078557 | 0.0078557 | 0.97328 | -0.51459 | 0.97321 | -0.51582 | 2.1581
111 | 0.0040404 | 0.0010122 | -0.0040402 | -0.0010123 | 1.7229e-07 | -4.9753e-08 | 0.0060743 | 0.0060743 | 0.0060743 | 0.98975 | -0.19449 | 0.9897 | -0.19539 | 1.6688
112 | 0.20361 | 0.052094 | -0.20342 | -0.05197 | 0.00019552 | 0.000124 | 0.3065 | 0.3065 | 0.3065 | 0.98975 | -0.19449 | 0.98871 | -0.21435 | 21.0508
113 | 0.003614 | 0.00090517 | -0.0036138 | -0.00090531 | 2.6902e-07 | -1.4011e-07 | 0.0054333 | 0.0054334 | 0.0054334 | 0.98975 | -0.19449 | 0.98967 | -0.19605 | 1.4927
114 | -0.2561 | -0.065648 | 0.25627 | 0.065754 | 0.00016732 | 0.00010645 | 0.38409 | 0.38408 | 0.38409 | 0.99353 | -0.12242 | 0.99424 | -0.10895 | 26.3795
115 | 0.0022746 | 0.00056975 | -0.0022745 | -0.00057004 | 1.2415e-07 | -2.843e-07 | 0.0034197 | 0.0034199 | 0.0034199 | 0.9897 | -0.19539 | 0.98964 | -0.19653 | 0.93953
116 | 0.0039435 | 0.00098779 | -0.0039432 | -0.00098788 | 2.7099e-07 | -8.9667e-08 | 0.0059348 | 0.0059349 | 0.0059349 | 0.98871 | -0.21435 | 0.98863 | -0.21579 | 1.6305
117 | 0.001479 | 0.0003703 | -0.001479 | -0.00037067 | 5.8658e-08 | -3.689e-07 | 0.0022237 | 0.0022238 | 0.0022238 | 0.98967 | -0.19605 | 0.98962 | -0.19689 | 0.61094
118 | -0.26861 | -0.068847 | 0.2688 | 0.06897 | 0.00019375 | 0.00012334 | 0.40255 | 0.40255 | 0.40255 | 0.99424 | -0.10895 | 0.99502 | -0.094082 | 27.6478
119 | 0.014565 | 0.0036514 | -0.014557 | -0.0036466 | 8.4416e-06 | 4.8033e-06 | 0.021931 | 0.021931 | 0.021931 | 0.98827 | -0.22358 | 0.98764 | -0.23575 | 6.0251
120 | 0.0018803 | 0.00047087 | -0.0018802 | -0.00047123 | 9.805e-08 | -3.5584e-07 | 0.00283 | 0.0028301 | 0.0028301 | 0.98863 | -0.21579 | 0.98858 | -0.21689 | 0.7775
121 | -0.28863 | -0.073941 | 0.28945 | 0.074462 | 0.00081833 | 0.00052129 | 0.43221 | 0.43221 | 0.43221 | 0.99502 | -0.094082 | 0.9981 | -0.035752 | 29.6849
122 | 0.0015912 | 0.00039849 | -0.0015912 | -0.00039878 | 5.792e-08 | -2.9942e-07 | 0.0024104 | 0.0024105 | 0.0024105 | 0.98228 | -0.33999 | 0.98224 | -0.34076 | 0.66223
123 | 0.021095 | 0.0052418 | -0.021092 | -0.0052414 | 2.5751e-06 | 3.3502e-07 | 0.03224 | 0.032241 | 0.032241 | 0.97313 | -0.51757 | 0.973 | -0.52015 | 2.2143
124 | -0.022388 | -0.0055658 | 0.022389 | 0.0055661 | 1.6384e-06 | 3.0672e-07 | 0.034217 | 0.034217 | 0.034217 | 0.97313 | -0.51757 | 0.97321 | -0.51602 | 2.3501
125 | 0.019637 | 0.0048768 | -0.019636 | -0.0048767 | 1.1192e-06 | 5.8004e-08 | 0.030015 | 0.030016 | 0.030016 | 0.973 | -0.52015 | 0.97294 | -0.52135 | 2.0615
126 | -0.024085 | -0.005991 | 0.024086 | 0.0059914 | 1.3566e-06 | 3.3735e-07 | 0.036809 | 0.036809 | 0.036809 | 0.97321 | -0.51602 | 0.97327 | -0.51484 | 2.5281
127 | 0.018221 | 0.0045221 | -0.01822 | -0.0045221 | 1.4502e-06 | -6.2395e-08 | 0.027851 | 0.027852 | 0.027852 | 0.97294 | -0.52135 | 0.97285 | -0.52304 | 1.9129
128 | -0.00034946 | -8.7582e-05 | 0.00034946 | 8.753e-05 | 4.282e-10 | -5.2005e-08 | 0.0005276 | 0.00052758 | 0.0005276 | 0.98559 | -0.27536 | 0.98559 | -0.27534 | 0.14495
129 | -0.00073252 | -0.00018354 | 0.00073253 | 0.00018334 | 7.2428e-09 | -1.9663e-07 | 0.0011059 | 0.0011059 | 0.0011059 | 0.98559 | -0.27534 | 0.9856 | -0.27513 | 0.30382
130 | -0.29717 | -0.076396 | 0.29769 | 0.076726 | 0.00051724 | 0.00032956 | 0.44372 | 0.44372 | 0.44372 | 0.9981 | -0.035752 | 1 | 0 | 30.4752
131 | 0.0015589 | 0.00039033 | -0.0015588 | -0.00039068 | 6.2512e-08 | -3.4636e-07 | 0.0023491 | 0.0023492 | 0.0023492 | 0.98741 | -0.23918 | 0.98737 | -0.24003 | 0.64539
132 | -0.0024084 | -0.00060361 | 0.0024087 | 0.00060305 | 2.8736e-07 | -5.5782e-07 | 0.0036325 | 0.0036322 | 0.0036325 | 0.98659 | -0.25628 | 0.98672 | -0.25378 | 0.99794
133 | -0.0038585 | -0.0009664 | 0.0038588 | 0.00096629 | 2.9893e-07 | -1.0946e-07 | 0.0058186 | 0.0058185 | 0.0058186 | 0.98672 | -0.25378 | 0.9868 | -0.25215 | 1.5985
134 | 0.0041333 | 0.0010353 | -0.0041329 | -0.0010353 | 4.565e-07 | -8.655e-08 | 0.0063195 | 0.0063196 | 0.0063196 | 0.97321 | -0.51582 | 0.9731 | -0.51814 | 1.7362
135 | 0.0010048 | 0.00025148 | -0.0010047 | -0.00025181 | 2.4487e-08 | -3.2814e-07 | 0.0015361 | 0.0015363 | 0.0015363 | 0.97321 | -0.51582 | 0.97319 | -0.51633 | 0.42205
136 | 0.0020066 | 0.00050245 | -0.0020066 | -0.00050254 | 3.2173e-08 | -9.2618e-08 | 0.0030683 | 0.0030683 | 0.0030683 | 0.9731 | -0.51814 | 0.97308 | -0.51847 | 0.84294
137 | 0.0020066 | 0.00050254 | -0.0020065 | -0.00050287 | 1.139e-07 | -3.2784e-07 | 0.0030683 | 0.0030685 | 0.0030685 | 0.97308 | -0.51847 | 0.97302 | -0.51967 | 0.84298
138 | -0.001598 | -0.0004005 | 0.0015982 | 0.0003998 | 1.3333e-07 | -6.9834e-07 | 0.0024087 | 0.0024085 | 0.0024087 | 0.98719 | -0.24455 | 0.98728 | -0.2428 | 0.66174
139 | 0.0078869 | 0.0019754 | -0.0078859 | -0.001975 | 9.9059e-07 | 3.9493e-07 | 0.011887 | 0.011887 | 0.011887 | 0.98728 | -0.2428 | 0.98714 | -0.24543 | 3.2656
140 | -0.009485 | -0.0023752 | 0.0094882 | 0.0023767 | 3.1824e-06 | 1.5055e-06 | 0.014295 | 0.014295 | 0.014295 | 0.98728 | -0.2428 | 0.98764 | -0.23575 | 3.9272
141 | 0.0019963 | 0.00049983 | -0.0019962 | -0.00050029 | 1.4682e-07 | -4.5874e-07 | 0.0030091 | 0.0030093 | 0.0030093 | 0.98714 | -0.24543 | 0.98707 | -0.24698 | 0.82673
142 | 0.0058895 | 0.0014752 | -0.0058887 | -0.001475 | 8.4079e-07 | 1.7447e-07 | 0.0088775 | 0.0088777 | 0.0088777 | 0.98714 | -0.24543 | 0.98699 | -0.24843 | 2.4389
143 | 0.0050687 | 0.0012699 | -0.0050679 | -0.0012699 | 7.7669e-07 | 4.2665e-08 | 0.0076365 | 0.0076367 | 0.0076367 | 0.98764 | -0.23575 | 0.98748 | -0.23897 | 2.098
144 | 0.0058887 | 0.001475 | -0.0058877 | -0.0014748 | 1.0429e-06 | 2.1658e-07 | 0.0088777 | 0.0088778 | 0.0088778 | 0.98699 | -0.24843 | 0.9868 | -0.25215 | 2.439
145 | 0.0035262 | 0.00088352 | -0.0035259 | -0.00088368 | 2.8214e-07 | -1.603e-07 | 0.0053135 | 0.0053136 | 0.0053136 | 0.98748 | -0.23897 | 0.98739 | -0.24065 | 1.4598
146 | 0.0024814 | 0.00062163 | -0.0024813 | -0.00062186 | 1.4443e-07 | -2.3741e-07 | 0.0038014 | 0.0038015 | 0.0038015 | 0.9713 | -0.55366 | 0.97124 | -0.55488 | 1.0444
147 | 0.0013067 | 0.00032717 | -0.0013067 | -0.00032748 | 4.1036e-08 | -3.1189e-07 | 0.0020015 | 0.0020016 | 0.0020016 | 0.97141 | -0.55135 | 0.97138 | -0.55201 | 0.54989

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.30309 | 0.077666

## res_load
| p_mw | q_mvar
0 | 0.00048775 | 0.00012224
1 | 0.00032659 | 8.1852e-05
2 | 0.00040846 | 0.00010237
3 | 0.00061273 | 0.00015357
4 | 0.00049251 | 0.00012344
5 | 0.0013231 | 0.00033161
6 | 0.0002396 | 6.0049e-05
7 | 0.00021548 | 5.4005e-05
8 | 0.00059254 | 0.0001485
9 | 0.00010124 | 2.5372e-05
10 | 0.00064924 | 0.00016271
11 | 0.00014272 | 3.5769e-05
12 | 0.0012681 | 0.00031781
13 | 0.00016462 | 4.1258e-05
14 | 0.00016168 | 4.0522e-05
15 | 0.00041217 | 0.0001033
16 | 0.00036096 | 9.0466e-05
17 | 0.0038058 | 0.00095383
18 | 0.001647 | 0.00041279
19 | 0.0018396 | 0.00046103
20 | 0.0021653 | 0.00054268
21 | 0.0019314 | 0.00048405
22 | 0.0015477 | 0.00038789
23 | 0.0013434 | 0.00033668
24 | 0.002332 | 0.00058445
25 | 0.0021219 | 0.00053181
26 | 0.0013526 | 0.00033898
27 | 0.0014898 | 0.00037337
28 | 0.0010264 | 0.00025725
29 | 0.0010262 | 0.0002572
30 | 0.00090219 | 0.00022611
31 | 0.002366 | 0.00059296
32 | 0.00031457 | 7.8838e-05
33 | 0.00069181 | 0.00017339
34 | 0.00033248 | 8.3327e-05
35 | 0.0034766 | 0.00087133
36 | 0.0004851 | 0.00012158
37 | 0.00052359 | 0.00013123
38 | 0.00088873 | 0.00022274
39 | 0.00020793 | 5.2112e-05
40 | 0.0013486 | 0.000338
41 | 0.00041008 | 0.00010278
42 | 0.00051663 | 0.00012948
43 | 0.044759 | 0.011218
44 | 0.00069033 | 0.00017301
45 | 0.001372 | 0.00034386
46 | 0.00080059 | 0.00020065
47 | 0.0015415 | 0.00038635
48 | 0.0011261 | 0.00028222
49 | 0.0023397 | 0.0005864
50 | 0.0011098 | 0.00027814
51 | 0.0011026 | 0.00027633
52 | 0.001143 | 0.00028647
53 | 0.00096523 | 0.00024191
54 | 0.00054146 | 0.0001357
55 | 0.0014101 | 0.00035341
56 | 0.00083501 | 0.00020927
57 | 0.00088408 | 0.00022157
58 | 0.00093002 | 0.00023309
59 | 0.00080935 | 0.00020284
60 | 0.001401 | 0.00035112
61 | 0.0011859 | 0.00029721
62 | 0.0015424 | 0.00038656
63 | 0.00095784 | 0.00024006
64 | 0.0026914 | 0.00067453
65 | 0.0020174 | 0.00050561
66 | 0.0014981 | 0.00037546
67 | 0.0013835 | 0.00034674
68 | 0.0013213 | 0.00033116
69 | 0.001128 | 0.00028272
70 | 0.00096656 | 0.00024224
71 | 0.0017656 | 0.0004425
72 | 0.0021347 | 0.00053502
73 | 0.012339 | 0.0030926
74 | 0.0014756 | 0.00036982
75 | 0.0022745 | 0.00057004
76 | 0.0020629 | 0.00051701
77 | 0.001479 | 0.00037067
78 | 0.019834 | 0.0049708
79 | 0.00044037 | 0.00011037
80 | 0.0015912 | 0.00039878
81 | 0.0012929 | 0.00032403
82 | 0.001455 | 0.00036466
83 | 0.0016955 | 0.00042492
84 | 0.0014151 | 0.00035466
85 | 0.0016432 | 0.00041184
86 | 0.0016555 | 0.0004149
87 | 0.00034946 | 8.7582e-05
88 | 0.00038307 | 9.6005e-05
89 | 0.00041889 | 0.00010498
90 | 0.0077187 | 0.0019345
91 | 0.003749 | 0.00093959
92 | 0.070762 | 0.017735
93 | 0.0011656 | 0.00029213
94 | 0.001584 | 0.00039698
95 | 0.0015588 | 0.00039068
96 | 0.0018802 | 0.00047123
97 | 0.0015069 | 0.00037768
98 | 0.0024084 | 0.00060361
99 | 0.0014498 | 0.00036335
100 | 0.0021263 | 0.00053289
101 | 0.0010047 | 0.00025181
102 | 0.0020065 | 0.00050287
103 | 0.001598 | 0.0004005
104 | 0.0019962 | 0.00050029
105 | 0.0015417 | 0.00038639
106 | 0.0020289 | 0.00050848
107 | 0.0035259 | 0.00088368
108 | 0.0029595 | 0.00074172
109 | 0.0024813 | 0.00062186
110 | 0.0011011 | 0.00027597
111 | 0.0013067 | 0.00032748

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1