## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2621-3_0_10_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2621-3_0_10_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2621-3_0_10_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2621-3_0_10_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2621-3_0_10_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2621-3_0_10_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2621-3_0_10_node_145 | 0.4 | n |  | TRUE
7 | bus_LV_2621-3_0_10_node_143 | 0.4 | n |  | TRUE
8 | bus_LV_2621-3_0_10_node_144 | 0.4 | n |  | TRUE
9 | bus_LV_2621-3_0_10_node_57 | 0.4 | n |  | TRUE
10 | bus_LV_2621-3_0_10_node_43 | 0.4 | n |  | TRUE
11 | bus_LV_2621-3_0_10_node_86 | 0.4 | n |  | TRUE
12 | bus_LV_2621-3_0_10_node_56 | 0.4 | n |  | TRUE
13 | bus_LV_2621-3_0_10_node_41 | 0.4 | n |  | TRUE
14 | bus_LV_2621-3_0_10_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_2621-3_0_10_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_2621-3_0_10_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_2621-3_0_10_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2621-3_0_10_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2621-3_0_10_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2621-3_0_10_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_2621-3_0_10_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_2621-3_0_10_node_108 | 0.4 | n |  | TRUE
23 | bus_LV_2621-3_0_10_node_105 | 0.4 | n |  | TRUE
24 | bus_LV_2621-3_0_10_node_138 | 0.4 | n |  | TRUE
25 | bus_LV_2621-3_0_10_node_124 | 0.4 | n |  | TRUE
26 | bus_LV_2621-3_0_10_node_106 | 0.4 | n |  | TRUE
27 | bus_LV_2621-3_0_10_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_2621-3_0_10_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_2621-3_0_10_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_2621-3_0_10_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_2621-3_0_10_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_2621-3_0_10_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_2621-3_0_10_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_2621-3_0_10_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_2621-3_0_10_node_79 | 0.4 | n |  | TRUE
36 | bus_LV_2621-3_0_10_node_58 | 0.4 | n |  | TRUE
37 | bus_LV_2621-3_0_10_node_59 | 0.4 | n |  | TRUE
38 | bus_LV_2621-3_0_10_node_60 | 0.4 | n |  | TRUE
39 | bus_LV_2621-3_0_10_node_133 | 0.4 | n |  | TRUE
40 | bus_LV_2621-3_0_10_node_61 | 0.4 | n |  | TRUE
41 | bus_LV_2621-3_0_10_node_62 | 0.4 | n |  | TRUE
42 | bus_LV_2621-3_0_10_node_63 | 0.4 | n |  | TRUE
43 | bus_LV_2621-3_0_10_node_64 | 0.4 | n |  | TRUE
44 | bus_LV_2621-3_0_10_node_65 | 0.4 | n |  | TRUE
45 | bus_LV_2621-3_0_10_node_66 | 0.4 | n |  | TRUE
46 | bus_LV_2621-3_0_10_node_67 | 0.4 | n |  | TRUE
47 | bus_LV_2621-3_0_10_node_113 | 0.4 | n |  | TRUE
48 | bus_LV_2621-3_0_10_node_68 | 0.4 | n |  | TRUE
49 | bus_LV_2621-3_0_10_node_77 | 0.4 | n |  | TRUE
50 | bus_LV_2621-3_0_10_node_78 | 0.4 | n |  | TRUE
51 | bus_LV_2621-3_0_10_node_111 | 0.4 | n |  | TRUE
52 | bus_LV_2621-3_0_10_node_112 | 0.4 | n |  | TRUE
53 | bus_LV_2621-3_0_10_node_114 | 0.4 | n |  | TRUE
54 | bus_LV_2621-3_0_10_node_115 | 0.4 | n |  | TRUE
55 | bus_LV_2621-3_0_10_node_130 | 0.4 | n |  | TRUE
56 | bus_LV_2621-3_0_10_node_132 | 0.4 | n |  | TRUE
57 | bus_LV_2621-3_0_10_node_21 | 0.4 | n |  | TRUE
58 | bus_LV_2621-3_0_10_node_22 | 0.4 | n |  | TRUE
59 | bus_LV_2621-3_0_10_node_94 | 0.4 | n |  | TRUE
60 | bus_LV_2621-3_0_10_node_140 | 0.4 | n |  | TRUE
61 | bus_LV_2621-3_0_10_node_92 | 0.4 | n |  | TRUE
62 | bus_LV_2621-3_0_10_node_141 | 0.4 | n |  | TRUE
63 | bus_LV_2621-3_0_10_node_24 | 0.4 | n |  | TRUE
64 | bus_LV_2621-3_0_10_node_25 | 0.4 | n |  | TRUE
65 | bus_LV_2621-3_0_10_node_26 | 0.4 | n |  | TRUE
66 | bus_LV_2621-3_0_10_node_27 | 0.4 | n |  | TRUE
67 | bus_LV_2621-3_0_10_node_28 | 0.4 | n |  | TRUE
68 | bus_LV_2621-3_0_10_node_29 | 0.4 | n |  | TRUE
69 | bus_LV_2621-3_0_10_node_30 | 0.4 | n |  | TRUE
70 | bus_LV_2621-3_0_10_node_31 | 0.4 | n |  | TRUE
71 | bus_LV_2621-3_0_10_node_75 | 0.4 | n |  | TRUE
72 | bus_LV_2621-3_0_10_node_69 | 0.4 | n |  | TRUE
73 | bus_LV_2621-3_0_10_node_96 | 0.4 | n |  | TRUE
74 | bus_LV_2621-3_0_10_node_51 | 0.4 | n |  | TRUE
75 | bus_LV_2621-3_0_10_node_70 | 0.4 | n |  | TRUE
76 | bus_LV_2621-3_0_10_node_71 | 0.4 | n |  | TRUE
77 | bus_LV_2621-3_0_10_node_32 | 0.4 | n |  | TRUE
78 | bus_LV_2621-3_0_10_node_33 | 0.4 | n |  | TRUE
79 | bus_LV_2621-3_0_10_node_34 | 0.4 | n |  | TRUE
80 | bus_LV_2621-3_0_10_node_35 | 0.4 | n |  | TRUE
81 | bus_LV_2621-3_0_10_node_36 | 0.4 | n |  | TRUE
82 | bus_LV_2621-3_0_10_node_37 | 0.4 | n |  | TRUE
83 | bus_LV_2621-3_0_10_node_38 | 0.4 | n |  | TRUE
84 | bus_LV_2621-3_0_10_node_39 | 0.4 | n |  | TRUE
85 | bus_LV_2621-3_0_10_node_40 | 0.4 | n |  | TRUE
86 | bus_LV_2621-3_0_10_node_42 | 0.4 | n |  | TRUE
87 | bus_LV_2621-3_0_10_node_44 | 0.4 | n |  | TRUE
88 | bus_LV_2621-3_0_10_node_45 | 0.4 | n |  | TRUE
89 | bus_LV_2621-3_0_10_node_46 | 0.4 | n |  | TRUE
90 | bus_LV_2621-3_0_10_node_47 | 0.4 | n |  | TRUE
91 | bus_LV_2621-3_0_10_node_48 | 0.4 | n |  | TRUE
92 | bus_LV_2621-3_0_10_node_49 | 0.4 | n |  | TRUE
93 | bus_LV_2621-3_0_10_node_50 | 0.4 | n |  | TRUE
94 | bus_LV_2621-3_0_10_node_52 | 0.4 | n |  | TRUE
95 | bus_LV_2621-3_0_10_node_53 | 0.4 | n |  | TRUE
96 | bus_LV_2621-3_0_10_node_55 | 0.4 | n |  | TRUE
97 | bus_LV_2621-3_0_10_node_54 | 0.4 | n |  | TRUE
98 | bus_LV_2621-3_0_10_node_76 | 0.4 | n |  | TRUE
99 | bus_LV_2621-3_0_10_node_127 | 0.4 | n |  | TRUE
100 | bus_LV_2621-3_0_10_node_87 | 0.4 | n |  | TRUE
101 | bus_LV_2621-3_0_10_node_72 | 0.4 | n |  | TRUE
102 | bus_LV_2621-3_0_10_node_73 | 0.4 | n |  | TRUE
103 | bus_LV_2621-3_0_10_node_74 | 0.4 | n |  | TRUE
104 | bus_LV_2621-3_0_10_node_109 | 0.4 | n |  | TRUE
105 | bus_LV_2621-3_0_10_node_139 | 0.4 | n |  | TRUE
106 | bus_LV_2621-3_0_10_node_110 | 0.4 | n |  | TRUE
107 | bus_LV_2621-3_0_10_node_97 | 0.4 | n |  | TRUE
108 | bus_LV_2621-3_0_10_node_126 | 0.4 | n |  | TRUE
109 | bus_LV_2621-3_0_10_node_80 | 0.4 | n |  | TRUE
110 | bus_LV_2621-3_0_10_node_81 | 0.4 | n |  | TRUE
111 | bus_LV_2621-3_0_10_node_82 | 0.4 | n |  | TRUE
112 | bus_LV_2621-3_0_10_node_83 | 0.4 | n |  | TRUE
113 | bus_LV_2621-3_0_10_node_84 | 0.4 | n |  | TRUE
114 | bus_LV_2621-3_0_10_node_85 | 0.4 | n |  | TRUE
115 | bus_LV_2621-3_0_10_node_101 | 0.4 | n |  | TRUE
116 | bus_LV_2621-3_0_10_node_98 | 0.4 | n |  | TRUE
117 | bus_LV_2621-3_0_10_node_103 | 0.4 | n |  | TRUE
118 | bus_LV_2621-3_0_10_node_99 | 0.4 | n |  | TRUE
119 | bus_LV_2621-3_0_10_node_88 | 0.4 | n |  | TRUE
120 | bus_LV_2621-3_0_10_node_89 | 0.4 | n |  | TRUE
121 | bus_LV_2621-3_0_10_node_135 | 0.4 | n |  | TRUE
122 | bus_LV_2621-3_0_10_node_136 | 0.4 | n |  | TRUE
123 | bus_LV_2621-3_0_10_node_90 | 0.4 | n |  | TRUE
124 | bus_LV_2621-3_0_10_node_91 | 0.4 | n |  | TRUE
125 | bus_LV_2621-3_0_10_node_93 | 0.4 | n |  | TRUE
126 | bus_LV_2621-3_0_10_node_95 | 0.4 | n |  | TRUE
127 | bus_LV_2621-3_0_10_node_104 | 0.4 | n |  | TRUE
128 | bus_LV_2621-3_0_10_node_134 | 0.4 | n |  | TRUE
129 | bus_LV_2621-3_0_10_node_100 | 0.4 | n |  | TRUE
130 | bus_LV_2621-3_0_10_node_102 | 0.4 | n |  | TRUE
131 | bus_LV_2621-3_0_10_node_129 | 0.4 | n |  | TRUE
132 | bus_LV_2621-3_0_10_node_125 | 0.4 | n |  | TRUE
133 | bus_LV_2621-3_0_10_node_128 | 0.4 | n |  | TRUE
134 | bus_LV_2621-3_0_10_node_107 | 0.4 | n |  | TRUE
135 | bus_LV_2621-3_0_10_node_122 | 0.4 | n |  | TRUE
136 | bus_LV_2621-3_0_10_node_116 | 0.4 | n |  | TRUE
137 | bus_LV_2621-3_0_10_node_117 | 0.4 | n |  | TRUE
138 | bus_LV_2621-3_0_10_node_118 | 0.4 | n |  | TRUE
139 | bus_LV_2621-3_0_10_node_119 | 0.4 | n |  | TRUE
140 | bus_LV_2621-3_0_10_node_120 | 0.4 | n |  | TRUE
141 | bus_LV_2621-3_0_10_node_121 | 0.4 | n |  | TRUE
142 | bus_LV_2621-3_0_10_node_123 | 0.4 | n |  | TRUE
143 | bus_LV_2621-3_0_10_node_142 | 0.4 | n |  | TRUE
144 | bus_MV_287_0_node_16 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2621-3_0_10_load_0 | 0 | 0.00095351 | 0.00023897 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2621-3_0_10_load_2 | 2 | 0.0018865 | 0.00047281 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2621-3_0_10_load_4 | 3 | 0.0026475 | 0.00066352 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2621-3_0_10_load_143 | 7 | 0.004317 | 0.0010819 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2621-3_0_10_load_144 | 8 | 0.0060399 | 0.0015137 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2621-3_0_10_load_57 | 9 | 0.0038721 | 0.00097043 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2621-3_0_10_load_86 | 11 | 0.0028132 | 0.00070506 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2621-3_0_10_load_56 | 12 | 0.0021982 | 0.00055092 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2621-3_0_10_load_41 | 13 | 0.0040292 | 0.0010098 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2621-3_0_10_load_6 | 14 | 0.0013385 | 0.00033546 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2621-3_0_10_load_7 | 15 | 0.00059859 | 0.00015002 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2621-3_0_10_load_10 | 18 | 0.00093054 | 0.00023322 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2621-3_0_10_load_11 | 19 | 0.0024641 | 0.00061756 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2621-3_0_10_load_12 | 20 | 0.0026327 | 0.00065981 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2621-3_0_10_load_13 | 21 | 0.0010548 | 0.00026435 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2621-3_0_10_load_105 | 23 | 0.00092667 | 0.00023225 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2621-3_0_10_load_138 | 24 | 0.002461 | 0.00061678 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2621-3_0_10_load_124 | 25 | 0.0038919 | 0.0009754 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2621-3_0_10_load_106 | 26 | 0.00097192 | 0.00024359 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2621-3_0_10_load_14 | 27 | 0.0018826 | 0.00047183 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2621-3_0_10_load_16 | 30 | 0.00029187 | 7.315e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2621-3_0_10_load_17 | 31 | 0.00058719 | 0.00014716 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2621-3_0_10_load_19 | 32 | 0.019726 | 0.0049438 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2621-3_0_10_load_20 | 33 | 0.011587 | 0.0029039 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2621-3_0_10_load_23 | 34 | 0.0091469 | 0.0022924 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2621-3_0_10_load_58 | 36 | 0.010219 | 0.0025612 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2621-3_0_10_load_59 | 37 | 0.041829 | 0.010483 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2621-3_0_10_load_60 | 38 | 0.072994 | 0.018294 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2621-3_0_10_load_133 | 39 | 0.0082367 | 0.0020643 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2621-3_0_10_load_62 | 41 | 0.037938 | 0.0095081 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2621-3_0_10_load_63 | 42 | 0.0010005 | 0.00025075 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2621-3_0_10_load_64 | 43 | 0.00060582 | 0.00015183 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2621-3_0_10_load_65 | 44 | 0.0035938 | 0.00090069 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2621-3_0_10_load_66 | 45 | 0.00016352 | 4.0983e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2621-3_0_10_load_67 | 46 | 0.00017633 | 4.4193e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2621-3_0_10_load_113 | 47 | 0.0020207 | 0.00050642 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2621-3_0_10_load_68 | 48 | 0.00057993 | 0.00014535 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2621-3_0_10_load_77 | 49 | 0.00015368 | 3.8515e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2621-3_0_10_load_111 | 51 | 0.0019537 | 0.00048965 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2621-3_0_10_load_114 | 53 | 0.0017484 | 0.00043818 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2621-3_0_10_load_115 | 54 | 0.0040462 | 0.0010141 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2621-3_0_10_load_130 | 55 | 0.029626 | 0.0074249 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2621-3_0_10_load_21 | 57 | 0.00031654 | 7.9331e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2621-3_0_10_load_22 | 58 | 0.00061795 | 0.00015487 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2621-3_0_10_load_94 | 59 | 0.00062386 | 0.00015636 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2621-3_0_10_load_140 | 60 | 0.00038452 | 9.6371e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2621-3_0_10_load_92 | 61 | 0.00054958 | 0.00013774 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2621-3_0_10_load_141 | 62 | 0.00046254 | 0.00011592 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2621-3_0_10_load_24 | 63 | 0.0021822 | 0.00054692 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2621-3_0_10_load_25 | 64 | 0.001522 | 0.00038146 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2621-3_0_10_load_26 | 65 | 0.00045073 | 0.00011296 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2621-3_0_10_load_28 | 67 | 0.00028994 | 7.2665e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2621-3_0_10_load_29 | 68 | 0.0018458 | 0.00046259 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2621-3_0_10_load_30 | 69 | 0.003177 | 0.00079622 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2621-3_0_10_load_31 | 70 | 0.00218 | 0.00054636 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2621-3_0_10_load_96 | 73 | 0.0024141 | 0.00060502 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2621-3_0_10_load_51 | 74 | 0.0010764 | 0.00026976 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2621-3_0_10_load_70 | 75 | 0.003671 | 0.00092004 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2621-3_0_10_load_32 | 77 | 0.00048856 | 0.00012245 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2621-3_0_10_load_33 | 78 | 0.0021523 | 0.00053943 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2621-3_0_10_load_34 | 79 | 0.00048856 | 0.00012245 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2621-3_0_10_load_35 | 80 | 0.00038837 | 9.7334e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2621-3_0_10_load_36 | 81 | 0.00812 | 0.0020351 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2621-3_0_10_load_37 | 82 | 0.0068556 | 0.0017182 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2621-3_0_10_load_38 | 83 | 0.00088968 | 0.00022298 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2621-3_0_10_load_39 | 84 | 0.0022347 | 0.00056007 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2621-3_0_10_load_40 | 85 | 0.0012058 | 0.00030219 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2621-3_0_10_load_42 | 86 | 0.0006741 | 0.00016894 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2621-3_0_10_load_44 | 87 | 0.0039723 | 0.00099555 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2621-3_0_10_load_45 | 88 | 0.0013859 | 0.00034735 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2621-3_0_10_load_48 | 91 | 0.0023183 | 0.00058103 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2621-3_0_10_load_49 | 92 | 0.0016678 | 0.000418 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2621-3_0_10_load_50 | 93 | 0.0020316 | 0.00050917 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2621-3_0_10_load_52 | 94 | 0.0012718 | 0.00031875 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2621-3_0_10_load_53 | 95 | 0.00078618 | 0.00019704 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2621-3_0_10_load_54 | 97 | 0.0021137 | 0.00052975 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2621-3_0_10_load_76 | 98 | 0.0010199 | 0.0002556 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2621-3_0_10_load_127 | 99 | 0.001438 | 0.0003604 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2621-3_0_10_load_87 | 100 | 0.0076908 | 0.0019275 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2621-3_0_10_load_72 | 101 | 0.0019712 | 0.00049402 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2621-3_0_10_load_74 | 103 | 0.0015654 | 0.00039232 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2621-3_0_10_load_109 | 104 | 0.0026334 | 0.00065999 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2621-3_0_10_load_139 | 105 | 0.0071189 | 0.0017842 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2621-3_0_10_load_97 | 107 | 0.00085194 | 0.00021352 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2621-3_0_10_load_126 | 108 | 0.00060273 | 0.00015106 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2621-3_0_10_load_80 | 109 | 0.0024655 | 0.00061791 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2621-3_0_10_load_81 | 110 | 0.0024694 | 0.0006189 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2621-3_0_10_load_82 | 111 | 0.0059673 | 0.0014955 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2621-3_0_10_load_85 | 114 | 0.0024618 | 0.00061699 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2621-3_0_10_load_101 | 115 | 0.0017888 | 0.00044831 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2621-3_0_10_load_98 | 116 | 0.0011951 | 0.00029953 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2621-3_0_10_load_103 | 117 | 0.0022992 | 0.00057623 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2621-3_0_10_load_99 | 118 | 0.0045339 | 0.0011363 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2621-3_0_10_load_88 | 119 | 0.0023918 | 0.00059943 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2621-3_0_10_load_135 | 121 | 0.0082845 | 0.0020763 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2621-3_0_10_load_136 | 122 | 0.0039743 | 0.00099606 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2621-3_0_10_load_90 | 123 | 0.00064462 | 0.00016156 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2621-3_0_10_load_91 | 124 | 0.00038814 | 9.7278e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2621-3_0_10_load_93 | 125 | 0.0030729 | 0.00077013 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2621-3_0_10_load_95 | 126 | 0.00092329 | 0.0002314 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2621-3_0_10_load_104 | 127 | 0.0011386 | 0.00028536 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2621-3_0_10_load_134 | 128 | 0.0014521 | 0.00036393 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2621-3_0_10_load_100 | 129 | 0.00093585 | 0.00023455 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2621-3_0_10_load_102 | 130 | 0.00090251 | 0.00022619 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2621-3_0_10_load_128 | 133 | 0.0044841 | 0.0011238 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2621-3_0_10_load_107 | 134 | 0.0010913 | 0.00027351 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2621-3_0_10_load_122 | 135 | 0.0028912 | 0.00072459 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2621-3_0_10_load_116 | 136 | 0.010555 | 0.0026454 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2621-3_0_10_load_117 | 137 | 0.0008094 | 0.00020285 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2621-3_0_10_load_118 | 138 | 0.0098724 | 0.0024743 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2621-3_0_10_load_119 | 139 | 0.00097616 | 0.00024465 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2621-3_0_10_load_120 | 140 | 0.00091362 | 0.00022897 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2621-3_0_10_load_121 | 141 | 0.0016666 | 0.00041769 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2621-3_0_10_load_123 | 142 | 0.0016665 | 0.00041765 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2621-3_0_10_load_142 | 143 | 0.00036551 | 9.1607e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 123 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2621-3_0_10_line_0 |  | 0 | 1 | 0.09417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2621-3_0_10_line_1 |  | 1 | 2 | 0.063918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
2 | LV_2621-3_0_10_line_2 |  | 1 | 3 | 0.12785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
3 | LV_2621-3_0_10_line_3 |  | 2 | 4 | 0.018591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_2621-3_0_10_line_4 |  | 3 | 5 | 0.020141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
5 | LV_2621-3_0_10_line_5 |  | 4 | 9 | 0.0047835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2621-3_0_10_line_6 |  | 4 | 10 | 0.013538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2621-3_0_10_line_7 |  | 5 | 6 | 0.035218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_2621-3_0_10_line_8 |  | 6 | 7 | 0.21893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_2621-3_0_10_line_9 |  | 7 | 8 | 0.011503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_2621-3_0_10_line_10 |  | 8 | 106 | 0.39983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_2621-3_0_10_line_11 |  | 9 | 11 | 0.011262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2621-3_0_10_line_12 |  | 10 | 12 | 0.0395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2621-3_0_10_line_13 |  | 10 | 13 | 0.015095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2621-3_0_10_line_14 |  | 11 | 100 | 0.013578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2621-3_0_10_line_15 |  | 12 | 81 | 0.013006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2621-3_0_10_line_16 |  | 13 | 84 | 0.01483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2621-3_0_10_line_17 |  | 14 | 15 | 0.030607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2621-3_0_10_line_18 |  | 14 | 16 | 0.045539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2621-3_0_10_line_19 |  | 15 | 17 | 0.074704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2621-3_0_10_line_20 |  | 16 | 18 | 0.063691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2621-3_0_10_line_21 |  | 17 | 19 | 0.032476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2621-3_0_10_line_22 |  | 17 | 20 | 0.0050936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2621-3_0_10_line_23 |  | 18 | 21 | 0.020879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2621-3_0_10_line_24 |  | 19 | 22 | 0.006717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2621-3_0_10_line_25 |  | 20 | 23 | 0.033536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2621-3_0_10_line_26 |  | 22 | 24 | 0.016111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2621-3_0_10_line_27 |  | 22 | 25 | 0.024129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2621-3_0_10_line_28 |  | 23 | 26 | 0.020838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2621-3_0_10_line_29 |  | 24 | 114 | 0.025298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2621-3_0_10_line_30 |  | 25 | 135 | 0.015168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2621-3_0_10_line_31 |  | 26 | 134 | 0.0062822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2621-3_0_10_line_32 |  | 27 | 28 | 0.043544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_2621-3_0_10_line_33 |  | 27 | 29 | 0.13959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_2621-3_0_10_line_34 |  | 28 | 30 | 0.023895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_2621-3_0_10_line_35 |  | 28 | 31 | 0.029845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2621-3_0_10_line_36 |  | 29 | 32 | 0.036081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_2621-3_0_10_line_37 |  | 29 | 33 | 0.016383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2621-3_0_10_line_38 |  | 30 | 57 | 0.0032629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_2621-3_0_10_line_39 |  | 31 | 58 | 0.035651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2621-3_0_10_line_40 |  | 32 | 34 | 0.015643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_2621-3_0_10_line_41 |  | 34 | 35 | 0.10434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_2621-3_0_10_line_42 |  | 35 | 41 | 0.03657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_2621-3_0_10_line_43 |  | 35 | 50 | 0.05925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2621-3_0_10_line_44 |  | 36 | 37 | 0.016702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2621-3_0_10_line_45 |  | 36 | 38 | 0.058962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_2621-3_0_10_line_46 |  | 36 | 39 | 0.12215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_2621-3_0_10_line_47 |  | 38 | 40 | 0.025925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_2621-3_0_10_line_48 |  | 39 | 56 | 0.014793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_2621-3_0_10_line_49 |  | 40 | 41 | 0.019524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_2621-3_0_10_line_50 |  | 42 | 43 | 0.016457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2621-3_0_10_line_51 |  | 42 | 44 | 0.013933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2621-3_0_10_line_52 |  | 43 | 45 | 0.039904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2621-3_0_10_line_53 |  | 44 | 46 | 0.031483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2621-3_0_10_line_54 |  | 45 | 47 | 0.18113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2621-3_0_10_line_55 |  | 46 | 48 | 0.01264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2621-3_0_10_line_56 |  | 47 | 51 | 0.026579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2621-3_0_10_line_57 |  | 48 | 49 | 0.014192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2621-3_0_10_line_58 |  | 49 | 50 | 0.0025295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2621-3_0_10_line_59 |  | 51 | 52 | 0.032318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2621-3_0_10_line_60 |  | 52 | 53 | 0.032187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2621-3_0_10_line_61 |  | 53 | 54 | 0.0029104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2621-3_0_10_line_62 |  | 55 | 56 | 0.054175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_2621-3_0_10_line_63 |  | 57 | 59 | 0.018407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_2621-3_0_10_line_64 |  | 58 | 60 | 0.01924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2621-3_0_10_line_65 |  | 59 | 61 | 0.0092425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_2621-3_0_10_line_66 |  | 60 | 62 | 0.011014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2621-3_0_10_line_67 |  | 61 | 123 | 0.0091843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_2621-3_0_10_line_68 |  | 62 | 143 | 0.00053336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2621-3_0_10_line_69 |  | 63 | 64 | 0.0061512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2621-3_0_10_line_70 |  | 63 | 65 | 0.012916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2621-3_0_10_line_71 |  | 64 | 66 | 0.012156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2621-3_0_10_line_72 |  | 65 | 67 | 0.0092227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2621-3_0_10_line_73 |  | 66 | 68 | 0.056025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_2621-3_0_10_line_74 |  | 66 | 69 | 0.044895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
75 | LV_2621-3_0_10_line_75 |  | 67 | 70 | 0.015967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2621-3_0_10_line_76 |  | 68 | 71 | 0.026956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_2621-3_0_10_line_77 |  | 69 | 72 | 0.0059094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_2621-3_0_10_line_78 |  | 71 | 73 | 0.032463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2621-3_0_10_line_79 |  | 71 | 74 | 0.016338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
80 | LV_2621-3_0_10_line_80 |  | 72 | 75 | 0.017398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_2621-3_0_10_line_81 |  | 72 | 76 | 0.04215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2621-3_0_10_line_82 |  | 73 | 107 | 0.058822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2621-3_0_10_line_83 |  | 74 | 90 | 0.012119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
84 | LV_2621-3_0_10_line_84 |  | 75 | 101 | 0.0084586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_2621-3_0_10_line_85 |  | 76 | 102 | 0.026699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2621-3_0_10_line_86 |  | 76 | 103 | 0.021379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2621-3_0_10_line_87 |  | 77 | 78 | 0.019724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2621-3_0_10_line_88 |  | 77 | 79 | 0.007989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2621-3_0_10_line_89 |  | 78 | 80 | 0.021628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2621-3_0_10_line_90 |  | 80 | 81 | 0.039398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2621-3_0_10_line_91 |  | 82 | 83 | 0.0058841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2621-3_0_10_line_92 |  | 82 | 84 | 0.0032569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2621-3_0_10_line_93 |  | 83 | 85 | 0.0028257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2621-3_0_10_line_94 |  | 85 | 86 | 0.007675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2621-3_0_10_line_95 |  | 87 | 88 | 0.0078928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_2621-3_0_10_line_96 |  | 87 | 89 | 0.01597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_2621-3_0_10_line_97 |  | 88 | 90 | 0.019807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_2621-3_0_10_line_98 |  | 89 | 91 | 0.017579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
99 | LV_2621-3_0_10_line_99 |  | 89 | 92 | 0.0081818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2621-3_0_10_line_100 |  | 90 | 93 | 0.0023696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2621-3_0_10_line_101 |  | 91 | 94 | 0.026636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
102 | LV_2621-3_0_10_line_102 |  | 93 | 95 | 0.016559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2621-3_0_10_line_103 |  | 94 | 96 | 0.0092985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_2621-3_0_10_line_104 |  | 95 | 97 | 0.00093167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2621-3_0_10_line_105 |  | 96 | 98 | 0.020819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
106 | LV_2621-3_0_10_line_106 |  | 98 | 99 | 0.0093647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
107 | LV_2621-3_0_10_line_107 |  | 99 | 108 | 0.022718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
108 | LV_2621-3_0_10_line_108 |  | 100 | 119 | 0.012569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2621-3_0_10_line_109 |  | 101 | 104 | 0.0381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
110 | LV_2621-3_0_10_line_110 |  | 102 | 105 | 0.016567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2621-3_0_10_line_111 |  | 104 | 106 | 0.033834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_2621-3_0_10_line_112 |  | 108 | 133 | 0.027659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
113 | LV_2621-3_0_10_line_113 |  | 109 | 110 | 0.023231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2621-3_0_10_line_114 |  | 109 | 111 | 0.019795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2621-3_0_10_line_115 |  | 111 | 112 | 0.04426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2621-3_0_10_line_116 |  | 112 | 113 | 0.037502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2621-3_0_10_line_117 |  | 112 | 114 | 0.03669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2621-3_0_10_line_118 |  | 113 | 115 | 0.063167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2621-3_0_10_line_119 |  | 113 | 116 | 0.0056195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2621-3_0_10_line_120 |  | 115 | 117 | 0.015555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2621-3_0_10_line_121 |  | 116 | 118 | 0.038078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2621-3_0_10_line_122 |  | 118 | 129 | 0.002401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2621-3_0_10_line_123 |  | 119 | 120 | 0.008875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2621-3_0_10_line_124 |  | 120 | 121 | 0.0074903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2621-3_0_10_line_125 |  | 121 | 122 | 0.015766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2621-3_0_10_line_126 |  | 123 | 124 | 0.018826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
127 | LV_2621-3_0_10_line_127 |  | 124 | 125 | 0.026161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
128 | LV_2621-3_0_10_line_128 |  | 125 | 126 | 0.03714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
129 | LV_2621-3_0_10_line_129 |  | 126 | 127 | 0.00041687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
130 | LV_2621-3_0_10_line_130 |  | 127 | 128 | 0.0078364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
131 | LV_2621-3_0_10_line_131 |  | 128 | 132 | 0.026967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
132 | LV_2621-3_0_10_line_132 |  | 129 | 130 | 0.0080929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2621-3_0_10_line_133 |  | 130 | 131 | 0.038046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2621-3_0_10_line_134 |  | 131 | 132 | 0.025042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
135 | LV_2621-3_0_10_line_135 |  | 131 | 133 | 0.029873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
136 | LV_2621-3_0_10_line_136 |  | 132 | 140 | 0.029323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2621-3_0_10_line_137 |  | 135 | 141 | 0.039139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2621-3_0_10_line_138 |  | 136 | 137 | 0.10514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2621-3_0_10_line_139 |  | 136 | 138 | 0.025639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2621-3_0_10_line_140 |  | 137 | 139 | 0.0064095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2621-3_0_10_line_141 |  | 139 | 140 | 0.017368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2621-3_0_10_line_142 |  | 141 | 142 | 0.022457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2621-3_0_10_trafo_90 | 0.63 MVA 20/0.4 kV | 144 | 123 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2611914.7866 | 1250864.8964 | 2611913.5038 | 1250868.5406 | 2611909.1793 | 1250883.4083 | 2611903.4781 | 1250899.8521 | 2611900.5574 | 1250907.2622 | 2611896.678 | 1250914.7593 | 2611893.7693 | 1250919.968 | 2611889.4847 | 1250926.2858 | 2611879.9118 | 1250938.8637 | 2611872.734 | 1250947.9848
1 | 2611914.7866 | 1250864.8964 | 2611909.6038 | 1250863.6519 | 2611905.5677 | 1250862.6876 | 2611900.7678 | 1250862.4223 | 2611898.0726 | 1250862.7505 | 2611895.2099 | 1250863.801 | 2611891.9689 | 1250865.3511 | 2611888.4017 | 1250867.6677 | 2611879.5483 | 1250875.1883 | 2611876.3586 | 1250877.4834 | 2611873.0573 | 1250878.9333 | 2611869.0399 | 1250879.9482 | 2611863.9067 | 1250880.316 | 2611856.3311 | 1250880.0981
2 | 2611914.7866 | 1250864.8964 | 2612006.0449 | 1250775.3615
3 | 2611837.7478 | 1250879.5635 | 2611856.3311 | 1250880.0981
4 | 2612023.8702 | 1250765.9846 | 2612006.0449 | 1250775.3615
5 | 2611837.7478 | 1250879.5635 | 2611832.976 | 1250879.2292
6 | 2611837.7478 | 1250879.5635 | 2611837.5253 | 1250885.1778 | 2611836.6944 | 1250889.2677 | 2611835.5476 | 1250892.8344
7 | 2612054.512 | 1250748.6352 | 2612044.3704 | 1250754.7187 | 2612023.8702 | 1250765.9846
8 | 2612054.512 | 1250748.6352 | 2612212.8615 | 1250597.4543
9 | 2612212.8615 | 1250597.4543 | 2612219.1976 | 1250591.502 | 2612221.6827 | 1250590.1924
10 | 2612539.2007 | 1250347.1973 | 2612221.6827 | 1250590.1924
11 | 2611821.7412 | 1250878.4421 | 2611832.976 | 1250879.2292
12 | 2611835.5476 | 1250892.8344 | 2611830.5806 | 1250908.3235 | 2611829.5141 | 1250917.0938 | 2611829.7273 | 1250927.5677 | 2611829.0705 | 1250931.4355
13 | 2611835.5476 | 1250892.8344 | 2611849.6551 | 1250898.2049
14 | 2611821.7412 | 1250878.4421 | 2611821.7412 | 1250878.4421 | 2611813.3855 | 1250878.6256 | 2611808.1683 | 1250878.446
15 | 2611821.0402 | 1250941.6608 | 2611825.0595 | 1250936.82 | 2611829.0705 | 1250931.4355 | 2611829.0705 | 1250931.4355
16 | 2611849.6551 | 1250898.2049 | 2611857.7437 | 1250901.284 | 2611862.7978 | 1250904.8329
17 | 2613155.4663 | 1250467.2076 | 2613151.7034 | 1250459.2022 | 2613136.5833 | 1250443.5512
18 | 2613164.9652 | 1250510.6205 | 2613159.7023 | 1250501.2027 | 2613155.3495 | 1250486.3946 | 2613155.9933 | 1250468.3287 | 2613155.4663 | 1250467.2076
19 | 2613087.7994 | 1250387.3036 | 2613100.4015 | 1250406.0991 | 2613136.5833 | 1250443.5512
20 | 2613164.9652 | 1250510.6205 | 2613160.2569 | 1250509.8095 | 2613154.9687 | 1250508.4192 | 2613105.7735 | 1250487.5316
21 | 2613087.7994 | 1250387.3036 | 2613067.828 | 1250361.6941
22 | 2613087.7994 | 1250387.3036 | 2613091.2028 | 1250387.7002 | 2613092.8104 | 1250388.1419
23 | 2613086.5552 | 1250479.3718 | 2613105.7735 | 1250487.5316
24 | 2613063.6973 | 1250356.3973 | 2613067.828 | 1250361.6941
25 | 2613092.8104 | 1250388.1419 | 2613096.3024 | 1250389.1012 | 2613116.0976 | 1250394.4038 | 2613123.7981 | 1250397.3004 | 2613124.8417 | 1250397.8801
26 | 2613063.6973 | 1250356.3973 | 2613053.261 | 1250344.1238
27 | 2613063.6973 | 1250356.3973 | 2613062.0032 | 1250357.9057 | 2613056.0977 | 1250359.1046 | 2613051.8018 | 1250359.5065 | 2613040.2962 | 1250358.934
28 | 2613124.8417 | 1250397.8801 | 2613129.2037 | 1250400.3032 | 2613138.4001 | 1250406.0049 | 2613142.5784 | 1250408.8019
29 | 2613036.8734 | 1250324.8514 | 2613053.261 | 1250344.1238
30 | 2613025.1431 | 1250358.539 | 2613029.5968 | 1250358.4016 | 2613040.2962 | 1250358.934
31 | 2613147.7989 | 1250412.2964 | 2613142.5784 | 1250408.8019
32 | 2612940.8653 | 1250007.7474 | 2612944.9197 | 1249990.1225 | 2612945.902 | 1249979.251 | 2612946.3048 | 1249971.0576 | 2612945.8965 | 1249964.7305
33 | 2612945.8965 | 1249964.7305 | 2612985.8798 | 1249830.9864
34 | 2612940.8653 | 1250007.7474 | 2612936.1008 | 1250031.1629
35 | 2612940.8653 | 1250007.7474 | 2612948.8026 | 1250016.6037 | 2612961.8348 | 1250028.9506
36 | 2612985.8798 | 1249830.9864 | 2613011.7067 | 1249805.7904
37 | 2612985.8798 | 1249830.9864 | 2612974.2974 | 1249819.4001
38 | 2612935.4503 | 1250034.3603 | 2612936.1008 | 1250031.1629
39 | 2612961.8348 | 1250028.9506 | 2612971.5983 | 1250038.2006 | 2612975.1968 | 1250042.7003 | 2612978.8007 | 1250048.2006 | 2612983.7808 | 1250056.715
40 | 2613022.9041 | 1249794.8666 | 2613011.7067 | 1249805.7904
41 | 2613097.5968 | 1249722.0049 | 2613092.6793 | 1249726.7972 | 2613052.1969 | 1249766.2895 | 2613022.9041 | 1249794.8666
42 | 2613097.5968 | 1249722.0049 | 2613088.1042 | 1249713.2005 | 2613071.0205 | 1249696.8859
43 | 2613139.0979 | 1249679.6022 | 2613103.7255 | 1249715.7365 | 2613097.5968 | 1249722.0049
44 | 2613020.5352 | 1249750.5472 | 2613031.5503 | 1249763.1021
45 | 2613020.5352 | 1249750.5472 | 2613014.1692 | 1249743.2913 | 2613022.3149 | 1249719.0824 | 2613038.8566 | 1249702.017
46 | 2613020.5352 | 1249750.5472 | 2612902.8608 | 1249717.7964
47 | 2613056.9007 | 1249683.4017 | 2613038.8566 | 1249702.017
48 | 2612900.5503 | 1249703.1849 | 2612902.8608 | 1249717.7964
49 | 2613056.9007 | 1249683.4017 | 2613071.0205 | 1249696.8859
50 | 2613193.72 | 1249628.6211 | 2613207.0976 | 1249619.0357
51 | 2613193.72 | 1249628.6211 | 2613188.3027 | 1249632.5027 | 2613183.0515 | 1249637.5291
52 | 2613207.0976 | 1249619.0357 | 2613223.4177 | 1249607.342 | 2613239.844 | 1249596.239
53 | 2613183.0515 | 1249637.5291 | 2613160.3078 | 1249659.2993
54 | 2613239.844 | 1249596.239 | 2613361.2035 | 1249730.6961
55 | 2613160.3078 | 1249659.2993 | 2613151.1769 | 1249668.0393
56 | 2613361.2035 | 1249730.6961 | 2613384.986 | 1249718.828
57 | 2613140.925 | 1249677.8529 | 2613143.8716 | 1249675.032 | 2613151.1769 | 1249668.0393
58 | 2613139.0979 | 1249679.6022 | 2613140.925 | 1249677.8529
59 | 2613413.9034 | 1249704.3976 | 2613384.986 | 1249718.828
60 | 2613413.9034 | 1249704.3976 | 2613413.8023 | 1249712.4025 | 2613413.7979 | 1249717.7059 | 2613414.7984 | 1249722.6003 | 2613416.3969 | 1249726.8066 | 2613418.8021 | 1249731.5039 | 2613421.1165 | 1249734.8947
61 | 2613421.1165 | 1249734.8947 | 2613421.8043 | 1249735.9024 | 2613423.0144 | 1249737.0825
62 | 2612900.5503 | 1249703.1849 | 2612900.6321 | 1249665.4384 | 2612898.5151 | 1249649.1474
63 | 2612935.4503 | 1250034.3603 | 2612934.0972 | 1250041.0098 | 2612933.6684 | 1250052.6231
64 | 2612983.7808 | 1250056.715 | 2612993.4947 | 1250073.3228
65 | 2612933.3273 | 1250061.8593 | 2612933.6684 | 1250052.6231
66 | 2612999.0554 | 1250082.8299 | 2612993.4947 | 1250073.3228
67 | 2612932.9884 | 1250071.0374 | 2612933.3273 | 1250061.8593
68 | 2612999.0554 | 1250082.8299 | 2612999.3247 | 1250083.2903
69 | 2612688.1975 | 1250351.2592 | 2612685.3077 | 1250345.8291
70 | 2612694.2651 | 1250362.661 | 2612688.1975 | 1250351.2592
71 | 2612679.5968 | 1250335.0977 | 2612685.3077 | 1250345.8291
72 | 2612694.2651 | 1250362.661 | 2612698.5979 | 1250370.8027
73 | 2612679.5968 | 1250335.0977 | 2612689.4026 | 1250331.4051 | 2612696.7983 | 1250328.6969 | 2612703.6035 | 1250326.7991 | 2612714.1989 | 1250324.498 | 2612724.4986 | 1250322.7966 | 2612733.7274 | 1250321.4614
74 | 2612679.5968 | 1250335.0977 | 2612676.4013 | 1250336.3028 | 2612655.1029 | 1250345.3968 | 2612649.2029 | 1250347.5968 | 2612643.9989 | 1250349.0978 | 2612638.1988 | 1250350.4975 | 2612637.562 | 1250350.5768
75 | 2612706.0988 | 1250384.8977 | 2612698.5979 | 1250370.8027
76 | 2612760.6017 | 1250319.8053 | 2612758.3973 | 1250319.9006 | 2612750.0034 | 1250319.9049 | 2612742.8011 | 1250320.4009 | 2612734.7978 | 1250321.3066 | 2612733.7274 | 1250321.4614
77 | 2612631.6979 | 1250351.3065 | 2612637.562 | 1250350.5768
78 | 2612760.6017 | 1250319.8053 | 2612760.8001 | 1250322.2962 | 2612760.3041 | 1250324.7968 | 2612759.6019 | 1250328.3976 | 2612754.2026 | 1250343.4958 | 2612752.0582 | 1250350.9031
79 | 2612760.6017 | 1250319.8053 | 2612765.501 | 1250319.6045 | 2612770.1977 | 1250318.903 | 2612774.601 | 1250317.7006 | 2612776.5633 | 1250316.8961
80 | 2612631.6979 | 1250351.3065 | 2612628.7685 | 1250351.5782 | 2612624.3971 | 1250352.0026 | 2612614.4815 | 1250353.7274
81 | 2612609.4455 | 1250315.525 | 2612612.1979 | 1250320.4007 | 2612622.1982 | 1250335.2982 | 2612627.9014 | 1250344.0048 | 2612629.9994 | 1250347.8006 | 2612631.6979 | 1250351.3065
82 | 2612729.3344 | 1250405.0334 | 2612733.101 | 1250398.1973 | 2612736.8019 | 1250390.1 | 2612743.5984 | 1250374.6044 | 2612747.9992 | 1250363.9959 | 2612750.9022 | 1250354.8962 | 2612752.0582 | 1250350.9031
83 | 2612787.5968 | 1250311.9025 | 2612782.3979 | 1250314.5041 | 2612776.5633 | 1250316.8961
84 | 2612614.4815 | 1250353.7274 | 2612612.9041 | 1250354.0017 | 2612606.2476 | 1250355.65
85 | 2612609.4455 | 1250315.525 | 2612604.9658 | 1250317.1388 | 2612590.582 | 1250322.5897 | 2612584.4474 | 1250325.0895
86 | 2612609.4455 | 1250315.525 | 2612608.948 | 1250318.7483 | 2612609.8683 | 1250336.8397
87 | 2611783.7124 | 1250989.3114 | 2611768.2042 | 1251001.498
88 | 2611761.9226 | 1251006.4342 | 2611768.2042 | 1251001.498
89 | 2611783.7124 | 1250989.3114 | 2611791.4258 | 1250983.2502 | 2611795.5925 | 1250979.2336 | 2611798.8383 | 1250975.2152 | 2611799.3093 | 1250974.4894
90 | 2611799.3093 | 1250974.4894 | 2611808.3926 | 1250960.4912 | 2611818.2579 | 1250945.0118 | 2611821.0402 | 1250941.6608
91 | 2611865.3225 | 1250906.8822 | 2611869.7204 | 1250910.7914
92 | 2611862.7978 | 1250904.8329 | 2611863.8413 | 1250905.5656 | 2611865.3225 | 1250906.8822
93 | 2611871.8324 | 1250912.6686 | 2611869.7204 | 1250910.7914
94 | 2611877.5688 | 1250917.7676 | 2611871.8324 | 1250912.6686
95 | 2612782.8781 | 1250292.9382 | 2612782.4977 | 1250289.099 | 2612782.1306 | 1250285.0809
96 | 2612779.8001 | 1250269.3025 | 2612780.8984 | 1250274.5972 | 2612781.5021 | 1250278.2009 | 2612782.1306 | 1250285.0809
97 | 2612787.5968 | 1250311.9025 | 2612786.1971 | 1250309.8982 | 2612785.1983 | 1250307.5056 | 2612784.0992 | 1250302.6 | 2612783.3991 | 1250298.1957 | 2612782.8781 | 1250292.9382
98 | 2612779.8001 | 1250269.3025 | 2612796.7756 | 1250264.7372
99 | 2612779.8001 | 1250269.3025 | 2612771.9038 | 1250271.4451
100 | 2612787.5968 | 1250311.9025 | 2612789.6976 | 1250310.8063
101 | 2612796.7756 | 1250264.7372 | 2612822.4976 | 1250257.8196
102 | 2612802.8008 | 1250300.7057 | 2612802.8008 | 1250300.7057 | 2612796.9023 | 1250305.6962 | 2612789.6976 | 1250310.8063 | 2612789.6976 | 1250310.8063
103 | 2612831.477 | 1250255.4046 | 2612822.4976 | 1250257.8196
104 | 2612803.4403 | 1250300.0281 | 2612802.8008 | 1250300.7057
105 | 2612831.477 | 1250255.4046 | 2612844.5394 | 1250250.3295 | 2612850.272 | 1250246.6621
106 | 2612858.1542 | 1250241.6056 | 2612857.6164 | 1250241.9634 | 2612850.272 | 1250246.6621
107 | 2612877.0677 | 1250229.0205 | 2612858.1542 | 1250241.6056
108 | 2611795.7795 | 1250876.5734 | 2611804.1326 | 1250878.3071 | 2611808.1683 | 1250878.446
109 | 2612569.1887 | 1250358.2371 | 2612575.5533 | 1250358.2144 | 2612585.2022 | 1250360.8031 | 2612592.2017 | 1250359.8062 | 2612598.8024 | 1250358.1968 | 2612603.9999 | 1250356.2066 | 2612606.2476 | 1250355.65
110 | 2612588.1875 | 1250341.2301 | 2612584.4474 | 1250325.0895
111 | 2612539.2007 | 1250347.1973 | 2612541.105 | 1250349.8252 | 2612544.5409 | 1250352.7343 | 2612548.4905 | 1250355.4778 | 2612551.8005 | 1250357.2526 | 2612557.2479 | 1250358.4537 | 2612563.8003 | 1250358.2563 | 2612569.1887 | 1250358.2371
112 | 2612877.0677 | 1250229.0205 | 2612880.4006 | 1250226.8028 | 2612902.3632 | 1250218.0139
113 | 2613075.0384 | 1250308.6112 | 2613085.2009 | 1250312.605 | 2613096.592 | 1250317.2767
114 | 2613056.2951 | 1250302.266 | 2613059.9036 | 1250303.399 | 2613071.203 | 1250307.104 | 2613075.0384 | 1250308.6112
115 | 2613013.1021 | 1250296.9034 | 2613014.4024 | 1250296.0057 | 2613016.4043 | 1250295.2985 | 2613019.7028 | 1250295.4058 | 2613029.2024 | 1250297.2055 | 2613048.0972 | 1250300.2044 | 2613054.8043 | 1250301.7979 | 2613056.2951 | 1250302.266
116 | 2612985.9011 | 1250271.005 | 2613013.1021 | 1250296.9034
117 | 2613013.1021 | 1250296.9034 | 2613034.5149 | 1250322.0777 | 2613036.8734 | 1250324.8514
118 | 2612985.9011 | 1250271.005 | 2612984.6978 | 1250272.4033 | 2612983.102 | 1250273.8007 | 2612953.403 | 1250292.6038 | 2612950.1977 | 1250294.7983 | 2612947.6029 | 1250297.4054 | 2612943.802 | 1250302.7006 | 2612940.1992 | 1250307.1957 | 2612937.8026 | 1250308.9027 | 2612936.7186 | 1250309.5574
119 | 2612985.9011 | 1250271.005 | 2612981.1414 | 1250268.0178
120 | 2612923.4039 | 1250317.5993 | 2612936.7186 | 1250309.5574
121 | 2612981.1414 | 1250268.0178 | 2612948.8892 | 1250247.776
122 | 2612948.8892 | 1250247.776 | 2612946.8556 | 1250246.4997
123 | 2611787.8029 | 1250872.7044 | 2611795.479 | 1250876.511 | 2611795.7795 | 1250876.5734
124 | 2611787.8029 | 1250872.7044 | 2611782.0025 | 1250867.9653
125 | 2611769.7932 | 1250857.9897 | 2611782.0025 | 1250867.9653
126 | 2612932.9884 | 1250071.0374 | 2612932.7979 | 1250076.1965 | 2612933.7863 | 1250089.8237
127 | 2612933.7863 | 1250089.8237 | 2612933.8972 | 1250091.3531 | 2612936.3484 | 1250106.2348 | 2612938.3316 | 1250115.5717
128 | 2612938.3316 | 1250115.5717 | 2612946.0478 | 1250151.9008
129 | 2612946.1344 | 1250152.3085 | 2612946.0478 | 1250151.9008
130 | 2612946.1344 | 1250152.3085 | 2612947.0038 | 1250156.4016 | 2612947.4962 | 1250160.0203
131 | 2612945.021 | 1250186.4834 | 2612947.668 | 1250177.2387 | 2612948.6458 | 1250168.4685 | 2612947.4962 | 1250160.0203
132 | 2612946.8556 | 1250246.4997 | 2612940.0008 | 1250242.1975
133 | 2612929.6325 | 1250205.8959 | 2612935.2462 | 1250217.4489 | 2612940.0008 | 1250242.1975
134 | 2612945.021 | 1250186.4834 | 2612941.5638 | 1250193.3804 | 2612936.7194 | 1250199.5294 | 2612929.6325 | 1250205.8959
135 | 2612929.6325 | 1250205.8959 | 2612919.2264 | 1250211.2657 | 2612902.3632 | 1250218.0139
136 | 2612945.021 | 1250186.4834 | 2612959.3056 | 1250188.7715 | 2612973.7681 | 1250192.1716
137 | 2612986.0233 | 1250359.7099 | 2612997.4992 | 1250359.1987 | 2613023.2029 | 1250358.5989 | 2613025.1431 | 1250358.539
138 | 2613094.3121 | 1250235.4471 | 2613086.8685 | 1250230.5109 | 2613073.6915 | 1250222.3433 | 2613007.9012 | 1250200.196 | 2612996.9148 | 1250197.6132
139 | 2613094.3121 | 1250235.4471 | 2613104.3632 | 1250242.1125 | 2613115.3287 | 1250250.1204
140 | 2612990.6754 | 1250196.1463 | 2612996.9148 | 1250197.6132
141 | 2612990.6754 | 1250196.1463 | 2612973.7681 | 1250192.1716
142 | 2612963.6989 | 1250362.0046 | 2612972.9033 | 1250360.7016 | 2612981.797 | 1250359.8982 | 2612986.0233 | 1250359.7099

## bus_geodata
| x | y | coords
0 | 2611872.734 | 1250947.9848
1 | 2611914.7866 | 1250864.8964
2 | 2611856.3311 | 1250880.0981
3 | 2612006.0449 | 1250775.3615
4 | 2611837.7478 | 1250879.5635
5 | 2612023.8702 | 1250765.9846
6 | 2612054.512 | 1250748.6352
7 | 2612212.8615 | 1250597.4543
8 | 2612221.6827 | 1250590.1924
9 | 2611832.976 | 1250879.2292
10 | 2611835.5476 | 1250892.8344
11 | 2611821.7412 | 1250878.4421
12 | 2611829.0705 | 1250931.4355
13 | 2611849.6551 | 1250898.2049
14 | 2613155.4663 | 1250467.2076
15 | 2613136.5833 | 1250443.5512
16 | 2613164.9652 | 1250510.6205
17 | 2613087.7994 | 1250387.3036
18 | 2613105.7735 | 1250487.5316
19 | 2613067.828 | 1250361.6941
20 | 2613092.8104 | 1250388.1419
21 | 2613086.5552 | 1250479.3718
22 | 2613063.6973 | 1250356.3973
23 | 2613124.8417 | 1250397.8801
24 | 2613053.261 | 1250344.1238
25 | 2613040.2962 | 1250358.934
26 | 2613142.5784 | 1250408.8019
27 | 2612945.8965 | 1249964.7305
28 | 2612940.8653 | 1250007.7474
29 | 2612985.8798 | 1249830.9864
30 | 2612936.1008 | 1250031.1629
31 | 2612961.8348 | 1250028.9506
32 | 2613011.7067 | 1249805.7904
33 | 2612974.2974 | 1249819.4001
34 | 2613022.9041 | 1249794.8666
35 | 2613097.5968 | 1249722.0049
36 | 2613020.5352 | 1249750.5472
37 | 2613031.5503 | 1249763.1021
38 | 2613038.8566 | 1249702.017
39 | 2612902.8608 | 1249717.7964
40 | 2613056.9007 | 1249683.4017
41 | 2613071.0205 | 1249696.8859
42 | 2613193.72 | 1249628.6211
43 | 2613207.0976 | 1249619.0357
44 | 2613183.0515 | 1249637.5291
45 | 2613239.844 | 1249596.239
46 | 2613160.3078 | 1249659.2993
47 | 2613361.2035 | 1249730.6961
48 | 2613151.1769 | 1249668.0393
49 | 2613140.925 | 1249677.8529
50 | 2613139.0979 | 1249679.6022
51 | 2613384.986 | 1249718.828
52 | 2613413.9034 | 1249704.3976
53 | 2613421.1165 | 1249734.8947
54 | 2613423.0144 | 1249737.0825
55 | 2612898.5151 | 1249649.1474
56 | 2612900.5503 | 1249703.1849
57 | 2612935.4503 | 1250034.3603
58 | 2612983.7808 | 1250056.715
59 | 2612933.6684 | 1250052.6231
60 | 2612993.4947 | 1250073.3228
61 | 2612933.3273 | 1250061.8593
62 | 2612999.0554 | 1250082.8299
63 | 2612688.1975 | 1250351.2592
64 | 2612685.3077 | 1250345.8291
65 | 2612694.2651 | 1250362.661
66 | 2612679.5968 | 1250335.0977
67 | 2612698.5979 | 1250370.8027
68 | 2612733.7274 | 1250321.4614
69 | 2612637.562 | 1250350.5768
70 | 2612706.0988 | 1250384.8977
71 | 2612760.6017 | 1250319.8053
72 | 2612631.6979 | 1250351.3065
73 | 2612752.0582 | 1250350.9031
74 | 2612776.5633 | 1250316.8961
75 | 2612614.4815 | 1250353.7274
76 | 2612609.4455 | 1250315.525
77 | 2611768.2042 | 1251001.498
78 | 2611783.7124 | 1250989.3114
79 | 2611761.9226 | 1251006.4342
80 | 2611799.3093 | 1250974.4894
81 | 2611821.0402 | 1250941.6608
82 | 2611865.3225 | 1250906.8822
83 | 2611869.7204 | 1250910.7914
84 | 2611862.7978 | 1250904.8329
85 | 2611871.8324 | 1250912.6686
86 | 2611877.5688 | 1250917.7676
87 | 2612782.1306 | 1250285.0809
88 | 2612782.8781 | 1250292.9382
89 | 2612779.8001 | 1250269.3025
90 | 2612787.5968 | 1250311.9025
91 | 2612796.7756 | 1250264.7372
92 | 2612771.9038 | 1250271.4451
93 | 2612789.6976 | 1250310.8063
94 | 2612822.4976 | 1250257.8196
95 | 2612802.8008 | 1250300.7057
96 | 2612831.477 | 1250255.4046
97 | 2612803.4403 | 1250300.0281
98 | 2612850.272 | 1250246.6621
99 | 2612858.1542 | 1250241.6056
100 | 2611808.1683 | 1250878.446
101 | 2612606.2476 | 1250355.65
102 | 2612584.4474 | 1250325.0895
103 | 2612609.8683 | 1250336.8397
104 | 2612569.1887 | 1250358.2371
105 | 2612588.1875 | 1250341.2301
106 | 2612539.2007 | 1250347.1973
107 | 2612729.3344 | 1250405.0334
108 | 2612877.0677 | 1250229.0205
109 | 2613075.0384 | 1250308.6112
110 | 2613096.592 | 1250317.2767
111 | 2613056.2951 | 1250302.266
112 | 2613013.1021 | 1250296.9034
113 | 2612985.9011 | 1250271.005
114 | 2613036.8734 | 1250324.8514
115 | 2612936.7186 | 1250309.5574
116 | 2612981.1414 | 1250268.0178
117 | 2612923.4039 | 1250317.5993
118 | 2612948.8892 | 1250247.776
119 | 2611795.7795 | 1250876.5734
120 | 2611787.8029 | 1250872.7044
121 | 2611782.0025 | 1250867.9653
122 | 2611769.7932 | 1250857.9897
123 | 2612932.9884 | 1250071.0374
124 | 2612933.7863 | 1250089.8237
125 | 2612938.3316 | 1250115.5717
126 | 2612946.0478 | 1250151.9008
127 | 2612946.1344 | 1250152.3085
128 | 2612947.4962 | 1250160.0203
129 | 2612946.8556 | 1250246.4997
130 | 2612940.0008 | 1250242.1975
131 | 2612929.6325 | 1250205.8959
132 | 2612945.021 | 1250186.4834
133 | 2612902.3632 | 1250218.0139
134 | 2613147.7989 | 1250412.2964
135 | 2613025.1431 | 1250358.539
136 | 2613094.3121 | 1250235.4471
137 | 2612996.9148 | 1250197.6132
138 | 2613115.3287 | 1250250.1204
139 | 2612990.6754 | 1250196.1463
140 | 2612973.7681 | 1250192.1716
141 | 2612986.0233 | 1250359.7099
142 | 2612963.6989 | 1250362.0046
143 | 2612999.3247 | 1250083.2903
144 | 2612940.8653 | 1250007.7474

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97499 | -0.4824 | 0.00095351 | 0.00023897
1 | 0.97507 | -0.48075 | 0 | 0
2 | 0.97435 | -0.49497 | 0.0018865 | 0.00047281
3 | 0.97654 | -0.45191 | 0.0026475 | 0.00066352
4 | 0.97384 | -0.50501 | 0 | 0
5 | 0.97678 | -0.44718 | 0 | 0
6 | 0.9772 | -0.43891 | 0 | 0
7 | 0.97982 | -0.38765 | 0.004317 | 0.0010819
8 | 0.97997 | -0.38478 | 0.0060399 | 0.0015137
9 | 0.97371 | -0.50756 | 0.0038721 | 0.00097043
10 | 0.97347 | -0.51241 | 0 | 0
11 | 0.97345 | -0.51277 | 0.0028132 | 0.00070506
12 | 0.97296 | -0.52247 | 0.0021982 | 0.00055092
13 | 0.97324 | -0.51682 | 0.0040292 | 0.0010098
14 | 0.98692 | -0.25143 | 0.0013385 | 0.00033546
15 | 0.98701 | -0.2496 | 0.00059859 | 0.00015002
16 | 0.98684 | -0.25305 | 0 | 0
17 | 0.98728 | -0.24435 | 0 | 0
18 | 0.98672 | -0.25531 | 0.00093054 | 0.00023322
19 | 0.98757 | -0.23881 | 0.0024641 | 0.00061756
20 | 0.98726 | -0.24487 | 0.0026327 | 0.00065981
21 | 0.9867 | -0.25571 | 0.0010548 | 0.00026435
22 | 0.98764 | -0.23736 | 0 | 0
23 | 0.98716 | -0.24666 | 0.00092667 | 0.00023225
24 | 0.98797 | -0.23099 | 0.002461 | 0.00061678
25 | 0.98742 | -0.24173 | 0.0038919 | 0.0009754
26 | 0.98712 | -0.24743 | 0.00097192 | 0.00024359
27 | 0.9948 | -0.09841 | 0.0018826 | 0.00047183
28 | 0.99689 | -0.058715 | 0 | 0
29 | 0.98814 | -0.22585 | 0 | 0
30 | 0.99805 | -0.0368 | 0.00029187 | 7.315e-05
31 | 0.99682 | -0.059982 | 0.00058719 | 0.00014716
32 | 0.9865 | -0.25757 | 0.019726 | 0.0049438
33 | 0.98796 | -0.22924 | 0.011587 | 0.0029039
34 | 0.98584 | -0.27025 | 0.0091469 | 0.0022924
35 | 0.98164 | -0.35179 | 0 | 0
36 | 0.97793 | -0.42462 | 0.010219 | 0.0025612
37 | 0.97728 | -0.43736 | 0.041829 | 0.010483
38 | 0.97891 | -0.40531 | 0.072994 | 0.018294
39 | 0.97707 | -0.4415 | 0.0082367 | 0.0020643
40 | 0.97969 | -0.38995 | 0 | 0
41 | 0.98028 | -0.37841 | 0.037938 | 0.0095081
42 | 0.97975 | -0.38893 | 0.0010005 | 0.00025075
43 | 0.97959 | -0.39208 | 0.00060582 | 0.00015183
44 | 0.9799 | -0.38601 | 0.0035938 | 0.00090069
45 | 0.97922 | -0.39929 | 0.00016352 | 4.0983e-05
46 | 0.98034 | -0.37736 | 0.00017633 | 4.4193e-05
47 | 0.97758 | -0.43153 | 0.0020207 | 0.00050642
48 | 0.98052 | -0.37384 | 0.00057993 | 0.00014535
49 | 0.98072 | -0.36975 | 0.00015368 | 3.8515e-05
50 | 0.98076 | -0.36902 | 0 | 0
51 | 0.97738 | -0.43528 | 0.0019537 | 0.00048965
52 | 0.97721 | -0.4387 | 0 | 0
53 | 0.97704 | -0.44211 | 0.0017484 | 0.00043818
54 | 0.97703 | -0.44232 | 0.0040462 | 0.0010141
55 | 0.97624 | -0.45776 | 0.029626 | 0.0074249
56 | 0.97698 | -0.4431 | 0 | 0
57 | 0.99821 | -0.033808 | 0.00031654 | 7.9331e-05
58 | 0.99676 | -0.061128 | 0.00061795 | 0.00015487
59 | 0.9991 | -0.016927 | 0.00062386 | 0.00015636
60 | 0.99674 | -0.061537 | 0.00038452 | 9.6371e-05
61 | 0.99955 | -0.0084417 | 0.00054958 | 0.00013774
62 | 0.99673 | -0.061697 | 0.00046254 | 0.00011592
63 | 0.98773 | -0.23456 | 0.0021822 | 0.00054692
64 | 0.98775 | -0.234 | 0.001522 | 0.00038146
65 | 0.98769 | -0.23524 | 0.00045073 | 0.00011296
66 | 0.98783 | -0.23256 | 0 | 0
67 | 0.98767 | -0.23565 | 0.00028994 | 7.2665e-05
68 | 0.98888 | -0.21226 | 0.0018458 | 0.00046259
69 | 0.98704 | -0.2478 | 0.003177 | 0.00079622
70 | 0.98764 | -0.23627 | 0.00218 | 0.00054636
71 | 0.9894 | -0.20233 | 0 | 0
72 | 0.98694 | -0.24974 | 0 | 0
73 | 0.9893 | -0.20422 | 0.0024141 | 0.00060502
74 | 0.98972 | -0.19613 | 0.0010764 | 0.00026976
75 | 0.98667 | -0.25491 | 0.003671 | 0.00092004
76 | 0.9866 | -0.25629 | 0 | 0
77 | 0.97261 | -0.52941 | 0.00048856 | 0.00012245
78 | 0.97262 | -0.52906 | 0.0021523 | 0.00053943
79 | 0.9726 | -0.52949 | 0.00048856 | 0.00012245
80 | 0.97269 | -0.52781 | 0.00038837 | 9.7334e-05
81 | 0.97282 | -0.52526 | 0.00812 | 0.0020351
82 | 0.97305 | -0.52064 | 0.0068556 | 0.0017182
83 | 0.97304 | -0.52094 | 0.00088968 | 0.00022298
84 | 0.97308 | -0.52006 | 0.0022347 | 0.00056007
85 | 0.97303 | -0.52103 | 0.0012058 | 0.00030219
86 | 0.97303 | -0.52113 | 0.0006741 | 0.00016894
87 | 0.99054 | -0.18035 | 0.0039723 | 0.00099555
88 | 0.99038 | -0.18355 | 0.0013859 | 0.00034735
89 | 0.99089 | -0.17365 | 0 | 0
90 | 0.98996 | -0.19148 | 0 | 0
91 | 0.99128 | -0.16618 | 0.0023183 | 0.00058103
92 | 0.99088 | -0.17389 | 0.0016678 | 0.000418
93 | 0.98995 | -0.19169 | 0.0020316 | 0.00050917
94 | 0.99188 | -0.15466 | 0.0012718 | 0.00031875
95 | 0.98991 | -0.19254 | 0.00078618 | 0.00019704
96 | 0.99209 | -0.1506 | 0 | 0
97 | 0.98991 | -0.19258 | 0.0021137 | 0.00052975
98 | 0.99257 | -0.14151 | 0.0010199 | 0.0002556
99 | 0.99278 | -0.13739 | 0.001438 | 0.0003604
100 | 0.97317 | -0.51835 | 0.0076908 | 0.0019275
101 | 0.98654 | -0.25731 | 0.0019712 | 0.00049402
102 | 0.98643 | -0.2597 | 0 | 0
103 | 0.98657 | -0.25689 | 0.0015654 | 0.00039232
104 | 0.986 | -0.26788 | 0.0026334 | 0.00065999
105 | 0.98632 | -0.26181 | 0.0071189 | 0.0017842
106 | 0.98553 | -0.27695 | 0 | 0
107 | 0.98926 | -0.20511 | 0.00085194 | 0.00021352
108 | 0.99331 | -0.12729 | 0.00060273 | 0.00015106
109 | 0.98892 | -0.21253 | 0.0024655 | 0.00061791
110 | 0.98887 | -0.21355 | 0.0024694 | 0.0006189
111 | 0.98901 | -0.21079 | 0.0059673 | 0.0014955
112 | 0.98945 | -0.20219 | 0 | 0
113 | 0.99076 | -0.17687 | 0 | 0
114 | 0.98854 | -0.21989 | 0.0024618 | 0.00061699
115 | 0.99052 | -0.18146 | 0.0017888 | 0.00044831
116 | 0.99097 | -0.17268 | 0.0011951 | 0.00029953
117 | 0.99049 | -0.1821 | 0.0022992 | 0.00057623
118 | 0.99248 | -0.14349 | 0.0045339 | 0.0011363
119 | 0.97299 | -0.52174 | 0.0023918 | 0.00059943
120 | 0.97289 | -0.52374 | 0 | 0
121 | 0.97281 | -0.52544 | 0.0082845 | 0.0020763
122 | 0.97275 | -0.52659 | 0.0039743 | 0.00099606
123 | 1 | 0 | -0.48341 | -0.12368
124 | 0.99927 | -0.013833 | 0.00038814 | 9.7278e-05
125 | 0.99826 | -0.033054 | 0.0030729 | 0.00077013
126 | 0.99684 | -0.060008 | 0.00092329 | 0.0002314
127 | 0.99682 | -0.060309 | 0.0011386 | 0.00028536
128 | 0.99653 | -0.06595 | 0.0014521 | 0.00036393
129 | 0.99259 | -0.14146 | 0.00093585 | 0.00023455
130 | 0.99295 | -0.13448 | 0.00090251 | 0.00022619
131 | 0.99468 | -0.10116 | 0 | 0
132 | 0.99552 | -0.085247 | 0 | 0
133 | 0.99396 | -0.11495 | 0.0044841 | 0.0011238
134 | 0.98712 | -0.24755 | 0.0010913 | 0.00027351
135 | 0.98733 | -0.24342 | 0.0028912 | 0.00072459
136 | 0.99246 | -0.14432 | 0.010555 | 0.0026454
137 | 0.99442 | -0.10638 | 0.0008094 | 0.00020285
138 | 0.99223 | -0.1488 | 0.0098724 | 0.0024743
139 | 0.99454 | -0.10398 | 0.00097616 | 0.00024465
140 | 0.9949 | -0.097184 | 0.00091362 | 0.00022897
141 | 0.98721 | -0.24575 | 0.0016666 | 0.00041769
142 | 0.98718 | -0.24642 | 0.0016665 | 0.00041765
143 | 0.99673 | -0.061701 | 0.00036551 | 9.1607e-05
144 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00095351 | -0.00023897 | 0.00095359 | 0.00023785 | 7.4763e-08 | -1.1267e-06 | 0.0014552 | 0.0014548 | 0.0014552 | 0.97499 | -0.4824 | 0.97507 | -0.48075 | 0.39979
1 | 0.060753 | 0.015263 | -0.060712 | -0.01524 | 4.1218e-05 | 2.2396e-05 | 0.092726 | 0.092727 | 0.092727 | 0.97507 | -0.48075 | 0.97435 | -0.49497 | 5.0949
2 | -0.061707 | -0.015501 | 0.061792 | 0.015547 | 8.5046e-05 | 4.6444e-05 | 0.09418 | 0.094177 | 0.09418 | 0.97507 | -0.48075 | 0.97654 | -0.45191 | 5.1747
3 | 0.058825 | 0.014768 | -0.058797 | -0.01475 | 2.8139e-05 | 1.7546e-05 | 0.089846 | 0.089846 | 0.089846 | 0.97435 | -0.49497 | 0.97384 | -0.50501 | 12.3415
4 | -0.064439 | -0.016211 | 0.064454 | 0.016219 | 1.457e-05 | 8.0648e-06 | 0.098212 | 0.098211 | 0.098212 | 0.97654 | -0.45191 | 0.97678 | -0.44718 | 5.3962
5 | 0.029047 | 0.007287 | -0.029044 | -0.0072848 | 3.534e-06 | 2.2023e-06 | 0.044386 | 0.044386 | 0.044386 | 0.97384 | -0.50501 | 0.97371 | -0.50756 | 12.194
6 | 0.02975 | 0.0074631 | -0.029739 | -0.0074566 | 1.0492e-05 | 6.5463e-06 | 0.04546 | 0.04546 | 0.04546 | 0.97384 | -0.50501 | 0.97347 | -0.51241 | 12.489
7 | -0.064454 | -0.016219 | 0.064479 | 0.016233 | 2.5477e-05 | 1.41e-05 | 0.098211 | 0.09821 | 0.098211 | 0.97678 | -0.44718 | 0.9772 | -0.43891 | 5.3962
8 | -0.064479 | -0.016233 | 0.064637 | 0.01632 | 0.00015836 | 8.7603e-05 | 0.09821 | 0.098205 | 0.09821 | 0.9772 | -0.43891 | 0.97982 | -0.38765 | 5.3962
9 | -0.068954 | -0.017402 | 0.068964 | 0.017408 | 9.468e-06 | 5.335e-06 | 0.10476 | 0.10476 | 0.10476 | 0.97982 | -0.38765 | 0.97997 | -0.38478 | 5.7561
10 | -0.075004 | -0.018921 | 0.075393 | 0.019145 | 0.00038922 | 0.00022377 | 0.11393 | 0.11392 | 0.11393 | 0.97997 | -0.38478 | 0.98553 | -0.27695 | 6.26
11 | 0.025172 | 0.0063143 | -0.025165 | -0.0063105 | 6.25e-06 | 3.8599e-06 | 0.038469 | 0.038469 | 0.038469 | 0.97371 | -0.50756 | 0.97345 | -0.51277 | 10.5684
12 | 0.013845 | 0.0034715 | -0.013838 | -0.0034678 | 6.6345e-06 | 3.7553e-06 | 0.021163 | 0.021164 | 0.021164 | 0.97347 | -0.51241 | 0.97296 | -0.52247 | 5.8142
13 | 0.015895 | 0.0039851 | -0.015891 | -0.0039831 | 3.3416e-06 | 1.951e-06 | 0.024296 | 0.024297 | 0.024297 | 0.97347 | -0.51241 | 0.97324 | -0.51682 | 6.6749
14 | 0.022352 | 0.0056054 | -0.022346 | -0.0056018 | 5.9447e-06 | 3.6358e-06 | 0.034169 | 0.034169 | 0.034169 | 0.97345 | -0.51277 | 0.97317 | -0.51835 | 9.387
15 | 0.01164 | 0.0029168 | -0.011638 | -0.002916 | 1.5456e-06 | 8.277e-07 | 0.017802 | 0.017802 | 0.017802 | 0.97296 | -0.52247 | 0.97282 | -0.52526 | 4.8906
16 | 0.011862 | 0.0029733 | -0.01186 | -0.0029723 | 1.8293e-06 | 9.8648e-07 | 0.018136 | 0.018136 | 0.018136 | 0.97324 | -0.51682 | 0.97308 | -0.52006 | 4.9825
17 | -0.0033242 | -0.00083161 | 0.0033245 | 0.00083141 | 2.8826e-07 | -2.0666e-07 | 0.0050115 | 0.0050114 | 0.0050115 | 0.98692 | -0.25143 | 0.98701 | -0.2496 | 1.3768
18 | 0.0019857 | 0.00049616 | -0.0019856 | -0.00049664 | 1.5303e-07 | -4.8393e-07 | 0.0029934 | 0.0029936 | 0.0029936 | 0.98692 | -0.25143 | 0.98684 | -0.25305 | 0.82242
19 | -0.0039231 | -0.00098143 | 0.0039241 | 0.0009811 | 9.7967e-07 | -3.2804e-07 | 0.0059138 | 0.0059134 | 0.0059138 | 0.98701 | -0.2496 | 0.98728 | -0.24435 | 1.6247
20 | 0.0019856 | 0.00049664 | -0.0019853 | -0.00049732 | 2.1406e-07 | -6.7664e-07 | 0.0029936 | 0.0029939 | 0.0029939 | 0.98684 | -0.25305 | 0.98672 | -0.25531 | 0.8225
21 | -0.0095471 | -0.0023897 | 0.0095496 | 0.0023909 | 2.5212e-06 | 1.1981e-06 | 0.014388 | 0.014388 | 0.014388 | 0.98728 | -0.24435 | 0.98757 | -0.23881 | 3.9528
22 | 0.005623 | 0.0014086 | -0.0056229 | -0.0014086 | 1.3719e-07 | 2.2665e-08 | 0.0084747 | 0.0084747 | 0.0084747 | 0.98728 | -0.24435 | 0.98726 | -0.24487 | 2.3282
23 | 0.0010548 | 0.0002641 | -0.0010548 | -0.00026435 | 1.981e-08 | -2.54e-07 | 0.0015906 | 0.0015907 | 0.0015907 | 0.98672 | -0.25531 | 0.9867 | -0.25571 | 0.437
24 | -0.012014 | -0.0030085 | 0.012015 | 0.0030089 | 8.2528e-07 | 4.4223e-07 | 0.018101 | 0.018101 | 0.018101 | 0.98757 | -0.23881 | 0.98764 | -0.23736 | 4.9727
25 | 0.0029902 | 0.00074878 | -0.00299 | -0.00074904 | 2.5543e-07 | -2.653e-07 | 0.0045067 | 0.0045069 | 0.0045069 | 0.98726 | -0.24487 | 0.98716 | -0.24666 | 1.2382
26 | -0.022134 | -0.0055449 | 0.02214 | 0.005549 | 6.7181e-06 | 4.0933e-06 | 0.033347 | 0.033346 | 0.033347 | 0.98764 | -0.23736 | 0.98797 | -0.23099 | 9.1611
27 | 0.010119 | 0.002536 | -0.010117 | -0.0025349 | 2.1032e-06 | 1.0373e-06 | 0.015246 | 0.015246 | 0.015246 | 0.98764 | -0.23736 | 0.98742 | -0.24173 | 4.1884
28 | 0.0020633 | 0.0005168 | -0.0020632 | -0.00051702 | 7.5586e-08 | -2.1803e-07 | 0.00311 | 0.0031101 | 0.0031101 | 0.98716 | -0.24666 | 0.98712 | -0.24743 | 0.85443
29 | -0.024601 | -0.0061658 | 0.024614 | 0.0061738 | 1.3025e-05 | 8.0116e-06 | 0.037053 | 0.037053 | 0.037053 | 0.98797 | -0.23099 | 0.98854 | -0.21989 | 10.1794
30 | 0.0062251 | 0.0015595 | -0.0062246 | -0.0015594 | 5.0057e-07 | 1.2636e-07 | 0.0093809 | 0.009381 | 0.009381 | 0.98742 | -0.24173 | 0.98733 | -0.24342 | 2.5772
31 | 0.0010913 | 0.00027343 | -0.0010913 | -0.00027351 | 6.3753e-09 | -7.6228e-08 | 0.001645 | 0.0016451 | 0.0016451 | 0.98712 | -0.24743 | 0.98712 | -0.24755 | 0.45194
32 | -0.26287 | -0.067258 | 0.26338 | 0.067579 | 0.00050619 | 0.00032113 | 0.3937 | 0.3937 | 0.3937 | 0.9948 | -0.09841 | 0.99689 | -0.058715 | 21.6317
33 | 0.26099 | 0.066786 | -0.25939 | -0.065772 | 0.0015996 | 0.0010148 | 0.39088 | 0.39088 | 0.39088 | 0.9948 | -0.09841 | 0.98814 | -0.22585 | 21.4771
34 | -0.2658 | -0.068184 | 0.26608 | 0.068364 | 0.00028289 | 0.00017949 | 0.3973 | 0.3973 | 0.3973 | 0.99689 | -0.058715 | 0.99805 | -0.0368 | 21.8299
35 | 0.002418 | 0.00060486 | -0.0024178 | -0.00060515 | 1.4576e-07 | -2.958e-07 | 0.0036088 | 0.003609 | 0.003609 | 0.99689 | -0.058715 | 0.99682 | -0.059982 | 0.99148
36 | 0.2478 | 0.062867 | -0.24743 | -0.062628 | 0.00037737 | 0.00023921 | 0.37343 | 0.37343 | 0.37343 | 0.98814 | -0.22585 | 0.9865 | -0.25757 | 20.5183
37 | 0.011589 | 0.0029049 | -0.011587 | -0.0029039 | 1.871e-06 | 9.8759e-07 | 0.017451 | 0.017451 | 0.017451 | 0.98814 | -0.22585 | 0.98796 | -0.22924 | 4.7943
38 | -0.26637 | -0.068437 | 0.26641 | 0.068461 | 3.8713e-05 | 2.4563e-05 | 0.39774 | 0.39774 | 0.39774 | 0.99805 | -0.0368 | 0.99821 | -0.033808 | 21.8538
39 | 0.0018307 | 0.00045799 | -0.0018306 | -0.00045839 | 9.9823e-08 | -4.0083e-07 | 0.0027324 | 0.0027326 | 0.0027326 | 0.99682 | -0.059982 | 0.99676 | -0.061128 | 0.75072
40 | 0.2277 | 0.057684 | -0.22756 | -0.057596 | 0.00013858 | 8.7692e-05 | 0.34368 | 0.34368 | 0.34368 | 0.9865 | -0.25757 | 0.98584 | -0.27025 | 18.8835
41 | 0.21841 | 0.055304 | -0.21756 | -0.054765 | 0.00085159 | 0.00053839 | 0.32987 | 0.32988 | 0.32988 | 0.98584 | -0.27025 | 0.98164 | -0.35179 | 18.125
42 | 0.20147 | 0.050718 | -0.20121 | -0.050557 | 0.00025594 | 0.00016149 | 0.30548 | 0.30548 | 0.30548 | 0.98164 | -0.35179 | 0.98028 | -0.37841 | 16.7844
43 | 0.016093 | 0.0040472 | -0.01608 | -0.0040395 | 1.3228e-05 | 7.7176e-06 | 0.0244 | 0.0244 | 0.0244 | 0.98164 | -0.35179 | 0.98076 | -0.36902 | 6.7033
44 | 0.041854 | 0.010499 | -0.041829 | -0.010483 | 2.5405e-05 | 1.605e-05 | 0.063689 | 0.063689 | 0.063689 | 0.97793 | -0.42462 | 0.97728 | -0.43736 | 17.4969
45 | -0.089989 | -0.022574 | 0.090072 | 0.022623 | 8.292e-05 | 4.9367e-05 | 0.13694 | 0.13693 | 0.13694 | 0.97793 | -0.42462 | 0.97891 | -0.40531 | 7.5239
46 | 0.037916 | 0.0095135 | -0.037885 | -0.0095016 | 3.0498e-05 | 1.1863e-05 | 0.057697 | 0.0577 | 0.0577 | 0.97793 | -0.42462 | 0.97707 | -0.4415 | 3.1703
47 | -0.16307 | -0.040917 | 0.16319 | 0.040992 | 0.00011948 | 7.4838e-05 | 0.24789 | 0.24789 | 0.24789 | 0.97891 | -0.40531 | 0.97969 | -0.38995 | 13.6203
48 | 0.029649 | 0.0074373 | -0.029646 | -0.0074368 | 2.2623e-06 | 5.2156e-07 | 0.045156 | 0.045156 | 0.045156 | 0.97707 | -0.4415 | 0.97698 | -0.4431 | 2.4811
49 | -0.16319 | -0.040992 | 0.16328 | 0.041049 | 8.9981e-05 | 5.6358e-05 | 0.24789 | 0.24789 | 0.24789 | 0.97969 | -0.38995 | 0.98028 | -0.37841 | 13.6203
50 | 0.010562 | 0.0026519 | -0.01056 | -0.0026511 | 1.5883e-06 | 8.0931e-07 | 0.016043 | 0.016043 | 0.016043 | 0.97975 | -0.38893 | 0.97959 | -0.39208 | 4.4073
51 | -0.011562 | -0.0029027 | 0.011564 | 0.0029035 | 1.6116e-06 | 8.559e-07 | 0.017562 | 0.017562 | 0.017562 | 0.97975 | -0.38893 | 0.9799 | -0.38601 | 4.8248
52 | 0.0099543 | 0.0024993 | -0.0099508 | -0.0024976 | 3.4221e-06 | 1.688e-06 | 0.015122 | 0.015123 | 0.015123 | 0.97959 | -0.39208 | 0.97922 | -0.39929 | 4.1546
53 | -0.015158 | -0.0038042 | 0.015164 | 0.0038078 | 6.256e-06 | 3.6071e-06 | 0.023019 | 0.023019 | 0.023019 | 0.9799 | -0.38601 | 0.98034 | -0.37736 | 6.324
54 | 0.0097873 | 0.0024566 | -0.0097723 | -0.0024493 | 1.5028e-05 | 7.3432e-06 | 0.014874 | 0.014875 | 0.014875 | 0.97922 | -0.39929 | 0.97758 | -0.43153 | 4.0865
55 | -0.01534 | -0.003852 | 0.015343 | 0.0038535 | 2.5703e-06 | 1.4856e-06 | 0.023287 | 0.023287 | 0.023287 | 0.98034 | -0.37736 | 0.98052 | -0.37384 | 6.3975
56 | 0.0077516 | 0.0019429 | -0.0077502 | -0.0019423 | 1.3877e-06 | 5.5493e-07 | 0.011799 | 0.011799 | 0.011799 | 0.97758 | -0.43153 | 0.97738 | -0.43528 | 3.2416
57 | -0.015923 | -0.0039989 | 0.015926 | 0.0040007 | 3.1082e-06 | 1.8102e-06 | 0.024167 | 0.024167 | 0.024167 | 0.98052 | -0.37384 | 0.98072 | -0.36975 | 6.6393
58 | -0.016079 | -0.0040392 | 0.01608 | 0.0040395 | 5.6474e-07 | 3.2952e-07 | 0.0244 | 0.0244 | 0.0244 | 0.98072 | -0.36975 | 0.98076 | -0.36902 | 6.7033
59 | 0.0057965 | 0.0014526 | -0.0057956 | -0.0014524 | 9.4383e-07 | 1.991e-07 | 0.0088248 | 0.008825 | 0.008825 | 0.97738 | -0.43528 | 0.97721 | -0.4387 | 2.4244
60 | 0.0057956 | 0.0014524 | -0.0057946 | -0.0014522 | 9.4004e-07 | 1.9845e-07 | 0.008825 | 0.0088251 | 0.0088251 | 0.97721 | -0.4387 | 0.97704 | -0.44211 | 2.4245
61 | 0.0040463 | 0.0010141 | -0.0040462 | -0.0010141 | 4.1446e-08 | -9.923e-09 | 0.0061624 | 0.0061624 | 0.0061624 | 0.97704 | -0.44211 | 0.97703 | -0.44232 | 1.693
62 | -0.029626 | -0.0074249 | 0.029646 | 0.0074368 | 2.0712e-05 | 1.19e-05 | 0.045156 | 0.045156 | 0.045156 | 0.97624 | -0.45776 | 0.97698 | -0.4431 | 6.2028
63 | -0.26673 | -0.068541 | 0.26695 | 0.06868 | 0.00021891 | 0.0001389 | 0.39821 | 0.39821 | 0.39821 | 0.99821 | -0.033808 | 0.9991 | -0.016927 | 21.8797
64 | 0.0012126 | 0.00030352 | -0.0012126 | -0.00030375 | 2.3641e-08 | -2.3565e-07 | 0.0018101 | 0.0018102 | 0.0018102 | 0.99676 | -0.061128 | 0.99674 | -0.061537 | 0.4973
65 | -0.26757 | -0.068836 | 0.26768 | 0.068906 | 0.00011043 | 7.0072e-05 | 0.39914 | 0.39914 | 0.39914 | 0.9991 | -0.016927 | 0.99955 | -0.0084417 | 21.9307
66 | 0.00082806 | 0.00020738 | -0.00082805 | -0.00020752 | 6.3114e-09 | -1.3951e-07 | 0.0012361 | 0.0012362 | 0.0012362 | 0.99674 | -0.061537 | 0.99673 | -0.061697 | 0.33961
67 | -0.26823 | -0.069044 | 0.26834 | 0.069114 | 0.00011019 | 6.9918e-05 | 0.39996 | 0.39996 | 0.39996 | 0.99955 | -0.0084417 | 1 | 0 | 21.9757
68 | 0.00036551 | 9.16e-05 | -0.00036551 | -9.1607e-05 | 5.9774e-11 | -6.9136e-09 | 0.00054567 | 0.00054567 | 0.00054567 | 0.99673 | -0.061697 | 0.99673 | -0.061701 | 0.14991
69 | -0.0051031 | -0.0012786 | 0.0051033 | 0.0012786 | 1.3633e-07 | 8.5179e-09 | 0.0076878 | 0.0076877 | 0.0076878 | 0.98773 | -0.23456 | 0.98775 | -0.234 | 2.112
70 | 0.0029209 | 0.00073164 | -0.0029208 | -0.00073174 | 9.3778e-08 | -1.0529e-07 | 0.0044002 | 0.0044003 | 0.0044003 | 0.98773 | -0.23456 | 0.98769 | -0.23524 | 1.2089
71 | -0.0066253 | -0.00166 | 0.0066257 | 0.0016602 | 4.5409e-07 | 1.3501e-07 | 0.0099806 | 0.0099806 | 0.0099806 | 0.98775 | -0.234 | 0.98783 | -0.23256 | 2.7419
72 | 0.0024701 | 0.00061878 | -0.00247 | -0.00061887 | 4.7892e-08 | -8.7382e-08 | 0.0037212 | 0.0037212 | 0.0037212 | 0.98769 | -0.23524 | 0.98767 | -0.23565 | 1.0223
73 | -0.10234 | -0.02596 | 0.10244 | 0.026021 | 0.00010001 | 6.0414e-05 | 0.15427 | 0.15427 | 0.15427 | 0.98783 | -0.23256 | 0.98888 | -0.21226 | 8.4766
74 | 0.095716 | 0.0243 | -0.095646 | -0.024258 | 7.0106e-05 | 4.1997e-05 | 0.14429 | 0.14429 | 0.14429 | 0.98783 | -0.23256 | 0.98704 | -0.2478 | 7.9283
75 | 0.0021801 | 0.0005462 | -0.00218 | -0.00054636 | 6.4591e-08 | -1.6299e-07 | 0.0032844 | 0.0032845 | 0.0032845 | 0.98767 | -0.23565 | 0.98764 | -0.23627 | 0.90234
76 | -0.10429 | -0.026483 | 0.10434 | 0.026514 | 4.9864e-05 | 3.0183e-05 | 0.15705 | 0.15705 | 0.15705 | 0.98888 | -0.21226 | 0.9894 | -0.20233 | 8.6291
77 | 0.092469 | 0.023462 | -0.09246 | -0.023457 | 8.6255e-06 | 5.1427e-06 | 0.1395 | 0.13951 | 0.13951 | 0.98704 | -0.2478 | 0.98694 | -0.24974 | 7.6651
78 | 0.0032663 | 0.00081758 | -0.003266 | -0.00081781 | 2.9374e-07 | -2.2887e-07 | 0.0049121 | 0.0049122 | 0.0049122 | 0.9894 | -0.20233 | 0.9893 | -0.20422 | 1.3495
79 | -0.1076 | -0.027331 | 0.10764 | 0.027351 | 3.2142e-05 | 1.9521e-05 | 0.16196 | 0.16196 | 0.16196 | 0.9894 | -0.20233 | 0.98972 | -0.19613 | 8.899
80 | 0.083771 | 0.021279 | -0.083751 | -0.021267 | 2.085e-05 | 1.2232e-05 | 0.1264 | 0.1264 | 0.1264 | 0.98694 | -0.24974 | 0.98667 | -0.25491 | 6.9453
81 | 0.008689 | 0.0021781 | -0.0086862 | -0.0021769 | 2.7128e-06 | 1.1977e-06 | 0.013101 | 0.013101 | 0.013101 | 0.98694 | -0.24974 | 0.9866 | -0.25629 | 3.5991
82 | 0.00085198 | 0.00021278 | -0.00085194 | -0.00021352 | 3.6216e-08 | -7.3207e-07 | 0.0012812 | 0.0012815 | 0.0012815 | 0.9893 | -0.20422 | 0.98926 | -0.20511 | 0.35205
83 | -0.10871 | -0.02762 | 0.10874 | 0.027635 | 2.4322e-05 | 1.4787e-05 | 0.16358 | 0.16358 | 0.16358 | 0.98972 | -0.19613 | 0.98996 | -0.19148 | 8.9879
84 | 0.08008 | 0.020347 | -0.08007 | -0.020341 | 9.2681e-06 | 5.3915e-06 | 0.12087 | 0.12087 | 0.12087 | 0.98667 | -0.25491 | 0.98654 | -0.25731 | 6.6411
85 | 0.0071208 | 0.0017848 | -0.0071196 | -0.0017844 | 1.1549e-06 | 3.9822e-07 | 0.01074 | 0.01074 | 0.01074 | 0.9866 | -0.25629 | 0.98643 | -0.2597 | 2.9505
86 | 0.0015654 | 0.00039208 | -0.0015654 | -0.00039232 | 4.469e-08 | -2.444e-07 | 0.0023609 | 0.002361 | 0.002361 | 0.9866 | -0.25629 | 0.98657 | -0.25689 | 0.64864
87 | -0.00097713 | -0.00024479 | 0.00097714 | 0.00024456 | 1.6528e-08 | -2.342e-07 | 0.0014949 | 0.0014948 | 0.0014949 | 0.97261 | -0.52941 | 0.97262 | -0.52906 | 0.41069
88 | 0.00048856 | 0.00012235 | -0.00048856 | -0.00012245 | 1.6737e-09 | -9.8075e-08 | 0.00074743 | 0.00074747 | 0.00074747 | 0.97261 | -0.52941 | 0.9726 | -0.52949 | 0.20535
89 | -0.0031295 | -0.00078399 | 0.0031297 | 0.00078384 | 1.859e-07 | -1.4946e-07 | 0.0047877 | 0.0047876 | 0.0047877 | 0.97262 | -0.52906 | 0.97269 | -0.52781 | 1.3153
90 | -0.003518 | -0.00088117 | 0.0035185 | 0.00088095 | 4.2789e-07 | -2.1525e-07 | 0.0053817 | 0.0053815 | 0.0053817 | 0.97269 | -0.52781 | 0.97282 | -0.52526 | 1.4785
91 | 0.0027696 | 0.00069394 | -0.0027695 | -0.00069399 | 3.958e-08 | -4.7759e-08 | 0.0042353 | 0.0042353 | 0.0042353 | 0.97305 | -0.52064 | 0.97304 | -0.52094 | 1.1635
92 | -0.0096252 | -0.0024121 | 0.0096254 | 0.0024122 | 2.646e-07 | 1.2889e-07 | 0.014719 | 0.014719 | 0.014719 | 0.97305 | -0.52064 | 0.97308 | -0.52006 | 4.0437
93 | 0.0018799 | 0.00047101 | -0.0018799 | -0.00047104 | 8.757e-09 | -2.9494e-08 | 0.0028747 | 0.0028747 | 0.0028747 | 0.97304 | -0.52094 | 0.97303 | -0.52103 | 0.78977
94 | 0.0006741 | 0.00016885 | -0.0006741 | -0.00016894 | 3.0585e-09 | -9.3375e-08 | 0.0010308 | 0.0010309 | 0.0010309 | 0.97303 | -0.52103 | 0.97303 | -0.52113 | 0.28321
95 | 0.11512 | 0.029256 | -0.1151 | -0.029245 | 1.7732e-05 | 1.0841e-05 | 0.17307 | 0.17307 | 0.17307 | 0.99054 | -0.18035 | 0.99038 | -0.18355 | 9.5095
96 | -0.11909 | -0.030251 | 0.11913 | 0.030275 | 3.8394e-05 | 2.3544e-05 | 0.17904 | 0.17904 | 0.17904 | 0.99054 | -0.18035 | 0.99089 | -0.17365 | 9.8374
97 | 0.11371 | 0.028898 | -0.11367 | -0.028871 | 4.3435e-05 | 2.6524e-05 | 0.17099 | 0.17099 | 0.17099 | 0.99038 | -0.18355 | 0.98996 | -0.19148 | 9.3951
98 | -0.12079 | -0.030693 | 0.12084 | 0.030719 | 4.3452e-05 | 2.6677e-05 | 0.18154 | 0.18154 | 0.18154 | 0.99089 | -0.17365 | 0.99128 | -0.16618 | 9.975
99 | 0.0016678 | 0.0004179 | -0.0016678 | -0.000418 | 1.9246e-08 | -9.3074e-08 | 0.0025046 | 0.0025046 | 0.0025046 | 0.99089 | -0.17365 | 0.99088 | -0.17389 | 0.68808
100 | 0.0049317 | 0.0012358 | -0.0049316 | -0.0012358 | 4.8828e-08 | 7.8343e-10 | 0.0074127 | 0.0074128 | 0.0074128 | 0.98996 | -0.19148 | 0.98995 | -0.19169 | 2.0365
101 | -0.12316 | -0.0313 | 0.12322 | 0.031343 | 6.8389e-05 | 4.2051e-05 | 0.18502 | 0.18502 | 0.18502 | 0.99128 | -0.16618 | 0.99188 | -0.15466 | 10.1662
102 | 0.0029 | 0.00072664 | -0.0028999 | -0.00072677 | 1.1799e-07 | -1.3738e-07 | 0.004359 | 0.0043591 | 0.0043591 | 0.98995 | -0.19169 | 0.98991 | -0.19254 | 1.1976
103 | -0.1245 | -0.031661 | 0.12452 | 0.031676 | 2.4369e-05 | 1.4996e-05 | 0.18693 | 0.18693 | 0.18693 | 0.99188 | -0.15466 | 0.99209 | -0.1506 | 10.271
104 | 0.0021137 | 0.00052974 | -0.0021137 | -0.00052975 | 3.5269e-09 | -9.7202e-09 | 0.0031773 | 0.0031773 | 0.0031773 | 0.98991 | -0.19254 | 0.98991 | -0.19258 | 0.87289
105 | -0.12452 | -0.031676 | 0.12457 | 0.03171 | 5.4561e-05 | 3.3574e-05 | 0.18693 | 0.18693 | 0.18693 | 0.99209 | -0.1506 | 0.99257 | -0.14151 | 10.271
106 | -0.12559 | -0.031965 | 0.12562 | 0.031981 | 2.4946e-05 | 1.536e-05 | 0.18846 | 0.18846 | 0.18846 | 0.99257 | -0.14151 | 0.99278 | -0.13739 | 10.3549
107 | -0.12706 | -0.032341 | 0.12712 | 0.032379 | 6.1908e-05 | 3.8151e-05 | 0.19062 | 0.19061 | 0.19062 | 0.99278 | -0.13739 | 0.99331 | -0.12729 | 10.4734
108 | 0.014655 | 0.0036743 | -0.014653 | -0.0036729 | 2.3669e-06 | 1.3587e-06 | 0.022409 | 0.022409 | 0.022409 | 0.97317 | -0.51835 | 0.97299 | -0.52174 | 6.1564
109 | 0.078099 | 0.019847 | -0.078059 | -0.019824 | 3.9718e-05 | 2.2988e-05 | 0.1179 | 0.1179 | 0.1179 | 0.98654 | -0.25731 | 0.986 | -0.26788 | 6.4778
110 | 0.0071196 | 0.0017844 | -0.0071189 | -0.0017842 | 7.1661e-07 | 2.4717e-07 | 0.01074 | 0.01074 | 0.01074 | 0.98643 | -0.2597 | 0.98632 | -0.26181 | 2.9506
111 | 0.075426 | 0.019164 | -0.075393 | -0.019145 | 3.2934e-05 | 1.8921e-05 | 0.11392 | 0.11392 | 0.11392 | 0.986 | -0.26788 | 0.98553 | -0.27695 | 6.2595
112 | -0.12772 | -0.03253 | 0.1278 | 0.032577 | 7.6088e-05 | 4.6905e-05 | 0.19152 | 0.19152 | 0.19152 | 0.99331 | -0.12729 | 0.99396 | -0.11495 | 10.5229
113 | 0.0024696 | 0.00061868 | -0.0024694 | -0.0006189 | 1.2029e-07 | -2.2106e-07 | 0.0037158 | 0.0037159 | 0.0037159 | 0.98892 | -0.21253 | 0.98887 | -0.21355 | 1.0209
114 | -0.0049351 | -0.0012366 | 0.0049355 | 0.0012366 | 4.093e-07 | 7.9612e-09 | 0.0074256 | 0.0074256 | 0.0074256 | 0.98892 | -0.21253 | 0.98901 | -0.21079 | 2.04
115 | -0.010903 | -0.0027321 | 0.010907 | 0.0027344 | 4.466e-06 | 2.29e-06 | 0.016404 | 0.016403 | 0.016404 | 0.98901 | -0.21079 | 0.98945 | -0.20219 | 4.5065
116 | -0.038006 | -0.0095393 | 0.038052 | 0.0095683 | 4.5951e-05 | 2.8927e-05 | 0.057162 | 0.057162 | 0.057162 | 0.98945 | -0.20219 | 0.99076 | -0.17687 | 15.7038
117 | 0.027099 | 0.0068049 | -0.027076 | -0.0067908 | 2.2857e-05 | 1.4158e-05 | 0.040758 | 0.040759 | 0.040759 | 0.98945 | -0.20219 | 0.98854 | -0.21989 | 11.1974
118 | 0.0040889 | 0.0010241 | -0.0040881 | -0.0010244 | 8.9334e-07 | -2.4153e-07 | 0.006141 | 0.0061412 | 0.0061412 | 0.99076 | -0.17687 | 0.99052 | -0.18146 | 1.6872
119 | -0.042141 | -0.010592 | 0.04215 | 0.010598 | 8.4444e-06 | 5.3321e-06 | 0.063303 | 0.063303 | 0.063303 | 0.99076 | -0.17687 | 0.99097 | -0.17268 | 17.3909
120 | 0.0022993 | 0.00057608 | -0.0022992 | -0.00057623 | 6.9592e-08 | -1.5567e-07 | 0.003454 | 0.0034541 | 0.0034541 | 0.99052 | -0.18146 | 0.99049 | -0.1821 | 0.94893
121 | -0.043345 | -0.010897 | 0.043405 | 0.010936 | 6.051e-05 | 3.8235e-05 | 0.065097 | 0.065097 | 0.065097 | 0.99097 | -0.17268 | 0.99248 | -0.14349 | 17.8839
122 | -0.047939 | -0.012072 | 0.047944 | 0.012075 | 4.6538e-06 | 2.9474e-06 | 0.071895 | 0.071895 | 0.071895 | 0.99248 | -0.14349 | 0.99259 | -0.14146 | 19.7513
123 | 0.012261 | 0.0030735 | -0.01226 | -0.0030728 | 1.1702e-06 | 6.3873e-07 | 0.018751 | 0.018751 | 0.018751 | 0.97299 | -0.52174 | 0.97289 | -0.52374 | 5.1515
124 | 0.01226 | 0.0030728 | -0.012259 | -0.0030723 | 9.8765e-07 | 5.3909e-07 | 0.018751 | 0.018752 | 0.018752 | 0.97289 | -0.52374 | 0.97281 | -0.52544 | 5.1515
125 | 0.0039746 | 0.00099601 | -0.0039743 | -0.00099606 | 2.1853e-07 | -5.588e-08 | 0.0060795 | 0.0060796 | 0.0060796 | 0.97281 | -0.52544 | 0.97275 | -0.52659 | 1.6702
126 | 0.21342 | 0.054566 | -0.21327 | -0.054476 | 0.00014273 | 9.0115e-05 | 0.31795 | 0.31795 | 0.31795 | 1 | 0 | 0.99927 | -0.013833 | 17.4697
127 | 0.21289 | 0.054379 | -0.21269 | -0.054254 | 0.00019763 | 0.00012477 | 0.31737 | 0.31737 | 0.31737 | 0.99927 | -0.013833 | 0.99826 | -0.033054 | 17.438
128 | 0.20961 | 0.053484 | -0.20934 | -0.053312 | 0.00027253 | 0.00017199 | 0.31279 | 0.31279 | 0.31279 | 0.99826 | -0.033054 | 0.99684 | -0.060008 | 17.1864
129 | 0.20842 | 0.053081 | -0.20842 | -0.053079 | 3.032e-06 | 1.9133e-06 | 0.31141 | 0.31141 | 0.31141 | 0.99684 | -0.060008 | 0.99682 | -0.060309 | 17.1107
130 | 0.20728 | 0.052793 | -0.20722 | -0.052758 | 5.6377e-05 | 3.557e-05 | 0.30971 | 0.30971 | 0.30971 | 0.99682 | -0.060309 | 0.99653 | -0.06595 | 17.0173
131 | 0.20577 | 0.052394 | -0.20558 | -0.052273 | 0.0001913 | 0.00012068 | 0.30755 | 0.30755 | 0.30755 | 0.99653 | -0.06595 | 0.99552 | -0.085247 | 16.8982
132 | -0.04888 | -0.012309 | 0.048896 | 0.01232 | 1.6305e-05 | 1.033e-05 | 0.073298 | 0.073298 | 0.073298 | 0.99259 | -0.14146 | 0.99295 | -0.13448 | 20.1367
133 | -0.049798 | -0.012546 | 0.049878 | 0.012596 | 7.9506e-05 | 5.0391e-05 | 0.07465 | 0.07465 | 0.07465 | 0.99295 | -0.13448 | 0.99468 | -0.10116 | 20.5083
134 | -0.18225 | -0.046352 | 0.18239 | 0.04644 | 0.00013985 | 8.7879e-05 | 0.27288 | 0.27288 | 0.27288 | 0.99468 | -0.10116 | 0.99552 | -0.085247 | 14.9933
135 | 0.13237 | 0.033756 | -0.13228 | -0.033701 | 8.804e-05 | 5.4408e-05 | 0.19823 | 0.19823 | 0.19823 | 0.99468 | -0.10116 | 0.99396 | -0.11495 | 10.8917
136 | 0.023189 | 0.0058335 | -0.023176 | -0.0058254 | 1.3217e-05 | 8.0777e-06 | 0.034669 | 0.034669 | 0.034669 | 0.99552 | -0.085247 | 0.9949 | -0.097184 | 9.5244
137 | 0.0033335 | 0.00083482 | -0.0033331 | -0.00083509 | 3.7043e-07 | -2.6341e-07 | 0.0050237 | 0.0050239 | 0.0050239 | 0.98733 | -0.24342 | 0.98721 | -0.24575 | 1.3802
138 | -0.02043 | -0.0051207 | 0.020467 | 0.005143 | 3.6993e-05 | 2.2314e-05 | 0.030631 | 0.030631 | 0.030631 | 0.99246 | -0.14432 | 0.99442 | -0.10638 | 8.4152
139 | 0.0098745 | 0.0024753 | -0.0098724 | -0.0024743 | 2.1075e-06 | 1.0176e-06 | 0.014805 | 0.014805 | 0.014805 | 0.99246 | -0.14432 | 0.99223 | -0.1488 | 4.0674
140 | -0.021276 | -0.0053459 | 0.021279 | 0.0053474 | 2.437e-06 | 1.4765e-06 | 0.031842 | 0.031842 | 0.031842 | 0.99442 | -0.10638 | 0.99454 | -0.10398 | 8.7478
141 | -0.022255 | -0.005592 | 0.022262 | 0.0055964 | 7.2234e-06 | 4.3975e-06 | 0.033303 | 0.033302 | 0.033303 | 0.99454 | -0.10398 | 0.9949 | -0.097184 | 9.1491
142 | 0.0016665 | 0.0004174 | -0.0016665 | -0.00041765 | 5.3134e-08 | -2.5311e-07 | 0.0025118 | 0.0025119 | 0.0025119 | 0.98721 | -0.24575 | 0.98718 | -0.24642 | 0.69009

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48405 | 0.12384

## res_load
| p_mw | q_mvar
0 | 0.00095351 | 0.00023897
1 | 0.0018865 | 0.00047281
2 | 0.0026475 | 0.00066352
3 | 0.004317 | 0.0010819
4 | 0.0060399 | 0.0015137
5 | 0.0038721 | 0.00097043
6 | 0.0028132 | 0.00070506
7 | 0.0021982 | 0.00055092
8 | 0.0040292 | 0.0010098
9 | 0.0013385 | 0.00033546
10 | 0.00059859 | 0.00015002
11 | 0.00093054 | 0.00023322
12 | 0.0024641 | 0.00061756
13 | 0.0026327 | 0.00065981
14 | 0.0010548 | 0.00026435
15 | 0.00092667 | 0.00023225
16 | 0.002461 | 0.00061678
17 | 0.0038919 | 0.0009754
18 | 0.00097192 | 0.00024359
19 | 0.0018826 | 0.00047183
20 | 0.00029187 | 7.315e-05
21 | 0.00058719 | 0.00014716
22 | 0.019726 | 0.0049438
23 | 0.011587 | 0.0029039
24 | 0.0091469 | 0.0022924
25 | 0.010219 | 0.0025612
26 | 0.041829 | 0.010483
27 | 0.072994 | 0.018294
28 | 0.0082367 | 0.0020643
29 | 0.037938 | 0.0095081
30 | 0.0010005 | 0.00025075
31 | 0.00060582 | 0.00015183
32 | 0.0035938 | 0.00090069
33 | 0.00016352 | 4.0983e-05
34 | 0.00017633 | 4.4193e-05
35 | 0.0020207 | 0.00050642
36 | 0.00057993 | 0.00014535
37 | 0.00015368 | 3.8515e-05
38 | 0.0019537 | 0.00048965
39 | 0.0017484 | 0.00043818
40 | 0.0040462 | 0.0010141
41 | 0.029626 | 0.0074249
42 | 0.00031654 | 7.9331e-05
43 | 0.00061795 | 0.00015487
44 | 0.00062386 | 0.00015636
45 | 0.00038452 | 9.6371e-05
46 | 0.00054958 | 0.00013774
47 | 0.00046254 | 0.00011592
48 | 0.0021822 | 0.00054692
49 | 0.001522 | 0.00038146
50 | 0.00045073 | 0.00011296
51 | 0.00028994 | 7.2665e-05
52 | 0.0018458 | 0.00046259
53 | 0.003177 | 0.00079622
54 | 0.00218 | 0.00054636
55 | 0.0024141 | 0.00060502
56 | 0.0010764 | 0.00026976
57 | 0.003671 | 0.00092004
58 | 0.00048856 | 0.00012245
59 | 0.0021523 | 0.00053943
60 | 0.00048856 | 0.00012245
61 | 0.00038837 | 9.7334e-05
62 | 0.00812 | 0.0020351
63 | 0.0068556 | 0.0017182
64 | 0.00088968 | 0.00022298
65 | 0.0022347 | 0.00056007
66 | 0.0012058 | 0.00030219
67 | 0.0006741 | 0.00016894
68 | 0.0039723 | 0.00099555
69 | 0.0013859 | 0.00034735
70 | 0.0023183 | 0.00058103
71 | 0.0016678 | 0.000418
72 | 0.0020316 | 0.00050917
73 | 0.0012718 | 0.00031875
74 | 0.00078618 | 0.00019704
75 | 0.0021137 | 0.00052975
76 | 0.0010199 | 0.0002556
77 | 0.001438 | 0.0003604
78 | 0.0076908 | 0.0019275
79 | 0.0019712 | 0.00049402
80 | 0.0015654 | 0.00039232
81 | 0.0026334 | 0.00065999
82 | 0.0071189 | 0.0017842
83 | 0.00085194 | 0.00021352
84 | 0.00060273 | 0.00015106
85 | 0.0024655 | 0.00061791
86 | 0.0024694 | 0.0006189
87 | 0.0059673 | 0.0014955
88 | 0.0024618 | 0.00061699
89 | 0.0017888 | 0.00044831
90 | 0.0011951 | 0.00029953
91 | 0.0022992 | 0.00057623
92 | 0.0045339 | 0.0011363
93 | 0.0023918 | 0.00059943
94 | 0.0082845 | 0.0020763
95 | 0.0039743 | 0.00099606
96 | 0.00064462 | 0.00016156
97 | 0.00038814 | 9.7278e-05
98 | 0.0030729 | 0.00077013
99 | 0.00092329 | 0.0002314
100 | 0.0011386 | 0.00028536
101 | 0.0014521 | 0.00036393
102 | 0.00093585 | 0.00023455
103 | 0.00090251 | 0.00022619
104 | 0.0044841 | 0.0011238
105 | 0.0010913 | 0.00027351
106 | 0.0028912 | 0.00072459
107 | 0.010555 | 0.0026454
108 | 0.0008094 | 0.00020285
109 | 0.0098724 | 0.0024743
110 | 0.00097616 | 0.00024465
111 | 0.00091362 | 0.00022897
112 | 0.0016666 | 0.00041769
113 | 0.0016665 | 0.00041765
114 | 0.00036551 | 9.1607e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1