## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4164-1_1_2_node_256 | 0.4 | n |  | TRUE
1 | bus_LV_4164-1_1_2_node_254 | 0.4 | n |  | TRUE
2 | bus_LV_4164-1_1_2_node_259 | 0.4 | n |  | TRUE
3 | bus_LV_4164-1_1_2_node_258 | 0.4 | n |  | TRUE
4 | bus_LV_4164-1_1_2_node_260 | 0.4 | n |  | TRUE
5 | bus_LV_4164-1_1_2_node_131 | 0.4 | n |  | TRUE
6 | bus_LV_4164-1_1_2_node_115 | 0.4 | n |  | TRUE
7 | bus_LV_4164-1_1_2_node_132 | 0.4 | n |  | TRUE
8 | bus_LV_4164-1_1_2_node_264 | 0.4 | n |  | TRUE
9 | bus_LV_4164-1_1_2_node_262 | 0.4 | n |  | TRUE
10 | bus_LV_4164-1_1_2_node_263 | 0.4 | n |  | TRUE
11 | bus_LV_4164-1_1_2_node_136 | 0.4 | n |  | TRUE
12 | bus_LV_4164-1_1_2_node_137 | 0.4 | n |  | TRUE
13 | bus_LV_4164-1_1_2_node_138 | 0.4 | n |  | TRUE
14 | bus_LV_4164-1_1_2_node_139 | 0.4 | n |  | TRUE
15 | bus_LV_4164-1_1_2_node_244 | 0.4 | n |  | TRUE
16 | bus_LV_4164-1_1_2_node_148 | 0.4 | n |  | TRUE
17 | bus_LV_4164-1_1_2_node_140 | 0.4 | n |  | TRUE
18 | bus_LV_4164-1_1_2_node_141 | 0.4 | n |  | TRUE
19 | bus_LV_4164-1_1_2_node_116 | 0.4 | n |  | TRUE
20 | bus_LV_4164-1_1_2_node_142 | 0.4 | n |  | TRUE
21 | bus_LV_4164-1_1_2_node_283 | 0.4 | n |  | TRUE
22 | bus_LV_4164-1_1_2_node_265 | 0.4 | n |  | TRUE
23 | bus_LV_4164-1_1_2_node_301 | 0.4 | n |  | TRUE
24 | bus_LV_4164-1_1_2_node_147 | 0.4 | n |  | TRUE
25 | bus_LV_4164-1_1_2_node_270 | 0.4 | n |  | TRUE
26 | bus_LV_4164-1_1_2_node_271 | 0.4 | n |  | TRUE
27 | bus_LV_4164-1_1_2_node_272 | 0.4 | n |  | TRUE
28 | bus_LV_4164-1_1_2_node_282 | 0.4 | n |  | TRUE
29 | bus_LV_4164-1_1_2_node_280 | 0.4 | n |  | TRUE
30 | bus_LV_4164-1_1_2_node_281 | 0.4 | n |  | TRUE
31 | bus_LV_4164-1_1_2_node_246 | 0.4 | n |  | TRUE
32 | bus_LV_4164-1_1_2_node_284 | 0.4 | n |  | TRUE
33 | bus_LV_4164-1_1_2_node_305 | 0.4 | n |  | TRUE
34 | bus_LV_4164-1_1_2_node_285 | 0.4 | n |  | TRUE
35 | bus_LV_4164-1_1_2_node_286 | 0.4 | n |  | TRUE
36 | bus_LV_4164-1_1_2_node_287 | 0.4 | n |  | TRUE
37 | bus_LV_4164-1_1_2_node_288 | 0.4 | n |  | TRUE
38 | bus_LV_4164-1_1_2_node_289 | 0.4 | n |  | TRUE
39 | bus_LV_4164-1_1_2_node_302 | 0.4 | n |  | TRUE
40 | bus_LV_4164-1_1_2_node_293 | 0.4 | n |  | TRUE
41 | bus_LV_4164-1_1_2_node_290 | 0.4 | n |  | TRUE
42 | bus_LV_4164-1_1_2_node_291 | 0.4 | n |  | TRUE
43 | bus_LV_4164-1_1_2_node_292 | 0.4 | n |  | TRUE
44 | bus_LV_4164-1_1_2_node_294 | 0.4 | n |  | TRUE
45 | bus_LV_4164-1_1_2_node_308 | 0.4 | n |  | TRUE
46 | bus_LV_4164-1_1_2_node_295 | 0.4 | n |  | TRUE
47 | bus_LV_4164-1_1_2_node_296 | 0.4 | n |  | TRUE
48 | bus_LV_4164-1_1_2_node_297 | 0.4 | n |  | TRUE
49 | bus_LV_4164-1_1_2_node_298 | 0.4 | n |  | TRUE
50 | bus_LV_4164-1_1_2_node_299 | 0.4 | n |  | TRUE
51 | bus_LV_4164-1_1_2_node_300 | 0.4 | n |  | TRUE
52 | bus_LV_4164-1_1_2_node_309 | 0.4 | n |  | TRUE
53 | bus_LV_4164-1_1_2_node_303 | 0.4 | n |  | TRUE
54 | bus_LV_4164-1_1_2_node_304 | 0.4 | n |  | TRUE
55 | bus_LV_4164-1_1_2_node_306 | 0.4 | n |  | TRUE
56 | bus_LV_4164-1_1_2_node_307 | 0.4 | n |  | TRUE
57 | bus_LV_4164-1_1_2_node_112 | 0.4 | n |  | TRUE
58 | bus_LV_4164-1_1_2_node_113 | 0.4 | n |  | TRUE
59 | bus_LV_4164-1_1_2_node_114 | 0.4 | n |  | TRUE
60 | bus_LV_4164-1_1_2_node_241 | 0.4 | n |  | TRUE
61 | bus_LV_4164-1_1_2_node_242 | 0.4 | n |  | TRUE
62 | bus_LV_4164-1_1_2_node_243 | 0.4 | n |  | TRUE
63 | bus_LV_4164-1_1_2_node_245 | 0.4 | n |  | TRUE
64 | bus_LV_4164-1_1_2_node_252 | 0.4 | n |  | TRUE
65 | bus_LV_4164-1_1_2_node_253 | 0.4 | n |  | TRUE
66 | bus_LV_4164-1_1_2_node_255 | 0.4 | n |  | TRUE
67 | bus_MV_0_node_131 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4164-1_1_2_load_256 | 0 | 0.00037754 | 9.4621e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4164-1_1_2_load_254 | 1 | 0.0027412 | 0.00068702 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4164-1_1_2_load_258 | 3 | 0.00085299 | 0.00021378 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4164-1_1_2_load_115 | 6 | 0.00071055 | 0.00017808 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4164-1_1_2_load_132 | 7 | 0.00022857 | 5.7285e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4164-1_1_2_load_262 | 9 | 0.00036056 | 9.0366e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4164-1_1_2_load_263 | 10 | 0.00081239 | 0.0002036 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4164-1_1_2_load_136 | 11 | 0.0011151 | 0.00027946 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4164-1_1_2_load_137 | 12 | 0.0027908 | 0.00069944 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4164-1_1_2_load_139 | 14 | 0.0029676 | 0.00074374 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4164-1_1_2_load_148 | 16 | 0.0016551 | 0.00041481 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4164-1_1_2_load_140 | 17 | 0.0031333 | 0.00078528 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4164-1_1_2_load_141 | 18 | 0.0068297 | 0.0017117 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4164-1_1_2_load_142 | 20 | 0.0024303 | 0.00060909 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4164-1_1_2_load_301 | 23 | 0.00027729 | 6.9496e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4164-1_1_2_load_147 | 24 | 0.00094625 | 0.00023715 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4164-1_1_2_load_270 | 25 | 0.00017144 | 4.2968e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4164-1_1_2_load_271 | 26 | 0.00060323 | 0.00015118 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4164-1_1_2_load_282 | 28 | 0.0026074 | 0.00065348 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4164-1_1_2_load_280 | 29 | 0.0001598 | 4.005e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4164-1_1_2_load_281 | 30 | 0.0014975 | 0.0003753 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4164-1_1_2_load_284 | 32 | 0.0010372 | 0.00025996 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4164-1_1_2_load_305 | 33 | 0.0021207 | 0.0005315 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4164-1_1_2_load_285 | 34 | 0.0010707 | 0.00026835 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4164-1_1_2_load_286 | 35 | 0.000688 | 0.00017243 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4164-1_1_2_load_287 | 36 | 0.00066268 | 0.00016608 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4164-1_1_2_load_288 | 37 | 0.0011144 | 0.0002793 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4164-1_1_2_load_289 | 38 | 0.001051 | 0.0002634 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4164-1_1_2_load_302 | 39 | 0.00031549 | 7.9068e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4164-1_1_2_load_293 | 40 | 0.00028515 | 7.1466e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4164-1_1_2_load_290 | 41 | 0.0012064 | 0.00030234 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4164-1_1_2_load_291 | 42 | 0.00032973 | 8.2637e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4164-1_1_2_load_292 | 43 | 0.0010017 | 0.00025105 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4164-1_1_2_load_308 | 45 | 0.0034884 | 0.00087428 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4164-1_1_2_load_295 | 46 | 0.00078775 | 0.00019743 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4164-1_1_2_load_296 | 47 | 0.00042659 | 0.00010691 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4164-1_1_2_load_298 | 49 | 0.00054689 | 0.00013706 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4164-1_1_2_load_299 | 50 | 0.00064883 | 0.00016261 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4164-1_1_2_load_300 | 51 | 0.00051086 | 0.00012803 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4164-1_1_2_load_309 | 52 | 0.00025637 | 6.4253e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4164-1_1_2_load_303 | 53 | 0.0012434 | 0.00031164 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4164-1_1_2_load_304 | 54 | 0.00093714 | 0.00023487 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4164-1_1_2_load_306 | 55 | 0.0027413 | 0.00068703 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4164-1_1_2_load_307 | 56 | 0.00039566 | 9.9161e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4164-1_1_2_load_112 | 57 | 0.00077585 | 0.00019445 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4164-1_1_2_load_113 | 58 | 0.00088092 | 0.00022078 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4164-1_1_2_load_114 | 59 | 0.0010819 | 0.00027116 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4164-1_1_2_load_241 | 60 | 0.0003829 | 9.5963e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4164-1_1_2_load_245 | 63 | 0.00088005 | 0.00022056 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4164-1_1_2_load_252 | 64 | 0.00071156 | 0.00017833 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4164-1_1_2_load_253 | 65 | 0.0012828 | 0.00032151 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4164-1_1_2_load_255 | 66 | 0.00040927 | 0.00010257 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4164-1_1_2_line_0 |  | 0 | 1 | 0.0089587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4164-1_1_2_line_1 |  | 0 | 2 | 0.057062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4164-1_1_2_line_2 |  | 1 | 64 | 0.0068902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4164-1_1_2_line_3 |  | 2 | 3 | 0.017726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4164-1_1_2_line_4 |  | 3 | 4 | 0.011804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4164-1_1_2_line_5 |  | 4 | 9 | 0.016517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4164-1_1_2_line_6 |  | 4 | 10 | 0.0059837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4164-1_1_2_line_7 |  | 5 | 6 | 0.30935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4164-1_1_2_line_8 |  | 5 | 7 | 0.15989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4164-1_1_2_line_9 |  | 6 | 12 | 0.21441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4164-1_1_2_line_10 |  | 6 | 58 | 0.0090474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4164-1_1_2_line_11 |  | 7 | 8 | 0.0073343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4164-1_1_2_line_12 |  | 8 | 22 | 0.1033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4164-1_1_2_line_13 |  | 10 | 21 | 0.017786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4164-1_1_2_line_14 |  | 11 | 12 | 0.0074859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4164-1_1_2_line_15 |  | 11 | 13 | 0.0057338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4164-1_1_2_line_16 |  | 12 | 14 | 0.067815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4164-1_1_2_line_17 |  | 13 | 15 | 0.26051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4164-1_1_2_line_18 |  | 14 | 16 | 0.00045164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4164-1_1_2_line_19 |  | 15 | 25 | 0.082219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4164-1_1_2_line_20 |  | 15 | 61 | 0.16895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4164-1_1_2_line_21 |  | 16 | 24 | 0.022592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4164-1_1_2_line_22 |  | 17 | 18 | 0.0038049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4164-1_1_2_line_23 |  | 17 | 19 | 0.48656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4164-1_1_2_line_24 |  | 18 | 20 | 0.0022019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4164-1_1_2_line_25 |  | 19 | 59 | 0.18713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4164-1_1_2_line_26 |  | 21 | 32 | 0.02698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4164-1_1_2_line_27 |  | 21 | 28 | 0.0097376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4164-1_1_2_line_28 |  | 22 | 23 | 0.013194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4164-1_1_2_line_29 |  | 23 | 49 | 0.021242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4164-1_1_2_line_30 |  | 26 | 27 | 0.024055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4164-1_1_2_line_31 |  | 27 | 28 | 0.032288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4164-1_1_2_line_32 |  | 27 | 29 | 0.0087729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4164-1_1_2_line_33 |  | 29 | 30 | 0.019833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4164-1_1_2_line_34 |  | 30 | 31 | 0.14393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4164-1_1_2_line_35 |  | 31 | 62 | 0.0425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4164-1_1_2_line_36 |  | 32 | 33 | 0.003422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4164-1_1_2_line_37 |  | 33 | 53 | 0.009305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4164-1_1_2_line_38 |  | 34 | 35 | 0.012174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4164-1_1_2_line_39 |  | 34 | 36 | 0.017927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4164-1_1_2_line_40 |  | 35 | 37 | 0.018079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4164-1_1_2_line_41 |  | 36 | 38 | 0.013844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4164-1_1_2_line_42 |  | 37 | 39 | 0.011669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4164-1_1_2_line_43 |  | 38 | 40 | 0.0084139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4164-1_1_2_line_44 |  | 39 | 50 | 0.02231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4164-1_1_2_line_45 |  | 40 | 42 | 0.0016946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4164-1_1_2_line_46 |  | 41 | 42 | 0.019388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4164-1_1_2_line_47 |  | 41 | 43 | 0.0096899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4164-1_1_2_line_48 |  | 43 | 44 | 0.012807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4164-1_1_2_line_49 |  | 44 | 45 | 0.023752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4164-1_1_2_line_50 |  | 45 | 56 | 0.0050431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4164-1_1_2_line_51 |  | 46 | 47 | 0.0097494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4164-1_1_2_line_52 |  | 46 | 48 | 0.047188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4164-1_1_2_line_53 |  | 47 | 49 | 0.034826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4164-1_1_2_line_54 |  | 48 | 50 | 0.020179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4164-1_1_2_line_55 |  | 48 | 51 | 0.016037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4164-1_1_2_line_56 |  | 51 | 52 | 0.0051972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4164-1_1_2_line_57 |  | 53 | 54 | 0.0088919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4164-1_1_2_line_58 |  | 54 | 55 | 0.01579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4164-1_1_2_line_59 |  | 55 | 56 | 0.0029897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4164-1_1_2_line_60 |  | 57 | 58 | 0.00092593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4164-1_1_2_line_61 |  | 57 | 59 | 0.035881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4164-1_1_2_line_62 |  | 60 | 61 | 0.05183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4164-1_1_2_line_63 |  | 62 | 63 | 0.036277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4164-1_1_2_line_64 |  | 64 | 65 | 0.033909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4164-1_1_2_line_65 |  | 65 | 66 | 0.095849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4164-1_1_2_trafo_131 | 0.63 MVA 20/0.4 kV | 67 | 5 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2651147.8452 | 1265178.8435 | 2651147.956 | 1265187.8015
1 | 2651171.2813 | 1265238.7481 | 2651160.7388 | 1265223.1566 | 2651151.781 | 1265207.1564 | 2651148.0411 | 1265194.6817 | 2651147.956 | 1265187.8015
2 | 2651147.5814 | 1265171.9877 | 2651147.7664 | 1265172.4742 | 2651147.8452 | 1265178.8435
3 | 2651171.2813 | 1265238.7481 | 2651187.2094 | 1265230.97
4 | 2651197.8161 | 1265225.7904 | 2651187.2094 | 1265230.97
5 | 2651197.8161 | 1265225.7904 | 2651194.3345 | 1265241.9365
6 | 2651197.8161 | 1265225.7904 | 2651199.0425 | 1265222.4319 | 2651199.6625 | 1265220.1048
7 | 2651894.5712 | 1265190.4686 | 2651636.9235 | 1265019.2565
8 | 2651636.9235 | 1265019.2565 | 2651605.1092 | 1264972.556 | 2651563.7814 | 1264923.5155 | 2651556.4482 | 1264916.4576 | 2651544.0827 | 1264911.3461 | 2651533.591 | 1264909.8314 | 2651528.5012 | 1264909.9829
9 | 2651815.867 | 1265389.9062 | 2651894.5712 | 1265190.4686
10 | 2651903.3917 | 1265192.4824 | 2651898.6544 | 1265191.4056 | 2651894.5712 | 1265190.4686
11 | 2651521.1702 | 1264910.2012 | 2651528.5012 | 1264909.9829
12 | 2651421.2679 | 1264899.4353 | 2651433.3631 | 1264898.4175 | 2651447.2888 | 1264896.4594 | 2651458.9452 | 1264900.8528 | 2651473.2213 | 1264906.2143 | 2651488.2141 | 1264912.2936 | 2651502.763 | 1264913.132 | 2651521.1702 | 1264910.2012
13 | 2651204.2415 | 1265202.9183 | 2651199.6625 | 1265220.1048
14 | 2651815.867 | 1265389.9062 | 2651808.7331 | 1265387.6378
15 | 2651803.2689 | 1265385.9003 | 2651808.7331 | 1265387.6378
16 | 2651815.867 | 1265389.9062 | 2651880.4934 | 1265410.4555
17 | 2651803.2689 | 1265385.9003 | 2651664.2112 | 1265606.1894
18 | 2651880.9238 | 1265410.5923 | 2651880.4934 | 1265410.4555
19 | 2651664.2112 | 1265606.1894 | 2651654.6892 | 1265601.5585 | 2651642.7202 | 1265590.8795 | 2651603.2977 | 1265564.772 | 2651595.9579 | 1265560.8826
20 | 2651553.2772 | 1265486.412 | 2651563.0003 | 1265493.046 | 2651577.7811 | 1265497.3446 | 2651590.3691 | 1265502.7028 | 2651599.5855 | 1265509.5882 | 2651621.7366 | 1265536.4344 | 2651633.3608 | 1265552.1139 | 2651645.5526 | 1265571.7681 | 2651664.2112 | 1265606.1894
21 | 2651902.4541 | 1265417.4383 | 2651880.9238 | 1265410.5923
22 | 2652202.7435 | 1264669.0894 | 2652204.0743 | 1264665.5249
23 | 2652106.0332 | 1265145.9399 | 2652202.7435 | 1264669.0894
24 | 2652204.8445 | 1264663.462 | 2652204.0743 | 1264665.5249
25 | 2652106.0332 | 1265145.9399 | 2652099.3885 | 1265146.2927 | 2652091.4289 | 1265155.7295 | 2652077.9904 | 1265174.2247 | 2652071.2897 | 1265181.8046 | 2652059.6119 | 1265189.3517 | 2652039.3687 | 1265196.4677 | 2652019.1004 | 1265197.8905 | 2651988.8884 | 1265198.9257 | 2651955.2412 | 1265199.2747 | 2651939.6995 | 1265197.9585
26 | 2651204.2415 | 1265202.9183 | 2651204.3 | 1265176.1771 | 2651204.3259 | 1265175.9397
27 | 2651204.2415 | 1265202.9183 | 2651213.444 | 1265206.1017
28 | 2651421.2679 | 1264899.4353 | 2651411.6702 | 1264908.4889
29 | 2651411.6702 | 1264908.4889 | 2651403.8883 | 1264915.8295 | 2651396.3164 | 1264923.1677
30 | 2651244.027 | 1265216.3059 | 2651248.1409 | 1265224.692 | 2651258.703 | 1265234.936
31 | 2651244.027 | 1265216.3059 | 2651236.4971 | 1265214.5505 | 2651224.1214 | 1265209.7954 | 2651213.444 | 1265206.1017
32 | 2651244.027 | 1265216.3059 | 2651248.2093 | 1265216.8091 | 2651252.6358 | 1265215.7121
33 | 2651252.6358 | 1265215.7121 | 2651262.8187 | 1265213.1886 | 2651270.4584 | 1265207.8113
34 | 2651385.4091 | 1265132.3711 | 2651375.9697 | 1265130.2542 | 2651366.7461 | 1265130.1741 | 2651353.766 | 1265136.8996 | 2651323.5745 | 1265156.374 | 2651304.8796 | 1265170.8557 | 2651291.1994 | 1265185.3921 | 2651278.7515 | 1265201.9741 | 2651270.4584 | 1265207.8113
35 | 2651385.4091 | 1265132.3711 | 2651378.8503 | 1265146.2465 | 2651376.9268 | 1265163.0976 | 2651378.0284 | 1265173.2368
36 | 2651204.3259 | 1265175.9397 | 2651204.6972 | 1265172.5379
37 | 2651205.707 | 1265163.2878 | 2651204.6972 | 1265172.5379
38 | 2651270.3611 | 1265041.2013 | 2651279.9699 | 1265033.7269
39 | 2651270.3611 | 1265041.2013 | 2651265.8308 | 1265044.7254 | 2651258.4886 | 1265050.8329 | 2651257.1008 | 1265053.0758
40 | 2651279.9699 | 1265033.7269 | 2651288.7038 | 1265026.9329 | 2651294.7605 | 1265023.3952
41 | 2651249.8812 | 1265064.8863 | 2651250.523 | 1265063.7066 | 2651257.1008 | 1265053.0758
42 | 2651304.8362 | 1265017.5099 | 2651294.7605 | 1265023.3952
43 | 2651245.8603 | 1265072.2772 | 2651249.8812 | 1265064.8863
44 | 2651304.8362 | 1265017.5099 | 2651324.1005 | 1265006.2576
45 | 2651245.0504 | 1265073.7658 | 2651245.8603 | 1265072.2772
46 | 2651235.7853 | 1265090.7962 | 2651245.0504 | 1265073.7658
47 | 2651235.7853 | 1265090.7962 | 2651231.1546 | 1265099.3079
48 | 2651226.1589 | 1265111.0856 | 2651230.0461 | 1265101.3455 | 2651231.1546 | 1265099.3079
49 | 2651226.1589 | 1265111.0856 | 2651218.5155 | 1265130.2556 | 2651217.1463 | 1265133.0523
50 | 2651214.929 | 1265137.5817 | 2651217.1463 | 1265133.0523
51 | 2651371.7535 | 1264959.9935 | 2651376.6239 | 1264951.5477
52 | 2651341.5252 | 1264996.0797 | 2651368.4996 | 1264965.6362 | 2651371.7535 | 1264959.9935
53 | 2651376.6239 | 1264951.5477 | 2651388.7756 | 1264930.4756 | 2651396.3164 | 1264923.1677
54 | 2651341.5252 | 1264996.0797 | 2651324.1005 | 1265006.2576
55 | 2651341.5252 | 1264996.0797 | 2651346.7519 | 1265002.0628 | 2651351.1566 | 1265008.8513
56 | 2651351.1566 | 1265008.8513 | 2651351.3664 | 1265009.1747 | 2651353.3709 | 1265013.549
57 | 2651205.707 | 1265163.2878 | 2651206.6719 | 1265154.4485
58 | 2651206.6719 | 1265154.4485 | 2651206.6719 | 1265154.4485 | 2651213.6144 | 1265140.267
59 | 2651214.929 | 1265137.5817 | 2651213.6144 | 1265140.267
60 | 2651904.2946 | 1265192.6876 | 2651903.3917 | 1265192.4824
61 | 2651904.2946 | 1265192.6876 | 2651920.2301 | 1265196.3096 | 2651939.6995 | 1265197.9585
62 | 2651553.2772 | 1265486.412 | 2651525.8627 | 1265466.4363 | 2651512.9744 | 1265454.0002
63 | 2651378.0284 | 1265173.2368 | 2651368.7132 | 1265180.2276 | 2651360.0168 | 1265184.4663 | 2651354.4247 | 1265185.8966 | 2651345.2409 | 1265185.9649
64 | 2651147.5814 | 1265171.9877 | 2651139.7854 | 1265151.4899 | 2651133.9962 | 1265141.0027
65 | 2651133.9962 | 1265141.0027 | 2651129.9175 | 1265133.6139 | 2651126.1744 | 1265121.4949 | 2651126.3507 | 1265114.1689 | 2651128.9003 | 1265102.3379 | 2651135.0788 | 1265089.7154 | 2651149.2417 | 1265069.8456 | 2651157.8759 | 1265055.3875

## bus_geodata
| x | y | coords
0 | 2651147.956 | 1265187.8015
1 | 2651147.8452 | 1265178.8435
2 | 2651171.2813 | 1265238.7481
3 | 2651187.2094 | 1265230.97
4 | 2651197.8161 | 1265225.7904
5 | 2651636.9235 | 1265019.2565
6 | 2651894.5712 | 1265190.4686
7 | 2651528.5012 | 1264909.9829
8 | 2651521.1702 | 1264910.2012
9 | 2651194.3345 | 1265241.9365
10 | 2651199.6625 | 1265220.1048
11 | 2651808.7331 | 1265387.6378
12 | 2651815.867 | 1265389.9062
13 | 2651803.2689 | 1265385.9003
14 | 2651880.4934 | 1265410.4555
15 | 2651664.2112 | 1265606.1894
16 | 2651880.9238 | 1265410.5923
17 | 2652202.7435 | 1264669.0894
18 | 2652204.0743 | 1264665.5249
19 | 2652106.0332 | 1265145.9399
20 | 2652204.8445 | 1264663.462
21 | 2651204.2415 | 1265202.9183
22 | 2651421.2679 | 1264899.4353
23 | 2651411.6702 | 1264908.4889
24 | 2651902.4541 | 1265417.4383
25 | 2651595.9579 | 1265560.8826
26 | 2651258.703 | 1265234.936
27 | 2651244.027 | 1265216.3059
28 | 2651213.444 | 1265206.1017
29 | 2651252.6358 | 1265215.7121
30 | 2651270.4584 | 1265207.8113
31 | 2651385.4091 | 1265132.3711
32 | 2651204.3259 | 1265175.9397
33 | 2651204.6972 | 1265172.5379
34 | 2651270.3611 | 1265041.2013
35 | 2651279.9699 | 1265033.7269
36 | 2651257.1008 | 1265053.0758
37 | 2651294.7605 | 1265023.3952
38 | 2651249.8812 | 1265064.8863
39 | 2651304.8362 | 1265017.5099
40 | 2651245.8603 | 1265072.2772
41 | 2651235.7853 | 1265090.7962
42 | 2651245.0504 | 1265073.7658
43 | 2651231.1546 | 1265099.3079
44 | 2651226.1589 | 1265111.0856
45 | 2651217.1463 | 1265133.0523
46 | 2651371.7535 | 1264959.9935
47 | 2651376.6239 | 1264951.5477
48 | 2651341.5252 | 1264996.0797
49 | 2651396.3164 | 1264923.1677
50 | 2651324.1005 | 1265006.2576
51 | 2651351.1566 | 1265008.8513
52 | 2651353.3709 | 1265013.549
53 | 2651205.707 | 1265163.2878
54 | 2651206.6719 | 1265154.4485
55 | 2651213.6144 | 1265140.267
56 | 2651214.929 | 1265137.5817
57 | 2651904.2946 | 1265192.6876
58 | 2651903.3917 | 1265192.4824
59 | 2651939.6995 | 1265197.9585
60 | 2651512.9744 | 1265454.0002
61 | 2651553.2772 | 1265486.412
62 | 2651378.0284 | 1265173.2368
63 | 2651345.2409 | 1265185.9649
64 | 2651147.5814 | 1265171.9877
65 | 2651133.9962 | 1265141.0027
66 | 2651157.8759 | 1265055.3875
67 | 2651636.9235 | 1265019.2565

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1