## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5428-5_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5428-5_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5428-5_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5428-5_0_3_node_35 | 0.4 | n |  | TRUE
4 | bus_LV_5428-5_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_5428-5_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_5428-5_0_3_node_149 | 0.4 | n |  | TRUE
7 | bus_LV_5428-5_0_3_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_5428-5_0_3_node_135 | 0.4 | n |  | TRUE
9 | bus_LV_5428-5_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_5428-5_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_5428-5_0_3_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_5428-5_0_3_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_5428-5_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_5428-5_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_5428-5_0_3_node_72 | 0.4 | n |  | TRUE
16 | bus_LV_5428-5_0_3_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_5428-5_0_3_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_5428-5_0_3_node_71 | 0.4 | n |  | TRUE
19 | bus_LV_5428-5_0_3_node_73 | 0.4 | n |  | TRUE
20 | bus_LV_5428-5_0_3_node_74 | 0.4 | n |  | TRUE
21 | bus_LV_5428-5_0_3_node_147 | 0.4 | n |  | TRUE
22 | bus_LV_5428-5_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_5428-5_0_3_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_5428-5_0_3_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_5428-5_0_3_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_5428-5_0_3_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_5428-5_0_3_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_5428-5_0_3_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_5428-5_0_3_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_5428-5_0_3_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_5428-5_0_3_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_5428-5_0_3_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_5428-5_0_3_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_5428-5_0_3_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_5428-5_0_3_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_5428-5_0_3_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_5428-5_0_3_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_5428-5_0_3_node_148 | 0.4 | n |  | TRUE
39 | bus_LV_5428-5_0_3_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_5428-5_0_3_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_5428-5_0_3_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_5428-5_0_3_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_5428-5_0_3_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_5428-5_0_3_node_46 | 0.4 | n |  | TRUE
45 | bus_LV_5428-5_0_3_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_5428-5_0_3_node_44 | 0.4 | n |  | TRUE
47 | bus_LV_5428-5_0_3_node_38 | 0.4 | n |  | TRUE
48 | bus_LV_5428-5_0_3_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_5428-5_0_3_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_5428-5_0_3_node_41 | 0.4 | n |  | TRUE
51 | bus_LV_5428-5_0_3_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_5428-5_0_3_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_5428-5_0_3_node_45 | 0.4 | n |  | TRUE
54 | bus_LV_5428-5_0_3_node_55 | 0.4 | n |  | TRUE
55 | bus_LV_5428-5_0_3_node_69 | 0.4 | n |  | TRUE
56 | bus_LV_5428-5_0_3_node_56 | 0.4 | n |  | TRUE
57 | bus_LV_5428-5_0_3_node_68 | 0.4 | n |  | TRUE
58 | bus_LV_5428-5_0_3_node_47 | 0.4 | n |  | TRUE
59 | bus_LV_5428-5_0_3_node_48 | 0.4 | n |  | TRUE
60 | bus_LV_5428-5_0_3_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_5428-5_0_3_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_5428-5_0_3_node_51 | 0.4 | n |  | TRUE
63 | bus_LV_5428-5_0_3_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_5428-5_0_3_node_61 | 0.4 | n |  | TRUE
65 | bus_LV_5428-5_0_3_node_53 | 0.4 | n |  | TRUE
66 | bus_LV_5428-5_0_3_node_62 | 0.4 | n |  | TRUE
67 | bus_LV_5428-5_0_3_node_57 | 0.4 | n |  | TRUE
68 | bus_LV_5428-5_0_3_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_5428-5_0_3_node_59 | 0.4 | n |  | TRUE
70 | bus_LV_5428-5_0_3_node_60 | 0.4 | n |  | TRUE
71 | bus_LV_5428-5_0_3_node_65 | 0.4 | n |  | TRUE
72 | bus_LV_5428-5_0_3_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_5428-5_0_3_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_5428-5_0_3_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_5428-5_0_3_node_70 | 0.4 | n |  | TRUE
76 | bus_LV_5428-5_0_3_node_67 | 0.4 | n |  | TRUE
77 | bus_MV_313_0_node_2 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5428-5_0_3_load_0 | 0 | 0.00016921 | 4.2409e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5428-5_0_3_load_3 | 4 | 0.00035905 | 8.9987e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5428-5_0_3_load_149 | 6 | 0.0027554 | 0.00069057 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5428-5_0_3_load_135 | 8 | 0.00085844 | 0.00021515 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5428-5_0_3_load_5 | 9 | 0.00024867 | 6.2323e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5428-5_0_3_load_6 | 10 | 0.00062353 | 0.00015627 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5428-5_0_3_load_14 | 11 | 0.025102 | 0.0062912 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5428-5_0_3_load_15 | 12 | 0.067544 | 0.016928 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5428-5_0_3_load_7 | 13 | 0.012127 | 0.0030393 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5428-5_0_3_load_72 | 15 | 0.0043691 | 0.001095 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5428-5_0_3_load_9 | 16 | 0.012613 | 0.0031612 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5428-5_0_3_load_71 | 18 | 0.0013978 | 0.00035031 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5428-5_0_3_load_74 | 20 | 0.0034773 | 0.00087149 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5428-5_0_3_load_147 | 21 | 0.0053536 | 0.0013417 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5428-5_0_3_load_13 | 22 | 0.019596 | 0.0049112 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5428-5_0_3_load_12 | 23 | 0.008983 | 0.0022513 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5428-5_0_3_load_24 | 25 | 0.0074157 | 0.0018586 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5428-5_0_3_load_28 | 30 | 0.0080716 | 0.0020229 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5428-5_0_3_load_25 | 31 | 0.008012 | 0.002008 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5428-5_0_3_load_20 | 32 | 0.017071 | 0.0042784 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5428-5_0_3_load_26 | 33 | 0.064286 | 0.016112 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5428-5_0_3_load_27 | 36 | 0.016051 | 0.0040228 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5428-5_0_3_load_148 | 38 | 0.0080477 | 0.0020169 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5428-5_0_3_load_33 | 40 | 0.00077193 | 0.00019346 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5428-5_0_3_load_31 | 41 | 0.0010433 | 0.00026148 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5428-5_0_3_load_37 | 42 | 0.0013183 | 0.00033039 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5428-5_0_3_load_34 | 43 | 0.0020594 | 0.00051613 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5428-5_0_3_load_36 | 45 | 0.00048227 | 0.00012087 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5428-5_0_3_load_38 | 47 | 0.0013233 | 0.00033165 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5428-5_0_3_load_39 | 48 | 0.001733 | 0.00043434 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5428-5_0_3_load_40 | 49 | 0.00088854 | 0.00022269 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5428-5_0_3_load_41 | 50 | 0.0030981 | 0.00077645 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5428-5_0_3_load_42 | 51 | 0.0036282 | 0.00090932 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5428-5_0_3_load_43 | 52 | 0.0018374 | 0.0004605 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5428-5_0_3_load_69 | 55 | 0.0038233 | 0.0009582 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5428-5_0_3_load_56 | 56 | 0.0017077 | 0.000428 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5428-5_0_3_load_68 | 57 | 0.0035201 | 0.00088222 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5428-5_0_3_load_47 | 58 | 0.0012305 | 0.0003084 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5428-5_0_3_load_48 | 59 | 0.0023436 | 0.00058737 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5428-5_0_3_load_50 | 61 | 0.0017115 | 0.00042895 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5428-5_0_3_load_51 | 62 | 0.0017149 | 0.0004298 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5428-5_0_3_load_52 | 63 | 0.0029265 | 0.00073346 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5428-5_0_3_load_61 | 64 | 0.0017282 | 0.00043313 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5428-5_0_3_load_53 | 65 | 0.0020721 | 0.00051932 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5428-5_0_3_load_62 | 66 | 0.0008826 | 0.0002212 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5428-5_0_3_load_57 | 67 | 0.0029171 | 0.0007311 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5428-5_0_3_load_58 | 68 | 0.001717 | 0.00043033 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5428-5_0_3_load_59 | 69 | 0.001707 | 0.0004278 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5428-5_0_3_load_60 | 70 | 0.00099561 | 0.00024952 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5428-5_0_3_load_66 | 72 | 0.0017095 | 0.00042845 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5428-5_0_3_load_64 | 73 | 0.0017098 | 0.00042851 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5428-5_0_3_load_63 | 74 | 0.001696 | 0.00042505 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5428-5_0_3_load_70 | 75 | 0.00079972 | 0.00020043 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5428-5_0_3_load_67 | 76 | 0.0035194 | 0.00088205 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 33 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5428-5_0_3_line_0 |  | 0 | 1 | 0.088892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5428-5_0_3_line_1 |  | 0 | 2 | 0.020051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5428-5_0_3_line_2 |  | 1 | 3 | 0.39027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5428-5_0_3_line_3 |  | 2 | 4 | 0.025927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5428-5_0_3_line_4 |  | 2 | 5 | 0.004496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5428-5_0_3_line_5 |  | 3 | 6 | 0.020635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5428-5_0_3_line_6 |  | 3 | 7 | 0.097974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5428-5_0_3_line_7 |  | 5 | 8 | 0.028757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5428-5_0_3_line_8 |  | 5 | 9 | 0.063616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5428-5_0_3_line_9 |  | 7 | 43 | 0.069384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5428-5_0_3_line_10 |  | 7 | 41 | 0.02847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5428-5_0_3_line_11 |  | 9 | 10 | 0.090938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5428-5_0_3_line_12 |  | 11 | 12 | 0.0065138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5428-5_0_3_line_13 |  | 12 | 26 | 0.052318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5428-5_0_3_line_14 |  | 13 | 14 | 0.021333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5428-5_0_3_line_15 |  | 13 | 15 | 0.10133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5428-5_0_3_line_16 |  | 14 | 16 | 0.0062916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5428-5_0_3_line_17 |  | 14 | 17 | 0.026556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5428-5_0_3_line_18 |  | 15 | 19 | 0.092082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5428-5_0_3_line_19 |  | 15 | 18 | 0.026885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5428-5_0_3_line_20 |  | 17 | 22 | 0.03818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5428-5_0_3_line_21 |  | 17 | 23 | 0.024887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5428-5_0_3_line_22 |  | 19 | 20 | 0.033868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5428-5_0_3_line_23 |  | 20 | 21 | 0.028149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5428-5_0_3_line_24 |  | 22 | 24 | 0.012895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5428-5_0_3_line_25 |  | 24 | 25 | 0.051377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5428-5_0_3_line_26 |  | 25 | 31 | 0.064356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5428-5_0_3_line_27 |  | 26 | 27 | 0.05617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_5428-5_0_3_line_28 |  | 26 | 28 | 0.004044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5428-5_0_3_line_29 |  | 26 | 29 | 0.010764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5428-5_0_3_line_30 |  | 27 | 30 | 0.015941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_5428-5_0_3_line_31 |  | 28 | 31 | 0.02748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5428-5_0_3_line_32 |  | 29 | 32 | 0.010514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5428-5_0_3_line_33 |  | 30 | 33 | 0.041575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_5428-5_0_3_line_34 |  | 32 | 39 | 0.054622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5428-5_0_3_line_35 |  | 33 | 36 | 0.044174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5428-5_0_3_line_36 |  | 34 | 35 | 0.024049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5428-5_0_3_line_37 |  | 34 | 36 | 0.0346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5428-5_0_3_line_38 |  | 35 | 40 | 0.018899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5428-5_0_3_line_39 |  | 35 | 41 | 0.043702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5428-5_0_3_line_40 |  | 37 | 38 | 0.009382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5428-5_0_3_line_41 |  | 37 | 39 | 0.008088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5428-5_0_3_line_42 |  | 40 | 42 | 0.032632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5428-5_0_3_line_43 |  | 42 | 45 | 0.014185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5428-5_0_3_line_44 |  | 43 | 44 | 0.059167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5428-5_0_3_line_45 |  | 44 | 46 | 0.027403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5428-5_0_3_line_46 |  | 45 | 47 | 0.023739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5428-5_0_3_line_47 |  | 46 | 53 | 0.043355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5428-5_0_3_line_48 |  | 46 | 52 | 0.067413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5428-5_0_3_line_49 |  | 47 | 48 | 0.032736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5428-5_0_3_line_50 |  | 48 | 49 | 0.0053895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5428-5_0_3_line_51 |  | 50 | 51 | 0.0013785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5428-5_0_3_line_52 |  | 50 | 52 | 0.026307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5428-5_0_3_line_53 |  | 53 | 54 | 0.09759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5428-5_0_3_line_54 |  | 53 | 55 | 0.043597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5428-5_0_3_line_55 |  | 54 | 56 | 0.0028975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5428-5_0_3_line_56 |  | 55 | 57 | 0.031551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5428-5_0_3_line_57 |  | 56 | 67 | 0.016092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5428-5_0_3_line_58 |  | 57 | 76 | 0.03091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5428-5_0_3_line_59 |  | 58 | 59 | 0.01591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5428-5_0_3_line_60 |  | 58 | 60 | 0.0047597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5428-5_0_3_line_61 |  | 60 | 61 | 0.025533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5428-5_0_3_line_62 |  | 60 | 62 | 0.018714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5428-5_0_3_line_63 |  | 61 | 63 | 0.015108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5428-5_0_3_line_64 |  | 62 | 64 | 0.0031469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5428-5_0_3_line_65 |  | 63 | 65 | 0.012915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5428-5_0_3_line_66 |  | 64 | 66 | 0.0043906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5428-5_0_3_line_67 |  | 66 | 74 | 0.02955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5428-5_0_3_line_68 |  | 67 | 68 | 0.011967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5428-5_0_3_line_69 |  | 68 | 69 | 0.018012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5428-5_0_3_line_70 |  | 69 | 70 | 0.0048112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5428-5_0_3_line_71 |  | 70 | 71 | 0.020714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5428-5_0_3_line_72 |  | 71 | 72 | 0.0031832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_5428-5_0_3_line_73 |  | 71 | 73 | 0.012845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5428-5_0_3_line_74 |  | 72 | 75 | 0.014469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_5428-5_0_3_line_75 |  | 73 | 74 | 0.0026029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5428-5_0_3_trafo_26 | 0.63 MVA 20/0.4 kV | 77 | 33 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2513225.861 | 1152351.0874 | 2513196.3054 | 1152384.6227 | 2513185.1371 | 1152397.2914 | 2513167.0865 | 1152417.7761
1 | 2513153.8303 | 1152432.8199 | 2513167.0865 | 1152417.7761
2 | 2513365.9523 | 1151986.83 | 2513225.861 | 1152351.0874
3 | 2513153.8303 | 1152432.8199 | 2513152.6462 | 1152444.355 | 2513155.523 | 1152451.173 | 2513159.3503 | 1152456.9513
4 | 2513150.8552 | 1152436.1982 | 2513153.8303 | 1152432.8199
5 | 2513351.9332 | 1151971.6563 | 2513365.9523 | 1151986.83
6 | 2513440.8079 | 1151929.0626 | 2513432.13 | 1151928.7429 | 2513423.2707 | 1151932.3503 | 2513377.7266 | 1151972.4631 | 2513377.0006 | 1151976.4092 | 2513365.9523 | 1151986.83
7 | 2513131.819 | 1152457.7971 | 2513150.8552 | 1152436.1982
8 | 2513150.8552 | 1152436.1982 | 2513149.3461 | 1152442.7684 | 2513147.1561 | 1152449.4929 | 2513147.1217 | 1152458.7989 | 2513154.9249 | 1152477.7752 | 2513163.6638 | 1152495.7415
9 | 2513440.8079 | 1151929.0626 | 2513399.6882 | 1151884.1612 | 2513393.9481 | 1151877.8927
10 | 2513440.8079 | 1151929.0626 | 2513460.0339 | 1151950.0608
11 | 2513163.6638 | 1152495.7415 | 2513251.1279 | 1152470.8454
12 | 2513573.7122 | 1152140.3404 | 2513578.4924 | 1152135.9156
13 | 2513620.4448 | 1152104.7731 | 2513598.1974 | 1152119.9461 | 2513584.3721 | 1152130.4731 | 2513578.4924 | 1152135.9156
14 | 2513717.2958 | 1151988.5143 | 2513704.0411 | 1151971.7993
15 | 2513704.0411 | 1151971.7993 | 2513716.7018 | 1151871.2609
16 | 2513717.2958 | 1151988.5143 | 2513721.3387 | 1151993.335
17 | 2513691.5827 | 1151995.4317 | 2513698.856 | 1151993.6152 | 2513717.2958 | 1151988.5143
18 | 2513791.6167 | 1151916.784 | 2513777.873 | 1151917.0034 | 2513770.179 | 1151916.2466 | 2513763.8842 | 1151914.0466 | 2513756.2698 | 1151909.2085 | 2513733.1703 | 1151889.1501 | 2513726.4087 | 1151882.2318 | 2513716.7018 | 1151871.2609
19 | 2513716.7018 | 1151871.2609 | 2513709.5171 | 1151863.1406 | 2513708.7448 | 1151856.3922 | 2513713.4323 | 1151848.4178
20 | 2513691.5827 | 1151995.4317 | 2513686.0078 | 1151996.857 | 2513677.3667 | 1152000.1607 | 2513658.6639 | 1152013.8456
21 | 2513691.5827 | 1151995.4317 | 2513692.6786 | 1151997.9842 | 2513697.0532 | 1152005.9817 | 2513705.3333 | 1152015.9946
22 | 2513791.6167 | 1151916.784 | 2513788.68 | 1151901.4726 | 2513787.9419 | 1151896.0355 | 2513779.2584 | 1151886.6439
23 | 2513760.1482 | 1151865.9753 | 2513779.2584 | 1151886.6439
24 | 2513647.0753 | 1152017.4947 | 2513653.2356 | 1152017.8175 | 2513658.6639 | 1152013.8456
25 | 2513647.0753 | 1152017.4947 | 2513645.5299 | 1152024.7878 | 2513646.1641 | 1152034.2065 | 2513648.5085 | 1152044.6012 | 2513652.1093 | 1152052.6877 | 2513660.3514 | 1152064.3651 | 2513660.7302 | 1152064.9304
26 | 2513660.7302 | 1152064.9304 | 2513661.9672 | 1152066.7767 | 2513662.9893 | 1152070.6087 | 2513660.872 | 1152073.8855 | 2513646.8542 | 1152082.2473 | 2513641.6649 | 1152083.8005 | 2513636.6556 | 1152082.3826 | 2513631.569 | 1152078.7869 | 2513624.4037 | 1152074.2204 | 2513619.6278 | 1152073.5553 | 2513615.5546 | 1152075.8596 | 2513613.8494 | 1152078.4411
27 | 2513620.4448 | 1152104.7731 | 2513604.4866 | 1152096.6753 | 2513590.5532 | 1152088.4706 | 2513578.766 | 1152078.4673 | 2513574.1741 | 1152073.5193
28 | 2513620.4448 | 1152104.7731 | 2513623.8439 | 1152102.5674
29 | 2513620.4448 | 1152104.7731 | 2513630.9132 | 1152107.4021
30 | 2513574.1741 | 1152073.5193 | 2513580.197 | 1152058.7602
31 | 2513623.8439 | 1152102.5674 | 2513624.1048 | 1152095.6151 | 2513613.9928 | 1152082.0079 | 2513613.8494 | 1152078.4411 | 2513613.8494 | 1152078.4411
32 | 2513630.9132 | 1152107.4021 | 2513641.1082 | 1152109.9711
33 | 2513580.197 | 1152058.7602 | 2513580.9284 | 1152056.968 | 2513584.859 | 1152045.816 | 2513569.4589 | 1152022.6533
34 | 2513695.249 | 1152116.0727 | 2513685.5127 | 1152116.3236 | 2513645.2719 | 1152111.0203 | 2513641.1082 | 1152109.9711
35 | 2513569.4589 | 1152022.6533 | 2513553.9026 | 1151999.2555 | 2513547.3157 | 1151995.4257 | 2513538.8584 | 1151995.4539
36 | 2513489.5458 | 1151982.293 | 2513505.9182 | 1151999.9457
37 | 2513505.9182 | 1151999.9457 | 2513511.6078 | 1151995.2945 | 2513533.2243 | 1151995.4727 | 2513538.8584 | 1151995.4539
38 | 2513489.5458 | 1151982.293 | 2513504.1928 | 1151970.3498
39 | 2513489.5458 | 1151982.293 | 2513460.0339 | 1151950.0608
40 | 2513693.3694 | 1152109.1845 | 2513693.6735 | 1152107.9127 | 2513699.2072 | 1152102.0187
41 | 2513693.3694 | 1152109.1845 | 2513695.7439 | 1152110.9848 | 2513695.249 | 1152116.0727
42 | 2513504.1928 | 1151970.3498 | 2513517.4715 | 1151959.5224 | 2513507.1634 | 1151947.9487
43 | 2513497.7289 | 1151937.3558 | 2513507.1634 | 1151947.9487
44 | 2513353.9901 | 1151834.2564 | 2513393.9481 | 1151877.8927
45 | 2513353.9901 | 1151834.2564 | 2513368.8636 | 1151811.2175
46 | 2513497.7289 | 1151937.3558 | 2513481.9399 | 1151919.6284
47 | 2513393.4874 | 1151775.5418 | 2513387.4227 | 1151782.9446 | 2513368.8636 | 1151811.2175
48 | 2513368.8636 | 1151811.2175 | 2513417.4147 | 1151857.9867
49 | 2513460.1672 | 1151895.1825 | 2513481.9399 | 1151919.6284
50 | 2513460.1672 | 1151895.1825 | 2513456.5826 | 1151891.1578
51 | 2513436.3608 | 1151876.2374 | 2513437.3536 | 1151877.1937
52 | 2513436.3608 | 1151876.2374 | 2513417.4147 | 1151857.9867
53 | 2513393.4874 | 1151775.5418 | 2513398.4808 | 1151769.444 | 2513404.9207 | 1151762.5139 | 2513420.6498 | 1151745.5663 | 2513438.1769 | 1151722.8784 | 2513460.8002 | 1151740.1409
54 | 2513393.4874 | 1151775.5418 | 2513425.7197 | 1151804.8985
55 | 2513460.8002 | 1151740.1409 | 2513463.1035 | 1151741.8989
56 | 2513449.5473 | 1151825.5681 | 2513436.1947 | 1151814.4389 | 2513425.7197 | 1151804.8985
57 | 2513463.1035 | 1151741.8989 | 2513475.8951 | 1151751.6623
58 | 2513473.2913 | 1151845.3585 | 2513449.5473 | 1151825.5681
59 | 2513557.9257 | 1151723.0315 | 2513558.8383 | 1151722.7766 | 2513570.5961 | 1151732.0303
60 | 2513553.3415 | 1151724.312 | 2513557.9257 | 1151723.0315
61 | 2513553.3415 | 1151724.312 | 2513533.1708 | 1151708.657
62 | 2513553.3415 | 1151724.312 | 2513554.6858 | 1151730.7854 | 2513548.1945 | 1151740.9995
63 | 2513521.236 | 1151699.394 | 2513533.1708 | 1151708.657
64 | 2513546.5066 | 1151743.6555 | 2513548.1945 | 1151740.9995
65 | 2513521.236 | 1151699.394 | 2513511.0335 | 1151691.4756
66 | 2513544.1516 | 1151747.3611 | 2513546.5066 | 1151743.6555
67 | 2513544.1516 | 1151747.3611 | 2513528.3018 | 1151772.3008
68 | 2513485.408 | 1151758.9231 | 2513475.8951 | 1151751.6623
69 | 2513485.408 | 1151758.9231 | 2513499.7257 | 1151769.8513
70 | 2513499.7257 | 1151769.8513 | 2513503.5501 | 1151772.7703
71 | 2513520.0162 | 1151785.3383 | 2513503.5501 | 1151772.7703
72 | 2513520.0162 | 1151785.3383 | 2513520.4684 | 1151788.4892 | 2513520.4684 | 1151788.4892
73 | 2513520.0162 | 1151785.3383 | 2513526.9057 | 1151774.4976
74 | 2513531.8633 | 1151797.4063 | 2513520.4684 | 1151788.4892
75 | 2513528.3018 | 1151772.3008 | 2513526.9057 | 1151774.4976

## bus_geodata
| x | y | coords
0 | 2513167.0865 | 1152417.7761
1 | 2513225.861 | 1152351.0874
2 | 2513153.8303 | 1152432.8199
3 | 2513365.9523 | 1151986.83
4 | 2513159.3503 | 1152456.9513
5 | 2513150.8552 | 1152436.1982
6 | 2513351.9332 | 1151971.6563
7 | 2513440.8079 | 1151929.0626
8 | 2513131.819 | 1152457.7971
9 | 2513163.6638 | 1152495.7415
10 | 2513251.1279 | 1152470.8454
11 | 2513573.7122 | 1152140.3404
12 | 2513578.4924 | 1152135.9156
13 | 2513704.0411 | 1151971.7993
14 | 2513717.2958 | 1151988.5143
15 | 2513716.7018 | 1151871.2609
16 | 2513721.3387 | 1151993.335
17 | 2513691.5827 | 1151995.4317
18 | 2513713.4323 | 1151848.4178
19 | 2513791.6167 | 1151916.784
20 | 2513779.2584 | 1151886.6439
21 | 2513760.1482 | 1151865.9753
22 | 2513658.6639 | 1152013.8456
23 | 2513705.3333 | 1152015.9946
24 | 2513647.0753 | 1152017.4947
25 | 2513660.7302 | 1152064.9304
26 | 2513620.4448 | 1152104.7731
27 | 2513574.1741 | 1152073.5193
28 | 2513623.8439 | 1152102.5674
29 | 2513630.9132 | 1152107.4021
30 | 2513580.197 | 1152058.7602
31 | 2513613.8494 | 1152078.4411
32 | 2513641.1082 | 1152109.9711
33 | 2513569.4589 | 1152022.6533
34 | 2513505.9182 | 1151999.9457
35 | 2513489.5458 | 1151982.293
36 | 2513538.8584 | 1151995.4539
37 | 2513693.3694 | 1152109.1845
38 | 2513699.2072 | 1152102.0187
39 | 2513695.249 | 1152116.0727
40 | 2513504.1928 | 1151970.3498
41 | 2513460.0339 | 1151950.0608
42 | 2513507.1634 | 1151947.9487
43 | 2513393.9481 | 1151877.8927
44 | 2513353.9901 | 1151834.2564
45 | 2513497.7289 | 1151937.3559
46 | 2513368.8636 | 1151811.2175
47 | 2513481.9399 | 1151919.6284
48 | 2513460.1672 | 1151895.1825
49 | 2513456.5826 | 1151891.1578
50 | 2513436.3608 | 1151876.2374
51 | 2513437.3536 | 1151877.1937
52 | 2513417.4147 | 1151857.9867
53 | 2513393.4874 | 1151775.5418
54 | 2513460.8002 | 1151740.1409
55 | 2513425.7197 | 1151804.8985
56 | 2513463.1035 | 1151741.8989
57 | 2513449.5473 | 1151825.5681
58 | 2513557.9257 | 1151723.0315
59 | 2513570.5961 | 1151732.0303
60 | 2513553.3415 | 1151724.312
61 | 2513533.1708 | 1151708.657
62 | 2513548.1945 | 1151740.9995
63 | 2513521.236 | 1151699.394
64 | 2513546.5066 | 1151743.6555
65 | 2513511.0335 | 1151691.4756
66 | 2513544.1516 | 1151747.3611
67 | 2513475.8951 | 1151751.6623
68 | 2513485.408 | 1151758.9231
69 | 2513499.7257 | 1151769.8513
70 | 2513503.5501 | 1151772.7703
71 | 2513520.0162 | 1151785.3383
72 | 2513520.4684 | 1151788.4892
73 | 2513526.9057 | 1151774.4976
74 | 2513528.3018 | 1151772.3008
75 | 2513531.8633 | 1151797.4063
76 | 2513473.2913 | 1151845.3585
77 | 2513574.1741 | 1152073.5193

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1