## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5486-3_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5486-3_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5486-3_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5486-3_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5486-3_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5486-3_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_5486-3_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_5486-3_0_2_node_64 | 0.4 | n |  | TRUE
8 | bus_LV_5486-3_0_2_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_5486-3_0_2_node_61 | 0.4 | n |  | TRUE
10 | bus_LV_5486-3_0_2_node_37 | 0.4 | n |  | TRUE
11 | bus_LV_5486-3_0_2_node_72 | 0.4 | n |  | TRUE
12 | bus_LV_5486-3_0_2_node_36 | 0.4 | n |  | TRUE
13 | bus_LV_5486-3_0_2_node_63 | 0.4 | n |  | TRUE
14 | bus_LV_5486-3_0_2_node_49 | 0.4 | n |  | TRUE
15 | bus_LV_5486-3_0_2_node_73 | 0.4 | n |  | TRUE
16 | bus_LV_5486-3_0_2_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_5486-3_0_2_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_5486-3_0_2_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_5486-3_0_2_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_5486-3_0_2_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_5486-3_0_2_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_5486-3_0_2_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_5486-3_0_2_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_5486-3_0_2_node_35 | 0.4 | n |  | TRUE
25 | bus_LV_5486-3_0_2_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_5486-3_0_2_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_5486-3_0_2_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_5486-3_0_2_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_5486-3_0_2_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_5486-3_0_2_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_5486-3_0_2_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_5486-3_0_2_node_55 | 0.4 | n |  | TRUE
33 | bus_LV_5486-3_0_2_node_76 | 0.4 | n |  | TRUE
34 | bus_LV_5486-3_0_2_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_5486-3_0_2_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_5486-3_0_2_node_40 | 0.4 | n |  | TRUE
37 | bus_LV_5486-3_0_2_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_5486-3_0_2_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_5486-3_0_2_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_5486-3_0_2_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_5486-3_0_2_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_5486-3_0_2_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_5486-3_0_2_node_51 | 0.4 | n |  | TRUE
44 | bus_LV_5486-3_0_2_node_65 | 0.4 | n |  | TRUE
45 | bus_LV_5486-3_0_2_node_52 | 0.4 | n |  | TRUE
46 | bus_LV_5486-3_0_2_node_57 | 0.4 | n |  | TRUE
47 | bus_LV_5486-3_0_2_node_56 | 0.4 | n |  | TRUE
48 | bus_LV_5486-3_0_2_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_5486-3_0_2_node_67 | 0.4 | n |  | TRUE
50 | bus_LV_5486-3_0_2_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_5486-3_0_2_node_66 | 0.4 | n |  | TRUE
52 | bus_LV_5486-3_0_2_node_41 | 0.4 | n |  | TRUE
53 | bus_LV_5486-3_0_2_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_5486-3_0_2_node_59 | 0.4 | n |  | TRUE
55 | bus_LV_5486-3_0_2_node_60 | 0.4 | n |  | TRUE
56 | bus_LV_5486-3_0_2_node_58 | 0.4 | n |  | TRUE
57 | bus_LV_5486-3_0_2_node_42 | 0.4 | n |  | TRUE
58 | bus_LV_5486-3_0_2_node_43 | 0.4 | n |  | TRUE
59 | bus_LV_5486-3_0_2_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_5486-3_0_2_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_5486-3_0_2_node_46 | 0.4 | n |  | TRUE
62 | bus_LV_5486-3_0_2_node_71 | 0.4 | n |  | TRUE
63 | bus_LV_5486-3_0_2_node_70 | 0.4 | n |  | TRUE
64 | bus_LV_5486-3_0_2_node_75 | 0.4 | n |  | TRUE
65 | bus_LV_5486-3_0_2_node_68 | 0.4 | n |  | TRUE
66 | bus_LV_5486-3_0_2_node_50 | 0.4 | n |  | TRUE
67 | bus_LV_5486-3_0_2_node_69 | 0.4 | n |  | TRUE
68 | bus_LV_5486-3_0_2_node_74 | 0.4 | n |  | TRUE
69 | bus_MV_312_0_node_11 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5486-3_0_2_load_0 | 0 | 0.0065122 | 0.0016321 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5486-3_0_2_load_1 | 1 | 0.0071266 | 0.0017861 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5486-3_0_2_load_4 | 4 | 0.0012617 | 0.00031621 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5486-3_0_2_load_64 | 7 | 0.00088812 | 0.00022258 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5486-3_0_2_load_61 | 9 | 0.0022073 | 0.00055319 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5486-3_0_2_load_72 | 11 | 0.0016403 | 0.0004111 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5486-3_0_2_load_63 | 13 | 0.002691 | 0.00067444 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5486-3_0_2_load_49 | 14 | 0.00085736 | 0.00021488 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5486-3_0_2_load_73 | 15 | 0.00072224 | 0.00018101 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5486-3_0_2_load_7 | 16 | 0.0016954 | 0.0004249 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5486-3_0_2_load_8 | 17 | 0.0019415 | 0.00048658 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5486-3_0_2_load_11 | 20 | 0.0049115 | 0.0012309 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5486-3_0_2_load_22 | 21 | 0.010578 | 0.0026511 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5486-3_0_2_load_19 | 22 | 0.0093347 | 0.0023395 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5486-3_0_2_load_18 | 23 | 0.0035402 | 0.00088725 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5486-3_0_2_load_20 | 25 | 0.0059112 | 0.0014815 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5486-3_0_2_load_12 | 26 | 0.0016157 | 0.00040494 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5486-3_0_2_load_13 | 27 | 0.0016906 | 0.0004237 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5486-3_0_2_load_15 | 29 | 0.0021262 | 0.00053289 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5486-3_0_2_load_16 | 30 | 0.0048722 | 0.0012211 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5486-3_0_2_load_17 | 31 | 0.0025079 | 0.00062853 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5486-3_0_2_load_55 | 32 | 0.019029 | 0.0047692 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5486-3_0_2_load_76 | 33 | 0.0049333 | 0.0012364 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5486-3_0_2_load_38 | 34 | 0.0090488 | 0.0022678 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5486-3_0_2_load_21 | 35 | 0.0025756 | 0.00064551 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5486-3_0_2_load_26 | 37 | 0.0010707 | 0.00026834 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5486-3_0_2_load_23 | 38 | 0.0046376 | 0.0011623 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5486-3_0_2_load_24 | 39 | 0.0053734 | 0.0013467 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5486-3_0_2_load_27 | 41 | 0.001162 | 0.00029122 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5486-3_0_2_load_51 | 43 | 0.0033428 | 0.00083779 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5486-3_0_2_load_65 | 44 | 0.0026347 | 0.00066032 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5486-3_0_2_load_52 | 45 | 0.0016328 | 0.00040922 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5486-3_0_2_load_57 | 46 | 0.00017398 | 4.3605e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5486-3_0_2_load_56 | 47 | 0.00034835 | 8.7305e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5486-3_0_2_load_34 | 48 | 0.00042407 | 0.00010628 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5486-3_0_2_load_67 | 49 | 0.0028552 | 0.00071558 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5486-3_0_2_load_48 | 50 | 0.003027 | 0.00075864 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5486-3_0_2_load_66 | 51 | 0.00030222 | 7.5744e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5486-3_0_2_load_41 | 52 | 0.0031977 | 0.00080141 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5486-3_0_2_load_39 | 53 | 0.0050641 | 0.0012692 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5486-3_0_2_load_60 | 55 | 0.0018029 | 0.00045184 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5486-3_0_2_load_58 | 56 | 0.00029292 | 7.3412e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5486-3_0_2_load_42 | 57 | 0.00036013 | 9.0258e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5486-3_0_2_load_71 | 62 | 0.00051668 | 0.00012949 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5486-3_0_2_load_70 | 63 | 0.00022433 | 5.6223e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5486-3_0_2_load_75 | 64 | 0.0004817 | 0.00012072 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5486-3_0_2_load_50 | 66 | 0.0036999 | 0.00092728 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5486-3_0_2_load_69 | 67 | 0.0013533 | 0.00033917 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5486-3_0_2_load_74 | 68 | 0.001562 | 0.00039148 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5486-3_0_2_line_0 |  | 0 | 1 | 0.0021104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5486-3_0_2_line_1 |  | 0 | 2 | 0.033541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5486-3_0_2_line_2 |  | 1 | 3 | 0.017423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5486-3_0_2_line_3 |  | 2 | 4 | 0.043514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5486-3_0_2_line_4 |  | 2 | 5 | 0.014174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5486-3_0_2_line_5 |  | 2 | 6 | 0.049747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5486-3_0_2_line_6 |  | 3 | 7 | 0.037216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5486-3_0_2_line_7 |  | 5 | 8 | 0.039373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5486-3_0_2_line_8 |  | 5 | 9 | 0.036354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5486-3_0_2_line_9 |  | 6 | 10 | 0.038842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5486-3_0_2_line_10 |  | 6 | 11 | 0.021404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5486-3_0_2_line_11 |  | 7 | 13 | 0.00064776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5486-3_0_2_line_12 |  | 8 | 14 | 0.0082478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5486-3_0_2_line_13 |  | 10 | 12 | 0.027976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5486-3_0_2_line_14 |  | 11 | 15 | 0.017746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5486-3_0_2_line_15 |  | 12 | 34 | 0.0026328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5486-3_0_2_line_16 |  | 12 | 29 | 0.014264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5486-3_0_2_line_17 |  | 13 | 42 | 0.0075763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5486-3_0_2_line_18 |  | 14 | 50 | 0.011331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5486-3_0_2_line_19 |  | 15 | 68 | 0.00031929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5486-3_0_2_line_20 |  | 16 | 17 | 0.019617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5486-3_0_2_line_21 |  | 16 | 18 | 0.032313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5486-3_0_2_line_22 |  | 17 | 19 | 0.015892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5486-3_0_2_line_23 |  | 18 | 20 | 0.015183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5486-3_0_2_line_24 |  | 19 | 21 | 0.031205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5486-3_0_2_line_25 |  | 19 | 22 | 0.016809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5486-3_0_2_line_26 |  | 20 | 23 | 0.02995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5486-3_0_2_line_27 |  | 21 | 24 | 0.0033941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5486-3_0_2_line_28 |  | 22 | 25 | 0.018677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5486-3_0_2_line_29 |  | 24 | 36 | 0.027596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5486-3_0_2_line_30 |  | 24 | 37 | 0.0064652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5486-3_0_2_line_31 |  | 25 | 35 | 0.029336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5486-3_0_2_line_32 |  | 26 | 27 | 0.019428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5486-3_0_2_line_33 |  | 26 | 28 | 0.027356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5486-3_0_2_line_34 |  | 27 | 29 | 0.017518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5486-3_0_2_line_35 |  | 28 | 30 | 0.021806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5486-3_0_2_line_36 |  | 28 | 31 | 0.012847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5486-3_0_2_line_37 |  | 30 | 32 | 0.014307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5486-3_0_2_line_38 |  | 31 | 33 | 0.0021706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5486-3_0_2_line_39 |  | 34 | 54 | 0.050062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5486-3_0_2_line_40 |  | 36 | 52 | 0.01776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5486-3_0_2_line_41 |  | 36 | 53 | 0.025165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5486-3_0_2_line_42 |  | 37 | 39 | 0.0099024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5486-3_0_2_line_43 |  | 38 | 39 | 0.016653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5486-3_0_2_line_44 |  | 38 | 40 | 0.00026911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5486-3_0_2_line_45 |  | 40 | 41 | 0.01564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5486-3_0_2_line_46 |  | 40 | 42 | 0.038462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5486-3_0_2_line_47 |  | 41 | 43 | 0.042927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5486-3_0_2_line_48 |  | 42 | 44 | 0.032485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5486-3_0_2_line_49 |  | 43 | 45 | 0.017153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5486-3_0_2_line_50 |  | 46 | 47 | 0.010877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5486-3_0_2_line_51 |  | 47 | 59 | 0.11449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5486-3_0_2_line_52 |  | 48 | 49 | 2.9959e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5486-3_0_2_line_53 |  | 49 | 51 | 0.022917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5486-3_0_2_line_54 |  | 50 | 66 | 0.018363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5486-3_0_2_line_55 |  | 51 | 65 | 0.010202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5486-3_0_2_line_56 |  | 54 | 55 | 0.043042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5486-3_0_2_line_57 |  | 54 | 56 | 0.037964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5486-3_0_2_line_58 |  | 55 | 60 | 0.045726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5486-3_0_2_line_59 |  | 57 | 58 | 0.047632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5486-3_0_2_line_60 |  | 57 | 59 | 0.0020157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5486-3_0_2_line_61 |  | 58 | 60 | 0.00925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5486-3_0_2_line_62 |  | 58 | 61 | 0.017372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5486-3_0_2_line_63 |  | 60 | 62 | 0.0040668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5486-3_0_2_line_64 |  | 61 | 63 | 0.042173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5486-3_0_2_line_65 |  | 61 | 64 | 0.012532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5486-3_0_2_line_66 |  | 63 | 65 | 0.014439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5486-3_0_2_line_67 |  | 65 | 67 | 0.0073245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5486-3_0_2_trafo_64 | 0.63 MVA 20/0.4 kV | 69 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2520987.249 | 1162244.3916 | 2520986.0491 | 1162242.6555
1 | 2520998.9464 | 1162274.9944 | 2520998.3313 | 1162264.3518 | 2520991.3269 | 1162250.2914 | 2520987.249 | 1162244.3916
2 | 2520976.1426 | 1162228.3229 | 2520986.0491 | 1162242.6555
3 | 2520998.9464 | 1162274.9944 | 2521008.9581 | 1162267.2248 | 2521024.8565 | 1162252.0624 | 2521022.1776 | 1162243.5483
4 | 2520998.9464 | 1162274.9944 | 2520999.1947 | 1162279.3047 | 2520999.9218 | 1162289.1342
5 | 2520957.4157 | 1162273.0621 | 2520972.4079 | 1162282.7703 | 2520983.8793 | 1162284.0312 | 2520999.1947 | 1162279.3047 | 2520998.9464 | 1162274.9944
6 | 2520976.1426 | 1162228.3229 | 2520981.3484 | 1162223.9185 | 2521004.3159 | 1162204.007
7 | 2520999.9218 | 1162289.1342 | 2521001.0967 | 1162305.0502 | 2521004.1376 | 1162328.257
8 | 2520999.9218 | 1162289.1342 | 2521035.0807 | 1162279.8878
9 | 2520926.2771 | 1162258.5192 | 2520933.9213 | 1162254.2605 | 2520957.4157 | 1162273.0621
10 | 2520957.4157 | 1162273.0621 | 2520957.3774 | 1162282.368 | 2520960.4173 | 1162294.0776
11 | 2521004.3159 | 1162204.007 | 2521004.8053 | 1162203.5827
12 | 2521004.1376 | 1162328.257 | 2521012.2029 | 1162326.5316
13 | 2520926.2771 | 1162258.5192 | 2520901.9263 | 1162272.4146
14 | 2520960.4173 | 1162294.0776 | 2520964.8763 | 1162311.2539
15 | 2520901.9263 | 1162272.4146 | 2520899.6398 | 1162273.7198
16 | 2520901.9263 | 1162272.4146 | 2520898.4819 | 1162258.5729
17 | 2521010.5298 | 1162198.6199 | 2521004.8053 | 1162203.5827
18 | 2521023.2828 | 1162324.1613 | 2521012.2029 | 1162326.5316
19 | 2520964.8763 | 1162311.2539 | 2520964.9566 | 1162311.5629
20 | 2521090.5545 | 1162081.5998 | 2521080.2731 | 1162098.3065
21 | 2521096.9503 | 1162050.5421 | 2521097.2373 | 1162063.0456 | 2521094.6916 | 1162072.8181 | 2521090.5545 | 1162081.5998
22 | 2521071.8571 | 1162111.7852 | 2521073.1725 | 1162109.8446 | 2521080.2731 | 1162098.3065
23 | 2521096.9503 | 1162050.5421 | 2521095.1276 | 1162043.6176 | 2521091.7947 | 1162036.3197
24 | 2521071.8571 | 1162111.7852 | 2521054.3469 | 1162137.6144
25 | 2521071.8571 | 1162111.7852 | 2521061.9714 | 1162104.0996 | 2521059.1151 | 1162100.9025
26 | 2521079.353 | 1162009.0765 | 2521091.7947 | 1162036.3197
27 | 2521052.4423 | 1162140.4238 | 2521054.3469 | 1162137.6144
28 | 2521059.1151 | 1162100.9025 | 2521054.4123 | 1162095.6385 | 2521048.1979 | 1162087.4599 | 2521047.5781 | 1162086.2649
29 | 2521052.4423 | 1162140.4238 | 2521035.0806 | 1162118.9396
30 | 2521052.4423 | 1162140.4238 | 2521048.8133 | 1162145.7744
31 | 2521031.0051 | 1162062.5271 | 2521036.8619 | 1162067.3974 | 2521041.9321 | 1162075.3798 | 2521047.5781 | 1162086.2649
32 | 2520889.6186 | 1162243.6415 | 2520878.7166 | 1162227.5611
33 | 2520890.6346 | 1162204.5796 | 2520878.8811 | 1162219.1207 | 2520877.8348 | 1162223.4481 | 2520878.7166 | 1162227.5611
34 | 2520898.4819 | 1162258.5729 | 2520897.7515 | 1162255.6377 | 2520889.6186 | 1162243.6415
35 | 2520890.6346 | 1162204.5796 | 2520891.5813 | 1162205.4787 | 2520904.5498 | 1162221.356
36 | 2520890.6346 | 1162204.5796 | 2520881.336 | 1162195.7149
37 | 2520904.5498 | 1162221.356 | 2520909.1272 | 1162226.9601 | 2520912.61 | 1162233.1142
38 | 2520879.7649 | 1162194.2171 | 2520881.336 | 1162195.7149
39 | 2520863.1509 | 1162305.7005 | 2520867.5084 | 1162295.6594 | 2520878.4807 | 1162285.798 | 2520899.6398 | 1162273.7198
40 | 2521035.0806 | 1162118.9396 | 2521022.9411 | 1162105.9473
41 | 2521035.0806 | 1162118.9396 | 2521012.3417 | 1162129.7211
42 | 2521043.2551 | 1162153.9696 | 2521048.8133 | 1162145.7744
43 | 2521043.2551 | 1162153.9696 | 2521033.9077 | 1162167.7516
44 | 2521033.9077 | 1162167.7516 | 2521033.7566 | 1162167.9744
45 | 2521033.7566 | 1162167.9744 | 2521022.1034 | 1162157.5431
46 | 2521033.7566 | 1162167.9744 | 2521030.5929 | 1162172.1072 | 2521019.9923 | 1162187.5334 | 2521010.5298 | 1162198.6199
47 | 2520992.2859 | 1162126.8005 | 2520994.0215 | 1162127.8849 | 2521015.7762 | 1162151.8793 | 2521022.1034 | 1162157.5431
48 | 2521040.2944 | 1162211.2135 | 2521025.0285 | 1162206.9117 | 2521010.5298 | 1162198.6199
49 | 2520976.129 | 1162122.5617 | 2520986.9292 | 1162123.4534 | 2520992.2859 | 1162126.8005
50 | 2520895.6101 | 1162557.7004 | 2520899.063 | 1162568.0145
51 | 2520859.2655 | 1162449.135 | 2520895.6101 | 1162557.7004
52 | 2520939.8694 | 1162363.0575 | 2520939.8666 | 1162363.0587
53 | 2520918.8935 | 1162372.2958 | 2520939.8666 | 1162363.0587
54 | 2521041.2397 | 1162320.3199 | 2521023.2828 | 1162324.1613
55 | 2520909.5569 | 1162376.4078 | 2520918.8935 | 1162372.2958
56 | 2520863.1509 | 1162305.7005 | 2520858.6075 | 1162316.1664 | 2520851.3619 | 1162346.9576
57 | 2520863.1509 | 1162305.7005 | 2520848.8959 | 1162307.167 | 2520826.0808 | 1162313.3335
58 | 2520844.961 | 1162392.2238 | 2520850.837 | 1162349.188 | 2520851.3619 | 1162346.9576
59 | 2520845.8563 | 1162401.4285 | 2520849.6861 | 1162420.5113 | 2520858.6258 | 1162447.2235
60 | 2520859.2655 | 1162449.135 | 2520858.6258 | 1162447.2235
61 | 2520845.8563 | 1162401.4285 | 2520844.961 | 1162392.2238
62 | 2520860.6148 | 1162392.2619 | 2520855.287 | 1162394.956 | 2520845.8563 | 1162401.4285
63 | 2520844.961 | 1162392.2238 | 2520844.7382 | 1162396.2846
64 | 2520860.6148 | 1162392.2619 | 2520874.05 | 1162383.8467 | 2520889.3285 | 1162374.0174 | 2520897.1628 | 1162371.7621
65 | 2520860.6148 | 1162392.2619 | 2520866.1503 | 1162391.3774 | 2520871.0421 | 1162392.8026 | 2520872.6293 | 1162393.7156
66 | 2520909.5569 | 1162376.4078 | 2520906.5359 | 1162372.7566 | 2520899.7704 | 1162371.0114 | 2520897.1628 | 1162371.7621
67 | 2520909.5569 | 1162376.4078 | 2520912.3671 | 1162383.1717

## bus_geodata
| x | y | coords
0 | 2520987.249 | 1162244.3916
1 | 2520986.0491 | 1162242.6555
2 | 2520998.9464 | 1162274.9944
3 | 2520976.1426 | 1162228.3229
4 | 2521022.1776 | 1162243.5483
5 | 2520999.9218 | 1162289.1342
6 | 2520957.4157 | 1162273.0621
7 | 2521004.3159 | 1162204.007
8 | 2521004.1376 | 1162328.257
9 | 2521035.0807 | 1162279.8878
10 | 2520926.2771 | 1162258.5192
11 | 2520960.4173 | 1162294.0776
12 | 2520901.9263 | 1162272.4146
13 | 2521004.8053 | 1162203.5827
14 | 2521012.2029 | 1162326.5316
15 | 2520964.8763 | 1162311.2539
16 | 2521090.5545 | 1162081.5998
17 | 2521080.2731 | 1162098.3065
18 | 2521096.9503 | 1162050.5421
19 | 2521071.8571 | 1162111.7852
20 | 2521091.7947 | 1162036.3197
21 | 2521054.3469 | 1162137.6144
22 | 2521059.1151 | 1162100.9025
23 | 2521079.353 | 1162009.0765
24 | 2521052.4423 | 1162140.4238
25 | 2521047.5781 | 1162086.2649
26 | 2520878.7166 | 1162227.5611
27 | 2520889.6186 | 1162243.6415
28 | 2520890.6346 | 1162204.5796
29 | 2520898.4819 | 1162258.5729
30 | 2520904.5498 | 1162221.356
31 | 2520881.336 | 1162195.7149
32 | 2520912.61 | 1162233.1142
33 | 2520879.7649 | 1162194.2171
34 | 2520899.6398 | 1162273.7198
35 | 2521031.0051 | 1162062.5271
36 | 2521035.0806 | 1162118.9396
37 | 2521048.8133 | 1162145.7744
38 | 2521033.9077 | 1162167.7516
39 | 2521043.2551 | 1162153.9696
40 | 2521033.7566 | 1162167.9744
41 | 2521022.1034 | 1162157.5431
42 | 2521010.5298 | 1162198.6199
43 | 2520992.2859 | 1162126.8005
44 | 2521040.2944 | 1162211.2135
45 | 2520976.129 | 1162122.5617
46 | 2520899.063 | 1162568.0145
47 | 2520895.6101 | 1162557.7004
48 | 2520939.8694 | 1162363.0575
49 | 2520939.8666 | 1162363.0587
50 | 2521023.2828 | 1162324.1613
51 | 2520918.8935 | 1162372.2958
52 | 2521022.9411 | 1162105.9473
53 | 2521012.3417 | 1162129.7211
54 | 2520863.1509 | 1162305.7005
55 | 2520851.3619 | 1162346.9576
56 | 2520826.0808 | 1162313.3335
57 | 2520858.6258 | 1162447.2235
58 | 2520845.8563 | 1162401.4285
59 | 2520859.2655 | 1162449.135
60 | 2520844.961 | 1162392.2238
61 | 2520860.6148 | 1162392.2619
62 | 2520844.7382 | 1162396.2846
63 | 2520897.1628 | 1162371.7621
64 | 2520872.6293 | 1162393.7156
65 | 2520909.5569 | 1162376.4078
66 | 2521041.2397 | 1162320.3199
67 | 2520912.3671 | 1162383.1717
68 | 2520964.9566 | 1162311.5629
69 | 2521010.5298 | 1162198.6199

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1