## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6423-1_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6423-1_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6423-1_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6423-1_0_2_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_6423-1_0_2_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_6423-1_0_2_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_6423-1_0_2_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_6423-1_0_2_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_6423-1_0_2_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_6423-1_0_2_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_6423-1_0_2_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_6423-1_0_2_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_6423-1_0_2_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_6423-1_0_2_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_6423-1_0_2_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_6423-1_0_2_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_6423-1_0_2_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_6423-1_0_2_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_6423-1_0_2_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_6423-1_0_2_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_6423-1_0_2_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_6423-1_0_2_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_6423-1_0_2_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_6423-1_0_2_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_6423-1_0_2_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_6423-1_0_2_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_6423-1_0_2_node_114 | 0.4 | n |  | TRUE
27 | bus_LV_6423-1_0_2_node_140 | 0.4 | n |  | TRUE
28 | bus_LV_6423-1_0_2_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_6423-1_0_2_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_6423-1_0_2_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_6423-1_0_2_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_6423-1_0_2_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_6423-1_0_2_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_6423-1_0_2_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_6423-1_0_2_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_6423-1_0_2_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_6423-1_0_2_node_133 | 0.4 | n |  | TRUE
38 | bus_LV_6423-1_0_2_node_134 | 0.4 | n |  | TRUE
39 | bus_LV_6423-1_0_2_node_132 | 0.4 | n |  | TRUE
40 | bus_LV_6423-1_0_2_node_135 | 0.4 | n |  | TRUE
41 | bus_LV_6423-1_0_2_node_136 | 0.4 | n |  | TRUE
42 | bus_LV_6423-1_0_2_node_109 | 0.4 | n |  | TRUE
43 | bus_LV_6423-1_0_2_node_129 | 0.4 | n |  | TRUE
44 | bus_LV_6423-1_0_2_node_130 | 0.4 | n |  | TRUE
45 | bus_LV_6423-1_0_2_node_131 | 0.4 | n |  | TRUE
46 | bus_LV_6423-1_0_2_node_104 | 0.4 | n |  | TRUE
47 | bus_LV_6423-1_0_2_node_107 | 0.4 | n |  | TRUE
48 | bus_LV_6423-1_0_2_node_105 | 0.4 | n |  | TRUE
49 | bus_LV_6423-1_0_2_node_106 | 0.4 | n |  | TRUE
50 | bus_LV_6423-1_0_2_node_108 | 0.4 | n |  | TRUE
51 | bus_LV_6423-1_0_2_node_115 | 0.4 | n |  | TRUE
52 | bus_LV_6423-1_0_2_node_116 | 0.4 | n |  | TRUE
53 | bus_LV_6423-1_0_2_node_117 | 0.4 | n |  | TRUE
54 | bus_LV_6423-1_0_2_node_118 | 0.4 | n |  | TRUE
55 | bus_LV_6423-1_0_2_node_119 | 0.4 | n |  | TRUE
56 | bus_LV_6423-1_0_2_node_121 | 0.4 | n |  | TRUE
57 | bus_MV_0_node_16 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6423-1_0_2_load_0 | 0 | 0.002192 | 0.00054936 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6423-1_0_2_load_4 | 3 | 0.0021135 | 0.00052969 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6423-1_0_2_load_11 | 5 | 0.0021558 | 0.00054029 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6423-1_0_2_load_25 | 7 | 0.0018919 | 0.00047416 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6423-1_0_2_load_5 | 8 | 0.0066644 | 0.0016703 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6423-1_0_2_load_6 | 9 | 0.0012938 | 0.00032427 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6423-1_0_2_load_8 | 11 | 0.00037973 | 9.5168e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6423-1_0_2_load_9 | 12 | 0.0032783 | 0.00082163 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6423-1_0_2_load_12 | 13 | 0.001598 | 0.00040049 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6423-1_0_2_load_15 | 14 | 0.00065898 | 0.00016516 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6423-1_0_2_load_16 | 16 | 0.0022539 | 0.00056489 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6423-1_0_2_load_14 | 17 | 0.0019034 | 0.00047703 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6423-1_0_2_load_17 | 19 | 0.0028824 | 0.00072239 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6423-1_0_2_load_18 | 20 | 0.0039178 | 0.00098189 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6423-1_0_2_load_21 | 22 | 0.0016796 | 0.00042096 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6423-1_0_2_load_23 | 24 | 0.0006098 | 0.00015283 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6423-1_0_2_load_24 | 25 | 0.00054387 | 0.00013631 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6423-1_0_2_load_114 | 26 | 0.0018649 | 0.0004674 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6423-1_0_2_load_140 | 27 | 0.00065049 | 0.00016303 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6423-1_0_2_load_28 | 29 | 0.00091684 | 0.00022978 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6423-1_0_2_load_29 | 30 | 0.00039721 | 9.9551e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6423-1_0_2_load_33 | 31 | 0.00049496 | 0.00012405 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6423-1_0_2_load_30 | 32 | 0.00037153 | 9.3115e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6423-1_0_2_load_32 | 34 | 0.0023428 | 0.00058716 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6423-1_0_2_load_34 | 35 | 0.0014518 | 0.00036385 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6423-1_0_2_load_35 | 36 | 0.00074128 | 0.00018578 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6423-1_0_2_load_132 | 39 | 0.00016976 | 4.2547e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6423-1_0_2_load_135 | 40 | 0.00091222 | 0.00022862 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6423-1_0_2_load_136 | 41 | 0.0011021 | 0.00027621 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6423-1_0_2_load_109 | 42 | 0.0012688 | 0.000318 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6423-1_0_2_load_130 | 44 | 0.0001746 | 4.376e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6423-1_0_2_load_131 | 45 | 0.00044659 | 0.00011193 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6423-1_0_2_load_104 | 46 | 0.00066691 | 0.00016714 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6423-1_0_2_load_107 | 47 | 0.0010855 | 0.00027206 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6423-1_0_2_load_105 | 48 | 0.00038251 | 9.5867e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6423-1_0_2_load_106 | 49 | 0.00037343 | 9.3591e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6423-1_0_2_load_108 | 50 | 0.0001852 | 4.6415e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6423-1_0_2_load_115 | 51 | 0.0016537 | 0.00041445 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6423-1_0_2_load_116 | 52 | 0.00035342 | 8.8576e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6423-1_0_2_load_117 | 53 | 0.00039678 | 9.9442e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6423-1_0_2_load_118 | 54 | 0.0022551 | 0.00056519 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6423-1_0_2_load_119 | 55 | 0.00071201 | 0.00017845 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6423-1_0_2_load_121 | 56 | 0.00077011 | 0.00019301 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6423-1_0_2_line_0 |  | 0 | 1 | 0.0090695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6423-1_0_2_line_1 |  | 1 | 2 | 0.073513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6423-1_0_2_line_2 |  | 2 | 3 | 0.017162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6423-1_0_2_line_3 |  | 3 | 7 | 0.016806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6423-1_0_2_line_4 |  | 4 | 5 | 0.015043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6423-1_0_2_line_5 |  | 4 | 6 | 0.019905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6423-1_0_2_line_6 |  | 5 | 11 | 0.030383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6423-1_0_2_line_7 |  | 6 | 28 | 0.016655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6423-1_0_2_line_8 |  | 6 | 7 | 0.033264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6423-1_0_2_line_9 |  | 8 | 9 | 0.11617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6423-1_0_2_line_10 |  | 8 | 10 | 0.043127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6423-1_0_2_line_11 |  | 9 | 11 | 0.019469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6423-1_0_2_line_12 |  | 10 | 12 | 0.040673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6423-1_0_2_line_13 |  | 12 | 13 | 0.02732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6423-1_0_2_line_14 |  | 13 | 14 | 0.027763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6423-1_0_2_line_15 |  | 14 | 15 | 0.026599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6423-1_0_2_line_16 |  | 15 | 16 | 0.016946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6423-1_0_2_line_17 |  | 16 | 19 | 0.059721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6423-1_0_2_line_18 |  | 17 | 18 | 0.031109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6423-1_0_2_line_19 |  | 18 | 21 | 0.033342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6423-1_0_2_line_20 |  | 19 | 20 | 0.024463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6423-1_0_2_line_21 |  | 20 | 21 | 0.0075736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6423-1_0_2_line_22 |  | 21 | 22 | 0.031712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6423-1_0_2_line_23 |  | 22 | 23 | 0.043465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6423-1_0_2_line_24 |  | 23 | 24 | 0.088345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6423-1_0_2_line_25 |  | 24 | 25 | 0.13172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6423-1_0_2_line_26 |  | 25 | 26 | 0.035132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6423-1_0_2_line_27 |  | 25 | 27 | 0.77093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6423-1_0_2_line_28 |  | 26 | 51 | 0.07536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6423-1_0_2_line_29 |  | 27 | 43 | 0.25776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6423-1_0_2_line_30 |  | 28 | 29 | 0.045494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6423-1_0_2_line_31 |  | 28 | 30 | 0.065608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6423-1_0_2_line_32 |  | 29 | 31 | 0.089953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6423-1_0_2_line_33 |  | 30 | 32 | 0.16033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6423-1_0_2_line_34 |  | 31 | 35 | 0.025637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6423-1_0_2_line_35 |  | 32 | 33 | 0.053917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6423-1_0_2_line_36 |  | 33 | 34 | 0.19956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6423-1_0_2_line_37 |  | 35 | 36 | 0.040718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6423-1_0_2_line_38 |  | 37 | 38 | 0.022318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6423-1_0_2_line_39 |  | 37 | 39 | 0.32357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6423-1_0_2_line_40 |  | 38 | 40 | 0.022517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6423-1_0_2_line_41 |  | 38 | 41 | 0.068768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6423-1_0_2_line_42 |  | 39 | 45 | 0.037684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6423-1_0_2_line_43 |  | 41 | 42 | 0.38488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6423-1_0_2_line_44 |  | 42 | 50 | 0.043795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6423-1_0_2_line_45 |  | 43 | 44 | 0.093562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6423-1_0_2_line_46 |  | 44 | 45 | 0.045328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6423-1_0_2_line_47 |  | 46 | 47 | 0.43834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6423-1_0_2_line_48 |  | 47 | 48 | 0.053348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6423-1_0_2_line_49 |  | 48 | 49 | 0.0056687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6423-1_0_2_line_50 |  | 49 | 50 | 0.010474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6423-1_0_2_line_51 |  | 51 | 52 | 0.20203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6423-1_0_2_line_52 |  | 52 | 53 | 0.079225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6423-1_0_2_line_53 |  | 53 | 54 | 0.073812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6423-1_0_2_line_54 |  | 54 | 55 | 0.0025628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6423-1_0_2_line_55 |  | 55 | 56 | 0.25118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6423-1_0_2_trafo_16 | 0.63 MVA 20/0.4 kV | 57 | 16 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2554489.4566 | 1213489.5532 | 2554495.7893 | 1213496.0456
1 | 2554440.8537 | 1213434.415 | 2554443.8192 | 1213437.7942 | 2554446.869 | 1213441.2729 | 2554480.7334 | 1213480.2033 | 2554484.2355 | 1213484.2345 | 2554489.4566 | 1213489.5532
2 | 2554440.8537 | 1213434.415 | 2554429.5338 | 1213421.5151
3 | 2554429.5338 | 1213421.5151 | 2554418.4486 | 1213408.8828
4 | 2554383.9628 | 1213368.4009 | 2554374.2254 | 1213356.9344
5 | 2554383.9628 | 1213368.4009 | 2554396.5086 | 1213383.8805
6 | 2554374.2254 | 1213356.9344 | 2554354.5589 | 1213333.7755
7 | 2554396.5086 | 1213383.8805 | 2554382.0875 | 1213392.2849
8 | 2554396.5086 | 1213383.8805 | 2554418.4486 | 1213408.8828
9 | 2554341.9567 | 1213318.9354 | 2554328.4428 | 1213303.0217 | 2554289.4895 | 1213260.4625 | 2554265.506 | 1213234.4537 | 2554264.0563 | 1213232.77
10 | 2554238.08 | 1213198.4212 | 2554243.221 | 1213206.1084 | 2554252.4301 | 1213219.2675 | 2554264.0563 | 1213232.77
11 | 2554341.9567 | 1213318.9354 | 2554354.5589 | 1213333.7755
12 | 2554238.08 | 1213198.4212 | 2554214.8615 | 1213207.7164 | 2554211.5954 | 1213207.7415 | 2554202.508 | 1213199.3095
13 | 2554202.508 | 1213199.3095 | 2554192.9272 | 1213190.4195 | 2554183.9077 | 1213179.3865
14 | 2554183.9077 | 1213179.3865 | 2554176.2635 | 1213170.0358 | 2554164.9845 | 1213160.3725 | 2554164.5424 | 1213159.6666
15 | 2554153.1795 | 1213135.6823 | 2554161.0622 | 1213154.1102 | 2554164.5424 | 1213159.6666
16 | 2554153.1795 | 1213135.6823 | 2554149.0314 | 1213125.764 | 2554147.5797 | 1213119.7408
17 | 2554147.5797 | 1213119.7408 | 2554138.0842 | 1213080.3438 | 2554135.2938 | 1213062.2881 | 2554135.0695 | 1213061.39
18 | 2554157.583 | 1213016.1558 | 2554169.559 | 1213044.867
19 | 2554127.3064 | 1213030.3086 | 2554157.583 | 1213016.1558
20 | 2554135.0695 | 1213061.39 | 2554129.1416 | 1213037.6565
21 | 2554127.3064 | 1213030.3086 | 2554129.1416 | 1213037.6565
22 | 2554127.3064 | 1213030.3086 | 2554119.6196 | 1212999.542
23 | 2554133.553 | 1212965.6224 | 2554117.9164 | 1212975.0818 | 2554116.3194 | 1212979.7747 | 2554115.9483 | 1212984.8472 | 2554119.6196 | 1212999.542
24 | 2554133.553 | 1212965.6224 | 2554126.1857 | 1212952.9939 | 2554119.585 | 1212942.2496 | 2554102.3541 | 1212916.4118 | 2554085.1817 | 1212891.7421
25 | 2554085.1817 | 1212891.7421 | 2554049.5183 | 1212840.5083 | 2554035.8101 | 1212819.3795 | 2554021.9709 | 1212796.0505 | 2554014.0487 | 1212781.0241
26 | 2554014.0487 | 1212781.0241 | 2554009.5426 | 1212772.4771 | 2553998.2953 | 1212749.6251
27 | 2554014.0487 | 1212781.0241 | 2553322.4591 | 1213121.6668
28 | 2553967.1617 | 1212680.9988 | 2553980.0124 | 1212709.4461 | 2553996.6997 | 1212746.3833 | 2553998.2953 | 1212749.6251
29 | 2553075.0161 | 1213049.4595 | 2553322.4591 | 1213121.6668
30 | 2554382.0875 | 1213392.2849 | 2554380.2705 | 1213398.0133 | 2554395.1241 | 1213434.5974
31 | 2554382.0875 | 1213392.2849 | 2554328.7105 | 1213371.4933 | 2554320.7259 | 1213369.14
32 | 2554395.1241 | 1213434.5974 | 2554400.2995 | 1213447.3444 | 2554411.8082 | 1213465.289 | 2554429.6302 | 1213497.2824 | 2554438.6836 | 1213513.1341
33 | 2554320.7259 | 1213369.14 | 2554266.2133 | 1213353.0737 | 2554238.1566 | 1213349.5207 | 2554210.1444 | 1213350.748 | 2554190.6055 | 1213349.5088 | 2554165.1341 | 1213338.8649
34 | 2554438.6836 | 1213513.1341 | 2554451.3981 | 1213535.3961
35 | 2554119.1097 | 1213352.2058 | 2554132.8959 | 1213339.3253 | 2554138.5344 | 1213334.7013 | 2554145.589 | 1213333.435 | 2554152.7007 | 1213333.6693 | 2554165.1341 | 1213338.8649
36 | 2554119.1097 | 1213352.2058 | 2554118.8007 | 1213358.423 | 2554118.3204 | 1213368.0435 | 2554126.8921 | 1213381.2852 | 2554144.8961 | 1213399.2125 | 2554150.8354 | 1213415.8543 | 2554171.6161 | 1213500.3773 | 2554177.889 | 1213537.6621
37 | 2554451.3981 | 1213535.3961 | 2554471.5918 | 1213570.7538
38 | 2553011.4458 | 1213558.4841 | 2553021.2211 | 1213551.7028 | 2553027.4747 | 1213543.3263
39 | 2553029.8028 | 1213219.7612 | 2553027.4747 | 1213543.3263
40 | 2553011.4458 | 1213558.4841 | 2553008.1168 | 1213553.4185 | 2552996.0698 | 1213542.2092
41 | 2553011.4458 | 1213558.4841 | 2553011.7891 | 1213565.4077 | 2553003.7032 | 1213606.2179 | 2553005.2523 | 1213618.6574 | 2553009.3751 | 1213625.1569
42 | 2553029.8028 | 1213219.7612 | 2553041.3833 | 1213183.9011
43 | 2552633.0782 | 1213544.3317 | 2553009.3751 | 1213625.1569
44 | 2552633.0782 | 1213544.3317 | 2552620.2143 | 1213528.547 | 2552602.9646 | 1213512.688
45 | 2553075.0161 | 1213049.4595 | 2553062.4213 | 1213118.7553 | 2553055.313 | 1213140.7666
46 | 2553055.313 | 1213140.7666 | 2553041.3833 | 1213183.9011
47 | 2552610.9291 | 1213459.5468 | 2552253.7484 | 1213205.4497
48 | 2552610.9291 | 1213459.5468 | 2552590.5219 | 1213474.2069 | 2552586.8213 | 1213483.5642 | 2552589.264 | 1213494.5957 | 2552592.5435 | 1213500.6201
49 | 2552592.5435 | 1213500.6201 | 2552595.2537 | 1213505.5989 | 2552595.2537 | 1213505.5989
50 | 2552602.9646 | 1213512.688 | 2552595.2537 | 1213505.5989
51 | 2553967.1617 | 1212680.9988 | 2553929.6398 | 1212597.937 | 2553917.7024 | 1212572.1143 | 2553901.1003 | 1212538.4564 | 2553887.96 | 1212513.3213 | 2553879.698 | 1212498.9843
52 | 2553836.6921 | 1212432.4747 | 2553855.9217 | 1212461.2612 | 2553872.8434 | 1212487.0897 | 2553879.698 | 1212498.9843
53 | 2553836.6921 | 1212432.4747 | 2553795.6919 | 1212371.0978
54 | 2553795.6919 | 1212371.0978 | 2553794.2684 | 1212368.9668
55 | 2553794.2684 | 1212368.9668 | 2553657.8485 | 1212158.0566

## bus_geodata
| x | y | coords
0 | 2554495.7893 | 1213496.0456
1 | 2554489.4566 | 1213489.5532
2 | 2554440.8537 | 1213434.415
3 | 2554429.5338 | 1213421.5151
4 | 2554383.9628 | 1213368.4009
5 | 2554374.2254 | 1213356.9344
6 | 2554396.5086 | 1213383.8805
7 | 2554418.4486 | 1213408.8828
8 | 2554264.0563 | 1213232.77
9 | 2554341.9567 | 1213318.9354
10 | 2554238.08 | 1213198.4212
11 | 2554354.5589 | 1213333.7755
12 | 2554202.508 | 1213199.3095
13 | 2554183.9077 | 1213179.3865
14 | 2554164.5424 | 1213159.6666
15 | 2554153.1795 | 1213135.6823
16 | 2554147.5797 | 1213119.7408
17 | 2554169.559 | 1213044.867
18 | 2554157.583 | 1213016.1558
19 | 2554135.0695 | 1213061.39
20 | 2554129.1416 | 1213037.6565
21 | 2554127.3064 | 1213030.3086
22 | 2554119.6196 | 1212999.542
23 | 2554133.553 | 1212965.6224
24 | 2554085.1817 | 1212891.7421
25 | 2554014.0487 | 1212781.0241
26 | 2553998.2953 | 1212749.6251
27 | 2553322.4591 | 1213121.6668
28 | 2554382.0875 | 1213392.2849
29 | 2554395.1241 | 1213434.5974
30 | 2554320.7259 | 1213369.14
31 | 2554438.6836 | 1213513.1341
32 | 2554165.1341 | 1213338.8649
33 | 2554119.1097 | 1213352.2058
34 | 2554177.889 | 1213537.6621
35 | 2554451.3981 | 1213535.3961
36 | 2554471.5918 | 1213570.7538
37 | 2553027.4747 | 1213543.3263
38 | 2553011.4458 | 1213558.4841
39 | 2553029.8028 | 1213219.7612
40 | 2552996.0698 | 1213542.2092
41 | 2553009.3751 | 1213625.157
42 | 2552633.0782 | 1213544.3317
43 | 2553075.0161 | 1213049.4595
44 | 2553055.313 | 1213140.7666
45 | 2553041.3833 | 1213183.9011
46 | 2552253.7484 | 1213205.4497
47 | 2552610.9291 | 1213459.5468
48 | 2552592.5435 | 1213500.6201
49 | 2552595.2537 | 1213505.5989
50 | 2552602.9646 | 1213512.688
51 | 2553967.1617 | 1212680.9988
52 | 2553879.698 | 1212498.9843
53 | 2553836.6921 | 1212432.4747
54 | 2553795.6919 | 1212371.0978
55 | 2553794.2684 | 1212368.9668
56 | 2553657.8485 | 1212158.0566
57 | 2554147.5797 | 1213119.7408

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1