## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2422-12_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2422-12_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2422-12_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2422-12_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2422-12_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2422-12_0_3_node_98 | 0.4 | n |  | TRUE
6 | bus_LV_2422-12_0_3_node_96 | 0.4 | n |  | TRUE
7 | bus_LV_2422-12_0_3_node_121 | 0.4 | n |  | TRUE
8 | bus_LV_2422-12_0_3_node_97 | 0.4 | n |  | TRUE
9 | bus_LV_2422-12_0_3_node_95 | 0.4 | n |  | TRUE
10 | bus_LV_2422-12_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2422-12_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2422-12_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2422-12_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2422-12_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2422-12_0_3_node_41 | 0.4 | n |  | TRUE
16 | bus_LV_2422-12_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2422-12_0_3_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_2422-12_0_3_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_2422-12_0_3_node_42 | 0.4 | n |  | TRUE
20 | bus_LV_2422-12_0_3_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_2422-12_0_3_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_2422-12_0_3_node_45 | 0.4 | n |  | TRUE
23 | bus_LV_2422-12_0_3_node_113 | 0.4 | n |  | TRUE
24 | bus_LV_2422-12_0_3_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_2422-12_0_3_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_2422-12_0_3_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_2422-12_0_3_node_75 | 0.4 | n |  | TRUE
28 | bus_LV_2422-12_0_3_node_32 | 0.4 | n |  | TRUE
29 | bus_LV_2422-12_0_3_node_73 | 0.4 | n |  | TRUE
30 | bus_LV_2422-12_0_3_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_2422-12_0_3_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_2422-12_0_3_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_2422-12_0_3_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_2422-12_0_3_node_79 | 0.4 | n |  | TRUE
35 | bus_LV_2422-12_0_3_node_78 | 0.4 | n |  | TRUE
36 | bus_LV_2422-12_0_3_node_77 | 0.4 | n |  | TRUE
37 | bus_LV_2422-12_0_3_node_43 | 0.4 | n |  | TRUE
38 | bus_LV_2422-12_0_3_node_86 | 0.4 | n |  | TRUE
39 | bus_LV_2422-12_0_3_node_84 | 0.4 | n |  | TRUE
40 | bus_LV_2422-12_0_3_node_46 | 0.4 | n |  | TRUE
41 | bus_LV_2422-12_0_3_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_2422-12_0_3_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_2422-12_0_3_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_2422-12_0_3_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_2422-12_0_3_node_125 | 0.4 | n |  | TRUE
46 | bus_LV_2422-12_0_3_node_60 | 0.4 | n |  | TRUE
47 | bus_LV_2422-12_0_3_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_2422-12_0_3_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_2422-12_0_3_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_2422-12_0_3_node_30 | 0.4 | n |  | TRUE
51 | bus_LV_2422-12_0_3_node_114 | 0.4 | n |  | TRUE
52 | bus_LV_2422-12_0_3_node_81 | 0.4 | n |  | TRUE
53 | bus_LV_2422-12_0_3_node_100 | 0.4 | n |  | TRUE
54 | bus_LV_2422-12_0_3_node_80 | 0.4 | n |  | TRUE
55 | bus_LV_2422-12_0_3_node_99 | 0.4 | n |  | TRUE
56 | bus_LV_2422-12_0_3_node_33 | 0.4 | n |  | TRUE
57 | bus_LV_2422-12_0_3_node_34 | 0.4 | n |  | TRUE
58 | bus_LV_2422-12_0_3_node_70 | 0.4 | n |  | TRUE
59 | bus_LV_2422-12_0_3_node_65 | 0.4 | n |  | TRUE
60 | bus_LV_2422-12_0_3_node_126 | 0.4 | n |  | TRUE
61 | bus_LV_2422-12_0_3_node_71 | 0.4 | n |  | TRUE
62 | bus_LV_2422-12_0_3_node_63 | 0.4 | n |  | TRUE
63 | bus_LV_2422-12_0_3_node_127 | 0.4 | n |  | TRUE
64 | bus_LV_2422-12_0_3_node_36 | 0.4 | n |  | TRUE
65 | bus_LV_2422-12_0_3_node_37 | 0.4 | n |  | TRUE
66 | bus_LV_2422-12_0_3_node_38 | 0.4 | n |  | TRUE
67 | bus_LV_2422-12_0_3_node_39 | 0.4 | n |  | TRUE
68 | bus_LV_2422-12_0_3_node_40 | 0.4 | n |  | TRUE
69 | bus_LV_2422-12_0_3_node_67 | 0.4 | n |  | TRUE
70 | bus_LV_2422-12_0_3_node_93 | 0.4 | n |  | TRUE
71 | bus_LV_2422-12_0_3_node_68 | 0.4 | n |  | TRUE
72 | bus_LV_2422-12_0_3_node_91 | 0.4 | n |  | TRUE
73 | bus_LV_2422-12_0_3_node_106 | 0.4 | n |  | TRUE
74 | bus_LV_2422-12_0_3_node_105 | 0.4 | n |  | TRUE
75 | bus_LV_2422-12_0_3_node_104 | 0.4 | n |  | TRUE
76 | bus_LV_2422-12_0_3_node_107 | 0.4 | n |  | TRUE
77 | bus_LV_2422-12_0_3_node_111 | 0.4 | n |  | TRUE
78 | bus_LV_2422-12_0_3_node_110 | 0.4 | n |  | TRUE
79 | bus_LV_2422-12_0_3_node_109 | 0.4 | n |  | TRUE
80 | bus_LV_2422-12_0_3_node_47 | 0.4 | n |  | TRUE
81 | bus_LV_2422-12_0_3_node_48 | 0.4 | n |  | TRUE
82 | bus_LV_2422-12_0_3_node_49 | 0.4 | n |  | TRUE
83 | bus_LV_2422-12_0_3_node_50 | 0.4 | n |  | TRUE
84 | bus_LV_2422-12_0_3_node_51 | 0.4 | n |  | TRUE
85 | bus_LV_2422-12_0_3_node_87 | 0.4 | n |  | TRUE
86 | bus_LV_2422-12_0_3_node_120 | 0.4 | n |  | TRUE
87 | bus_LV_2422-12_0_3_node_56 | 0.4 | n |  | TRUE
88 | bus_LV_2422-12_0_3_node_61 | 0.4 | n |  | TRUE
89 | bus_LV_2422-12_0_3_node_52 | 0.4 | n |  | TRUE
90 | bus_LV_2422-12_0_3_node_53 | 0.4 | n |  | TRUE
91 | bus_LV_2422-12_0_3_node_54 | 0.4 | n |  | TRUE
92 | bus_LV_2422-12_0_3_node_112 | 0.4 | n |  | TRUE
93 | bus_LV_2422-12_0_3_node_102 | 0.4 | n |  | TRUE
94 | bus_LV_2422-12_0_3_node_117 | 0.4 | n |  | TRUE
95 | bus_LV_2422-12_0_3_node_101 | 0.4 | n |  | TRUE
96 | bus_LV_2422-12_0_3_node_57 | 0.4 | n |  | TRUE
97 | bus_LV_2422-12_0_3_node_58 | 0.4 | n |  | TRUE
98 | bus_LV_2422-12_0_3_node_59 | 0.4 | n |  | TRUE
99 | bus_LV_2422-12_0_3_node_62 | 0.4 | n |  | TRUE
100 | bus_LV_2422-12_0_3_node_64 | 0.4 | n |  | TRUE
101 | bus_LV_2422-12_0_3_node_66 | 0.4 | n |  | TRUE
102 | bus_LV_2422-12_0_3_node_89 | 0.4 | n |  | TRUE
103 | bus_LV_2422-12_0_3_node_90 | 0.4 | n |  | TRUE
104 | bus_LV_2422-12_0_3_node_69 | 0.4 | n |  | TRUE
105 | bus_LV_2422-12_0_3_node_94 | 0.4 | n |  | TRUE
106 | bus_LV_2422-12_0_3_node_92 | 0.4 | n |  | TRUE
107 | bus_LV_2422-12_0_3_node_85 | 0.4 | n |  | TRUE
108 | bus_LV_2422-12_0_3_node_72 | 0.4 | n |  | TRUE
109 | bus_LV_2422-12_0_3_node_74 | 0.4 | n |  | TRUE
110 | bus_LV_2422-12_0_3_node_76 | 0.4 | n |  | TRUE
111 | bus_LV_2422-12_0_3_node_116 | 0.4 | n |  | TRUE
112 | bus_LV_2422-12_0_3_node_118 | 0.4 | n |  | TRUE
113 | bus_LV_2422-12_0_3_node_82 | 0.4 | n |  | TRUE
114 | bus_LV_2422-12_0_3_node_83 | 0.4 | n |  | TRUE
115 | bus_LV_2422-12_0_3_node_103 | 0.4 | n |  | TRUE
116 | bus_LV_2422-12_0_3_node_122 | 0.4 | n |  | TRUE
117 | bus_LV_2422-12_0_3_node_123 | 0.4 | n |  | TRUE
118 | bus_LV_2422-12_0_3_node_129 | 0.4 | n |  | TRUE
119 | bus_LV_2422-12_0_3_node_108 | 0.4 | n |  | TRUE
120 | bus_LV_2422-12_0_3_node_119 | 0.4 | n |  | TRUE
121 | bus_LV_2422-12_0_3_node_115 | 0.4 | n |  | TRUE
122 | bus_MV_333_0_node_10 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2422-12_0_3_load_0 | 0 | 0.0015207 | 0.00038112 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2422-12_0_3_load_1 | 1 | 0.0015205 | 0.00038107 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2422-12_0_3_load_2 | 2 | 0.0013884 | 0.00034795 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2422-12_0_3_load_3 | 3 | 0.0021791 | 0.00054615 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2422-12_0_3_load_4 | 4 | 0.0010714 | 0.00026851 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2422-12_0_3_load_95 | 9 | 0.0037897 | 0.00094979 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2422-12_0_3_load_5 | 10 | 0.0013296 | 0.00033323 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2422-12_0_3_load_6 | 11 | 0.0020965 | 0.00052544 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2422-12_0_3_load_7 | 12 | 0.002397 | 0.00060075 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2422-12_0_3_load_8 | 13 | 0.0036894 | 0.00092465 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2422-12_0_3_load_41 | 15 | 0.0024572 | 0.00061584 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2422-12_0_3_load_21 | 17 | 0.0032489 | 0.00081426 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2422-12_0_3_load_22 | 18 | 0.002106 | 0.00052783 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2422-12_0_3_load_31 | 20 | 0.0023031 | 0.00057721 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2422-12_0_3_load_11 | 21 | 0.0025762 | 0.00064566 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2422-12_0_3_load_45 | 22 | 0.001715 | 0.00042983 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2422-12_0_3_load_113 | 23 | 0.0022112 | 0.00055417 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2422-12_0_3_load_10 | 24 | 0.0015585 | 0.0003906 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2422-12_0_3_load_12 | 25 | 0.0018017 | 0.00045156 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2422-12_0_3_load_14 | 26 | 0.002973 | 0.0007451 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2422-12_0_3_load_75 | 27 | 0.0017448 | 0.00043729 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2422-12_0_3_load_73 | 29 | 0.0013305 | 0.00033345 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2422-12_0_3_load_15 | 30 | 0.0018436 | 0.00046204 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2422-12_0_3_load_16 | 31 | 0.0031083 | 0.00077902 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2422-12_0_3_load_18 | 32 | 0.0021731 | 0.00054463 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2422-12_0_3_load_35 | 33 | 0.0026421 | 0.00066216 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2422-12_0_3_load_78 | 35 | 0.0027566 | 0.00069087 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2422-12_0_3_load_77 | 36 | 0.0025008 | 0.00062676 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2422-12_0_3_load_86 | 38 | 0.0029969 | 0.00075108 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2422-12_0_3_load_84 | 39 | 0.002769 | 0.00069398 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2422-12_0_3_load_46 | 40 | 0.0017909 | 0.00044883 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2422-12_0_3_load_23 | 42 | 0.00064336 | 0.00016124 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2422-12_0_3_load_24 | 43 | 0.00080822 | 0.00020256 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2422-12_0_3_load_25 | 44 | 0.00055656 | 0.00013949 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2422-12_0_3_load_125 | 45 | 0.001116 | 0.00027969 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2422-12_0_3_load_60 | 46 | 0.0011349 | 0.00028444 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2422-12_0_3_load_26 | 47 | 0.0027163 | 0.00068078 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2422-12_0_3_load_27 | 48 | 0.0014688 | 0.00036811 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2422-12_0_3_load_28 | 49 | 0.0019376 | 0.00048561 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2422-12_0_3_load_30 | 50 | 0.0010295 | 0.00025802 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2422-12_0_3_load_114 | 51 | 0.0027582 | 0.00069127 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2422-12_0_3_load_81 | 52 | 0.0021658 | 0.00054279 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2422-12_0_3_load_100 | 53 | 0.0022413 | 0.00056171 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2422-12_0_3_load_80 | 54 | 0.0013938 | 0.00034932 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2422-12_0_3_load_99 | 55 | 0.0020222 | 0.00050682 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2422-12_0_3_load_33 | 56 | 0.0029812 | 0.00074715 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2422-12_0_3_load_70 | 58 | 0.0048982 | 0.0012276 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2422-12_0_3_load_65 | 59 | 0.001741 | 0.00043634 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2422-12_0_3_load_126 | 60 | 0.0017628 | 0.00044179 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2422-12_0_3_load_71 | 61 | 0.0024902 | 0.00062412 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2422-12_0_3_load_63 | 62 | 0.0023401 | 0.00058648 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2422-12_0_3_load_127 | 63 | 0.0020992 | 0.00052611 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2422-12_0_3_load_36 | 64 | 0.0011898 | 0.00029819 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2422-12_0_3_load_37 | 65 | 0.002022 | 0.00050677 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2422-12_0_3_load_39 | 67 | 0.0029362 | 0.00073589 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2422-12_0_3_load_40 | 68 | 0.0028337 | 0.00071019 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2422-12_0_3_load_93 | 70 | 0.00097149 | 0.00024348 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2422-12_0_3_load_91 | 72 | 0.0020852 | 0.00052259 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2422-12_0_3_load_106 | 73 | 0.0018617 | 0.00046658 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2422-12_0_3_load_105 | 74 | 0.0017289 | 0.0004333 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2422-12_0_3_load_104 | 75 | 0.0025137 | 0.00063 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2422-12_0_3_load_107 | 76 | 0.0010492 | 0.00026294 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2422-12_0_3_load_111 | 77 | 0.0011939 | 0.00029922 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2422-12_0_3_load_110 | 78 | 0.0019442 | 0.00048725 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2422-12_0_3_load_109 | 79 | 0.0017824 | 0.00044671 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2422-12_0_3_load_47 | 80 | 0.0006127 | 0.00015356 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2422-12_0_3_load_48 | 81 | 0.00054977 | 0.00013779 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2422-12_0_3_load_49 | 82 | 0.00052386 | 0.00013129 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2422-12_0_3_load_50 | 83 | 0.0032751 | 0.00082083 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2422-12_0_3_load_51 | 84 | 0.0012247 | 0.00030695 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2422-12_0_3_load_87 | 85 | 0.0059993 | 0.0015036 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2422-12_0_3_load_120 | 86 | 0.00097504 | 0.00024437 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2422-12_0_3_load_61 | 88 | 0.00065033 | 0.00016299 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2422-12_0_3_load_52 | 89 | 0.0025047 | 0.00062773 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2422-12_0_3_load_53 | 90 | 0.00071607 | 0.00017946 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2422-12_0_3_load_54 | 91 | 0.0040045 | 0.0010036 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2422-12_0_3_load_112 | 92 | 0.002214 | 0.00055487 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2422-12_0_3_load_102 | 93 | 0.0062971 | 0.0015782 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2422-12_0_3_load_101 | 95 | 0.0034003 | 0.0008522 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2422-12_0_3_load_57 | 96 | 0.0012406 | 0.00031093 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2422-12_0_3_load_58 | 97 | 0.0007978 | 0.00019995 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2422-12_0_3_load_59 | 98 | 0.001162 | 0.00029122 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2422-12_0_3_load_62 | 99 | 0.0019255 | 0.00048257 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2422-12_0_3_load_64 | 100 | 0.0014569 | 0.00036514 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2422-12_0_3_load_66 | 101 | 0.0021097 | 0.00052873 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2422-12_0_3_load_89 | 102 | 0.0010216 | 0.00025603 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2422-12_0_3_load_90 | 103 | 0.0022183 | 0.00055596 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2422-12_0_3_load_69 | 104 | 0.0013108 | 0.00032852 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2422-12_0_3_load_92 | 106 | 0.00099142 | 0.00024847 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2422-12_0_3_load_85 | 107 | 0.0029528 | 0.00074005 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2422-12_0_3_load_72 | 108 | 0.0038241 | 0.00095842 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2422-12_0_3_load_74 | 109 | 0.0024457 | 0.00061295 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2422-12_0_3_load_76 | 110 | 0.0050732 | 0.0012715 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2422-12_0_3_load_118 | 112 | 0.0030173 | 0.00075621 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2422-12_0_3_load_82 | 113 | 0.001876 | 0.00047017 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2422-12_0_3_load_83 | 114 | 0.0022462 | 0.00056294 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2422-12_0_3_load_103 | 115 | 0.0019674 | 0.00049307 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2422-12_0_3_load_122 | 116 | 0.0022892 | 0.00057372 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2422-12_0_3_load_123 | 117 | 0.0024984 | 0.00062617 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2422-12_0_3_load_129 | 118 | 0.0013329 | 0.00033405 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2422-12_0_3_load_108 | 119 | 0.0013762 | 0.00034492 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2422-12_0_3_load_119 | 120 | 0.0034303 | 0.00085971 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2422-12_0_3_load_115 | 121 | 0.0042726 | 0.0010708 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2422-12_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.00429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2422-12_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0015201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2422-12_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.022685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2422-12_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.010117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2422-12_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.015945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2422-12_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0098546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2422-12_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.096331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2422-12_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.016838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2422-12_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.032885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2422-12_0_3_line_9 | NAYY 4x150 SE | 7 | 118 | 0.064642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2422-12_0_3_line_10 | NAYY 4x150 SE | 8 | 63 | 0.030059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2422-12_0_3_line_11 | NAYY 4x150 SE | 8 | 33 | 0.0033031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2422-12_0_3_line_12 | NAYY 4x150 SE | 9 | 34 | 0.018542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2422-12_0_3_line_13 | NAYY 4x150 SE | 10 | 11 | 0.022491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2422-12_0_3_line_14 | NAYY 4x150 SE | 10 | 12 | 0.032189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2422-12_0_3_line_15 | NAYY 4x150 SE | 11 | 13 | 0.021193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2422-12_0_3_line_16 | NAYY 4x150 SE | 12 | 14 | 0.020575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2422-12_0_3_line_17 | NAYY 4x150 SE | 13 | 15 | 0.027189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2422-12_0_3_line_18 | NAYY 4x150 SE | 14 | 16 | 0.044153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_2422-12_0_3_line_19 | NAYY 4x150 SE | 14 | 17 | 0.022308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2422-12_0_3_line_20 | NAYY 4x150 SE | 14 | 18 | 0.0094709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_2422-12_0_3_line_21 | NAYY 4x150 SE | 15 | 19 | 0.010227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2422-12_0_3_line_22 | NAYY 4x150 SE | 16 | 20 | 0.016199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2422-12_0_3_line_23 | NAYY 4x150 SE | 16 | 21 | 0.046101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_2422-12_0_3_line_24 | NAYY 4x150 SE | 17 | 22 | 0.010791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2422-12_0_3_line_25 | NAYY 4x150 SE | 18 | 23 | 0.01464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_2422-12_0_3_line_26 | NAYY 4x150 SE | 19 | 37 | 0.017841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2422-12_0_3_line_27 | NAYY 4x150 SE | 20 | 28 | 0.023346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2422-12_0_3_line_28 | NAYY 4x150 SE | 21 | 24 | 0.028999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2422-12_0_3_line_29 | NAYY 4x150 SE | 22 | 40 | 0.017975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2422-12_0_3_line_30 | NAYY 4x150 SE | 23 | 41 | 0.03557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_2422-12_0_3_line_31 | NAYY 4x150 SE | 24 | 25 | 0.023838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2422-12_0_3_line_32 | NAYY 4x150 SE | 25 | 26 | 0.010603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2422-12_0_3_line_33 | NAYY 4x150 SE | 26 | 27 | 0.021774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2422-12_0_3_line_34 | NAYY 4x150 SE | 27 | 29 | 0.0191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2422-12_0_3_line_35 | NAYY 4x150 SE | 28 | 56 | 0.013462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2422-12_0_3_line_36 | NAYY 4x150 SE | 28 | 57 | 0.009266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2422-12_0_3_line_37 | NAYY 4x150 SE | 29 | 108 | 0.0085346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2422-12_0_3_line_38 | NAYY 4x150 SE | 30 | 31 | 0.002274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2422-12_0_3_line_39 | NAYY 4x150 SE | 31 | 32 | 0.021432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2422-12_0_3_line_40 | NAYY 4x150 SE | 32 | 33 | 0.032351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2422-12_0_3_line_41 | NAYY 4x150 SE | 34 | 35 | 0.015784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2422-12_0_3_line_42 | NAYY 4x150 SE | 35 | 36 | 0.029119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2422-12_0_3_line_43 | NAYY 4x150 SE | 37 | 73 | 0.038504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2422-12_0_3_line_44 | NAYY 4x150 SE | 38 | 39 | 0.016389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2422-12_0_3_line_45 | NAYY 4x150 SE | 39 | 107 | 0.012285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2422-12_0_3_line_46 | NAYY 4x150 SE | 40 | 78 | 0.0053523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2422-12_0_3_line_47 | NAYY 4x150 SE | 41 | 51 | 0.045789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2422-12_0_3_line_48 | NAYY 4x150 SE | 41 | 52 | 0.0062024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2422-12_0_3_line_49 | NAYY 4x150 SE | 41 | 48 | 0.017632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
50 | LV_2422-12_0_3_line_50 | NAYY 4x150 SE | 42 | 43 | 0.0043472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2422-12_0_3_line_51 | NAYY 4x150 SE | 43 | 44 | 0.042764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2422-12_0_3_line_52 | NAYY 4x150 SE | 44 | 45 | 0.1311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2422-12_0_3_line_53 | NAYY 4x150 SE | 45 | 46 | 0.017411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2422-12_0_3_line_54 | NAYY 4x150 SE | 46 | 97 | 0.039654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2422-12_0_3_line_55 | NAYY 4x150 SE | 47 | 48 | 0.022333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_2422-12_0_3_line_56 | NAYY 4x150 SE | 47 | 49 | 0.039044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
57 | LV_2422-12_0_3_line_57 | NAYY 4x150 SE | 49 | 50 | 0.018059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
58 | LV_2422-12_0_3_line_58 | NAYY 4x150 SE | 50 | 53 | 0.020526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2422-12_0_3_line_59 | NAYY 4x150 SE | 52 | 54 | 0.01015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2422-12_0_3_line_60 | NAYY 4x150 SE | 53 | 55 | 0.023143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2422-12_0_3_line_61 | NAYY 4x150 SE | 54 | 113 | 0.036181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2422-12_0_3_line_62 | NAYY 4x150 SE | 55 | 95 | 0.040942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2422-12_0_3_line_63 | NAYY 4x150 SE | 56 | 58 | 0.020614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2422-12_0_3_line_64 | NAYY 4x150 SE | 57 | 59 | 0.015101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2422-12_0_3_line_65 | NAYY 4x150 SE | 57 | 60 | 0.033321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2422-12_0_3_line_66 | NAYY 4x150 SE | 58 | 61 | 0.011104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2422-12_0_3_line_67 | NAYY 4x150 SE | 59 | 62 | 0.027602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2422-12_0_3_line_68 | NAYY 4x150 SE | 60 | 63 | 0.021969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2422-12_0_3_line_69 | NAYY 4x150 SE | 61 | 107 | 0.018414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2422-12_0_3_line_70 | NAYY 4x150 SE | 62 | 99 | 0.00065634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2422-12_0_3_line_71 | NAYY 4x150 SE | 64 | 65 | 0.022381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2422-12_0_3_line_72 | NAYY 4x150 SE | 64 | 66 | 0.024813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2422-12_0_3_line_73 | NAYY 4x150 SE | 65 | 67 | 0.0018059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2422-12_0_3_line_74 | NAYY 4x150 SE | 66 | 68 | 0.0068691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2422-12_0_3_line_75 | NAYY 4x150 SE | 67 | 69 | 0.015515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2422-12_0_3_line_76 | NAYY 4x150 SE | 68 | 70 | 0.012753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2422-12_0_3_line_77 | NAYY 4x150 SE | 69 | 71 | 0.012056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2422-12_0_3_line_78 | NAYY 4x150 SE | 70 | 72 | 0.023001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2422-12_0_3_line_79 | NAYY 4x150 SE | 71 | 77 | 0.0032918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2422-12_0_3_line_80 | NAYY 4x150 SE | 72 | 106 | 0.032876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2422-12_0_3_line_81 | NAYY 4x150 SE | 73 | 76 | 0.0092076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2422-12_0_3_line_82 | NAYY 4x150 SE | 74 | 75 | 0.00425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2422-12_0_3_line_83 | NAYY 4x150 SE | 75 | 115 | 0.014064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2422-12_0_3_line_84 | NAYY 4x150 SE | 76 | 105 | 0.01252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2422-12_0_3_line_85 | NAYY 4x150 SE | 78 | 79 | 0.021336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2422-12_0_3_line_86 | NAYY 4x150 SE | 79 | 119 | 0.0018828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2422-12_0_3_line_87 | NAYY 4x150 SE | 80 | 81 | 0.002563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2422-12_0_3_line_88 | NAYY 4x150 SE | 80 | 82 | 0.022326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2422-12_0_3_line_89 | NAYY 4x150 SE | 81 | 83 | 0.022871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2422-12_0_3_line_90 | NAYY 4x150 SE | 82 | 84 | 0.018847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2422-12_0_3_line_91 | NAYY 4x150 SE | 83 | 85 | 0.0054921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2422-12_0_3_line_92 | NAYY 4x150 SE | 84 | 86 | 0.0079331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2422-12_0_3_line_93 | NAYY 4x150 SE | 85 | 87 | 0.047478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2422-12_0_3_line_94 | NAYY 4x150 SE | 86 | 88 | 0.0064883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2422-12_0_3_line_95 | NAYY 4x150 SE | 87 | 92 | 0.044489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2422-12_0_3_line_96 | NAYY 4x150 SE | 87 | 93 | 0.020997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2422-12_0_3_line_97 | NAYY 4x150 SE | 87 | 91 | 0.016028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2422-12_0_3_line_98 | NAYY 4x150 SE | 88 | 98 | 0.026854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2422-12_0_3_line_99 | NAYY 4x150 SE | 89 | 90 | 0.027132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2422-12_0_3_line_100 | NAYY 4x150 SE | 89 | 91 | 0.013273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2422-12_0_3_line_101 | NAYY 4x150 SE | 92 | 94 | 0.01726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2422-12_0_3_line_102 | NAYY 4x150 SE | 93 | 95 | 0.00023654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2422-12_0_3_line_103 | NAYY 4x150 SE | 94 | 120 | 0.017836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2422-12_0_3_line_104 | NAYY 4x150 SE | 94 | 121 | 0.0030762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2422-12_0_3_line_105 | NAYY 4x150 SE | 96 | 97 | 0.0073156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2422-12_0_3_line_106 | NAYY 4x150 SE | 96 | 98 | 0.01875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2422-12_0_3_line_107 | NAYY 4x150 SE | 99 | 100 | 0.032032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2422-12_0_3_line_108 | NAYY 4x150 SE | 100 | 101 | 0.0064207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2422-12_0_3_line_109 | NAYY 4x150 SE | 101 | 102 | 0.0192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2422-12_0_3_line_110 | NAYY 4x150 SE | 102 | 103 | 0.022489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2422-12_0_3_line_111 | NAYY 4x150 SE | 103 | 116 | 0.012766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2422-12_0_3_line_112 | NAYY 4x150 SE | 104 | 105 | 0.013865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2422-12_0_3_line_113 | NAYY 4x150 SE | 105 | 106 | 0.016331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2422-12_0_3_line_114 | NAYY 4x150 SE | 108 | 109 | 0.023087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2422-12_0_3_line_115 | NAYY 4x150 SE | 109 | 110 | 0.0060744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2422-12_0_3_line_116 | NAYY 4x150 SE | 110 | 111 | 0.017202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2422-12_0_3_line_117 | NAYY 4x150 SE | 111 | 112 | 0.014804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2422-12_0_3_line_118 | NAYY 4x150 SE | 113 | 114 | 0.0047507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2422-12_0_3_line_119 | NAYY 4x150 SE | 114 | 115 | 0.016061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2422-12_0_3_line_120 | NAYY 4x150 SE | 116 | 117 | 0.010085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2422-12_0_3_trafo_11 | 0.25 MVA 20/0.4 kV | 122 | 21 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2619092.3893 | 1240693.5163 | 2619090.0714 | 1240689.9064
1 | 2619092.3893 | 1240693.5163 | 2619093.2107 | 1240694.7955
2 | 2619090.0714 | 1240689.9064 | 2619077.8144 | 1240670.8174
3 | 2619093.2107 | 1240694.7955 | 2619098.6771 | 1240703.3089
4 | 2619069.1993 | 1240657.4002 | 2619077.8144 | 1240670.8174
5 | 2619104.0016 | 1240711.6013 | 2619098.6771 | 1240703.3089
6 | 2619015.3986 | 1240604.7063 | 2619036.1002 | 1240592.8984 | 2619069.1993 | 1240657.4002
7 | 2619113.8547 | 1240725.2748 | 2619104.0016 | 1240711.6013
8 | 2619104.0016 | 1240711.6013 | 2619114.6174 | 1240706.7434 | 2619127.4802 | 1240689.8778
9 | 2619015.3986 | 1240604.7063 | 2619045.3982 | 1240662.0047
10 | 2619113.8547 | 1240725.2748 | 2619106.1764 | 1240733.6554 | 2619097.3203 | 1240750.1172
11 | 2619113.8547 | 1240725.2748 | 2619116.0796 | 1240727.7162
12 | 2619138.7245 | 1240675.1344 | 2619127.4802 | 1240689.8778
13 | 2619034.5022 | 1240874.4002 | 2619056.1101 | 1240880.6398
14 | 2619034.5022 | 1240874.4002 | 2619022.4033 | 1240870.9064 | 2619006.0103 | 1240860.1695
15 | 2619056.1101 | 1240880.6398 | 2619076.4716 | 1240886.5195
16 | 2618988.7989 | 1240848.8965 | 2619006.0103 | 1240860.1695
17 | 2619102.5937 | 1240894.0627 | 2619076.4716 | 1240886.5195
18 | 2619023.6043 | 1240821.6016 | 2618988.7989 | 1240848.8965
19 | 2618988.7989 | 1240848.8965 | 2618979.2228 | 1240828.7481
20 | 2618988.7989 | 1240848.8965 | 2618983.0866 | 1240856.4508
21 | 2619112.4188 | 1240896.8999 | 2619102.5937 | 1240894.0627
22 | 2619023.6043 | 1240821.6016 | 2619036.6521 | 1240812.0018
23 | 2619023.6043 | 1240821.6016 | 2619000.5209 | 1240781.6961
24 | 2618979.2228 | 1240828.7481 | 2618974.5908 | 1240819.0021
25 | 2618974.2564 | 1240868.1284 | 2618983.0866 | 1240856.4508
26 | 2619102.7009 | 1240911.8781 | 2619112.4188 | 1240896.8999
27 | 2619055.4566 | 1240798.1666 | 2619036.6521 | 1240812.0018
28 | 2618986.0006 | 1240756.5938 | 2619000.5209 | 1240781.6961
29 | 2618974.5908 | 1240819.0021 | 2618966.8749 | 1240802.7677
30 | 2618952.8026 | 1240896.5005 | 2618974.2564 | 1240868.1284
31 | 2618974.0644 | 1240735.9591 | 2618986.0006 | 1240756.5938
32 | 2618974.0644 | 1240735.9591 | 2618968.7554 | 1240726.7811
33 | 2618957.853 | 1240707.9335 | 2618968.7554 | 1240726.7811
34 | 2618948.2892 | 1240691.4001 | 2618957.853 | 1240707.9335
35 | 2619055.4566 | 1240798.1666 | 2619063.5848 | 1240807.454 | 2619064.6496 | 1240807.8026
36 | 2619063.1021 | 1240792.8989 | 2619055.4566 | 1240798.1666
37 | 2618944.0159 | 1240684.0124 | 2618948.2892 | 1240691.4001
38 | 2619155.5789 | 1240767.357 | 2619153.8534 | 1240765.8758
39 | 2619137.8813 | 1240751.6175 | 2619140.1866 | 1240754.1441 | 2619153.8534 | 1240765.8758
40 | 2619137.8813 | 1240751.6175 | 2619121.3437 | 1240733.4929 | 2619116.0796 | 1240727.7162
41 | 2619138.7245 | 1240675.1344 | 2619150.9011 | 1240685.1771
42 | 2619173.365 | 1240703.7043 | 2619150.9011 | 1240685.1771
43 | 2619102.7009 | 1240911.8781 | 2619072.4244 | 1240935.6665
44 | 2619123.9685 | 1240827.2264 | 2619139.5441 | 1240832.3265
45 | 2619123.9685 | 1240827.2264 | 2619112.2933 | 1240823.4034
46 | 2618964.5774 | 1240797.9336 | 2618966.8749 | 1240802.7677
47 | 2618952.8026 | 1240896.5005 | 2618939.227 | 1240852.7633
48 | 2618952.8026 | 1240896.5005 | 2618958.9289 | 1240897.4688
49 | 2618952.8026 | 1240896.5005 | 2618936.5994 | 1240889.5464
50 | 2618669.3981 | 1240851.5282 | 2618666.5525 | 1240848.2417
51 | 2618669.3981 | 1240851.5282 | 2618676.4002 | 1240859.6151 | 2618695.7983 | 1240882.0011 | 2618696.0446 | 1240884.434
52 | 2618825.6151 | 1240864.4881 | 2618696.0446 | 1240884.434
53 | 2618825.6151 | 1240864.4881 | 2618833.2066 | 1240880.1564
54 | 2618858.7306 | 1240905.7883 | 2618851.6381 | 1240905.1848 | 2618846.1313 | 1240903.6553 | 2618833.7726 | 1240881.3244 | 2618833.2066 | 1240880.1564
55 | 2618936.5994 | 1240889.5464 | 2618934.4027 | 1240888.6037 | 2618924.4024 | 1240878.3988 | 2618922.9594 | 1240872.9312
56 | 2618912.9967 | 1240835.1801 | 2618922.9594 | 1240872.9312
57 | 2618912.9967 | 1240835.1801 | 2618908.3885 | 1240817.7187
58 | 2618908.3885 | 1240817.7187 | 2618908.0044 | 1240816.2634 | 2618906.3643 | 1240808.9536 | 2618903.8359 | 1240797.7049
59 | 2618968.9546 | 1240899.0533 | 2618958.9289 | 1240897.4688
60 | 2618896.2633 | 1240776.1694 | 2618900.4672 | 1240782.7185 | 2618903.8359 | 1240797.7049
61 | 2618968.9546 | 1240899.0533 | 2619004.6922 | 1240904.7015
62 | 2618896.2633 | 1240776.1694 | 2618894.1024 | 1240772.8032 | 2618876.5035 | 1240750.6001 | 2618868.4444 | 1240747.569
63 | 2619064.6496 | 1240807.8026 | 2619084.2405 | 1240814.2176
64 | 2619063.1021 | 1240792.8989 | 2619055.3975 | 1240779.9116
65 | 2619063.1021 | 1240792.8989 | 2619075.5161 | 1240781.2869 | 2619086.3208 | 1240769.0523
66 | 2619094.7934 | 1240817.6731 | 2619084.2405 | 1240814.2176
67 | 2619041.3144 | 1240756.1726 | 2619055.3975 | 1240779.9116
68 | 2619086.3208 | 1240769.0523 | 2619088.401 | 1240766.6968 | 2619097.3203 | 1240750.1172
69 | 2619112.2933 | 1240823.4034 | 2619094.7934 | 1240817.6731
70 | 2619041.3144 | 1240756.1726 | 2619040.9795 | 1240755.6081
71 | 2618997.3994 | 1240982.3118 | 2619019.0453 | 1240988.0005
72 | 2618973.401 | 1240976.0048 | 2618997.3994 | 1240982.3118
73 | 2619020.7919 | 1240988.4595 | 2619019.0453 | 1240988.0005
74 | 2618973.401 | 1240976.0048 | 2618976.0446 | 1240969.6648 | 2618976.0446 | 1240969.6648
75 | 2619035.7975 | 1240992.4031 | 2619020.7919 | 1240988.4595
76 | 2618976.0446 | 1240969.6648 | 2618982.1028 | 1240964.2029 | 2618986.0953 | 1240961.9251
77 | 2619047.3994 | 1240995.7979 | 2619035.7975 | 1240992.4031
78 | 2619006.0731 | 1240950.5271 | 2618986.0953 | 1240961.9251
79 | 2619047.3994 | 1240995.7979 | 2619050.6177 | 1240996.4894
80 | 2619006.0731 | 1240950.5271 | 2619009.0974 | 1240948.8016 | 2619023.0123 | 1240945.2994 | 2619038.0486 | 1240945.825
81 | 2619072.4244 | 1240935.6665 | 2619065.1844 | 1240941.3551
82 | 2619039.2907 | 1240908.6939 | 2619043.5354 | 1240908.907
83 | 2619039.2907 | 1240908.6939 | 2619025.6038 | 1240908.0066 | 2619025.2488 | 1240907.9505
84 | 2619054.3216 | 1240947.1896 | 2619060.2249 | 1240945.2517 | 2619065.1844 | 1240941.3551
85 | 2618955.4187 | 1240778.6635 | 2618964.5774 | 1240797.9336
86 | 2618954.6105 | 1240776.963 | 2618955.4187 | 1240778.6635
87 | 2618871.8168 | 1240812.6534 | 2618870.7544 | 1240810.321
88 | 2618876.0182 | 1240834.2416 | 2618876.3574 | 1240827.659 | 2618874.775 | 1240821.1944 | 2618873.7003 | 1240816.7882 | 2618871.8168 | 1240812.6534
89 | 2618870.7544 | 1240810.321 | 2618867.183 | 1240802.4808 | 2618862.6019 | 1240788.9808
90 | 2618876.0182 | 1240834.2416 | 2618875.882 | 1240836.8855 | 2618873.1784 | 1240852.8579
91 | 2618862.6019 | 1240788.9808 | 2618862.2467 | 1240787.9339 | 2618859.8779 | 1240784.2419
92 | 2618873.1784 | 1240852.8579 | 2618872.6845 | 1240855.7761 | 2618872.4936 | 1240860.7458
93 | 2618848.5698 | 1240740.0939 | 2618847.4718 | 1240757.3346 | 2618849.073 | 1240767.4015 | 2618859.8779 | 1240784.2419
94 | 2618872.2446 | 1240867.2293 | 2618872.4936 | 1240860.7458
95 | 2618848.5698 | 1240740.0939 | 2618856.7996 | 1240722.1977 | 2618869.415 | 1240700.8563
96 | 2618848.5698 | 1240740.0939 | 2618868.223 | 1240747.4857
97 | 2618848.5698 | 1240740.0939 | 2618834.1659 | 1240733.0635
98 | 2618872.2446 | 1240867.2293 | 2618872.0334 | 1240872.7291 | 2618873.2804 | 1240894.0425
99 | 2618822.2383 | 1240727.2418 | 2618797.8561 | 1240715.3411
100 | 2618822.2383 | 1240727.2418 | 2618834.1659 | 1240733.0635
101 | 2618878.1979 | 1240685.9984 | 2618869.415 | 1240700.8563
102 | 2618868.223 | 1240747.4857 | 2618868.4444 | 1240747.569
103 | 2618878.1979 | 1240685.9984 | 2618865.4594 | 1240673.5147
104 | 2618878.1979 | 1240685.9984 | 2618880.1114 | 1240683.5897
105 | 2618866.0199 | 1240906.4085 | 2618858.7306 | 1240905.7883
106 | 2618866.0199 | 1240906.4085 | 2618870.504 | 1240906.79 | 2618873.7259 | 1240904.0541 | 2618873.5897 | 1240899.3284 | 2618873.2804 | 1240894.0425
107 | 2619040.9795 | 1240755.6081 | 2619024.6363 | 1240728.0594
108 | 2619021.3603 | 1240722.5373 | 2619024.6363 | 1240728.0594
109 | 2619021.3603 | 1240722.5373 | 2619011.5642 | 1240706.0247
110 | 2619011.5642 | 1240706.0247 | 2619000.0899 | 1240686.6831
111 | 2618993.5764 | 1240675.7038 | 2619000.0899 | 1240686.6831
112 | 2619054.3216 | 1240947.1896 | 2619049.0653 | 1240960.0193
113 | 2619054.3216 | 1240947.1896 | 2619038.4187 | 1240945.8379 | 2619038.0486 | 1240945.825
114 | 2618944.0159 | 1240684.0124 | 2618932.456 | 1240664.0281
115 | 2618928.9485 | 1240659.099 | 2618930.9972 | 1240661.5062 | 2618932.456 | 1240664.0281
116 | 2618917.7999 | 1240645.999 | 2618928.9485 | 1240659.099
117 | 2618917.7999 | 1240645.999 | 2618929.5667 | 1240637.0156
118 | 2619009.3847 | 1240905.4432 | 2619004.6922 | 1240904.7015
119 | 2619009.3847 | 1240905.4432 | 2619025.2488 | 1240907.9505
120 | 2618993.5764 | 1240675.7038 | 2618988.431 | 1240667.0305

## bus_geodata
| x | y | coords
0 | 2619092.3893 | 1240693.5163
1 | 2619090.0714 | 1240689.9064
2 | 2619093.2107 | 1240694.7955
3 | 2619077.8144 | 1240670.8174
4 | 2619098.6771 | 1240703.3089
5 | 2619069.1993 | 1240657.4002
6 | 2619104.0016 | 1240711.6013
7 | 2619015.3986 | 1240604.7063
8 | 2619113.8547 | 1240725.2748
9 | 2619127.4802 | 1240689.8778
10 | 2619034.5022 | 1240874.4002
11 | 2619056.1101 | 1240880.6398
12 | 2619006.0103 | 1240860.1695
13 | 2619076.4716 | 1240886.5195
14 | 2618988.7989 | 1240848.8965
15 | 2619102.5937 | 1240894.0627
16 | 2619023.6043 | 1240821.6016
17 | 2618979.2228 | 1240828.7481
18 | 2618983.0866 | 1240856.4508
19 | 2619112.4188 | 1240896.8999
20 | 2619036.6521 | 1240812.0018
21 | 2619000.5209 | 1240781.6961
22 | 2618974.5908 | 1240819.0021
23 | 2618974.2564 | 1240868.1284
24 | 2618986.0006 | 1240756.5938
25 | 2618974.0644 | 1240735.9591
26 | 2618968.7554 | 1240726.7811
27 | 2618957.853 | 1240707.9335
28 | 2619055.4566 | 1240798.1666
29 | 2618948.2892 | 1240691.4001
30 | 2619155.5789 | 1240767.357
31 | 2619153.8534 | 1240765.8758
32 | 2619137.8813 | 1240751.6175
33 | 2619116.0796 | 1240727.7162
34 | 2619138.7245 | 1240675.1344
35 | 2619150.9011 | 1240685.1771
36 | 2619173.365 | 1240703.7043
37 | 2619102.7009 | 1240911.8781
38 | 2619139.5441 | 1240832.3265
39 | 2619123.9685 | 1240827.2264
40 | 2618966.8749 | 1240802.7677
41 | 2618952.8026 | 1240896.5005
42 | 2618666.5525 | 1240848.2417
43 | 2618669.3981 | 1240851.5282
44 | 2618696.0446 | 1240884.434
45 | 2618825.6151 | 1240864.4881
46 | 2618833.2066 | 1240880.1564
47 | 2618922.9594 | 1240872.9312
48 | 2618936.5994 | 1240889.5464
49 | 2618912.9967 | 1240835.1801
50 | 2618908.3885 | 1240817.7187
51 | 2618939.227 | 1240852.7633
52 | 2618958.9289 | 1240897.4688
53 | 2618903.8359 | 1240797.7049
54 | 2618968.9546 | 1240899.0533
55 | 2618896.2633 | 1240776.1694
56 | 2619064.6496 | 1240807.8026
57 | 2619063.1021 | 1240792.8989
58 | 2619084.2405 | 1240814.2176
59 | 2619055.3975 | 1240779.9116
60 | 2619086.3208 | 1240769.0523
61 | 2619094.7934 | 1240817.6731
62 | 2619041.3144 | 1240756.1726
63 | 2619097.3203 | 1240750.1172
64 | 2618997.3994 | 1240982.3118
65 | 2619019.0453 | 1240988.0005
66 | 2618973.401 | 1240976.0048
67 | 2619020.7919 | 1240988.4595
68 | 2618976.0446 | 1240969.6648
69 | 2619035.7975 | 1240992.4031
70 | 2618986.0953 | 1240961.9251
71 | 2619047.3994 | 1240995.7979
72 | 2619006.0731 | 1240950.5271
73 | 2619072.4244 | 1240935.6665
74 | 2619043.5354 | 1240908.907
75 | 2619039.2907 | 1240908.6939
76 | 2619065.1844 | 1240941.3551
77 | 2619050.6177 | 1240996.4894
78 | 2618964.5774 | 1240797.9336
79 | 2618955.4187 | 1240778.6635
80 | 2618871.8168 | 1240812.6534
81 | 2618870.7544 | 1240810.321
82 | 2618876.0182 | 1240834.2416
83 | 2618862.6019 | 1240788.9808
84 | 2618873.1784 | 1240852.8579
85 | 2618859.8779 | 1240784.2419
86 | 2618872.4936 | 1240860.7458
87 | 2618848.5698 | 1240740.0939
88 | 2618872.2446 | 1240867.2293
89 | 2618822.2383 | 1240727.2418
90 | 2618797.8561 | 1240715.3411
91 | 2618834.1659 | 1240733.0635
92 | 2618869.415 | 1240700.8563
93 | 2618868.223 | 1240747.4857
94 | 2618878.1979 | 1240685.9984
95 | 2618868.4444 | 1240747.569
96 | 2618866.0199 | 1240906.4085
97 | 2618858.7306 | 1240905.7883
98 | 2618873.2804 | 1240894.0426
99 | 2619040.9795 | 1240755.6081
100 | 2619024.6363 | 1240728.0594
101 | 2619021.3603 | 1240722.5373
102 | 2619011.5642 | 1240706.0247
103 | 2619000.0899 | 1240686.6831
104 | 2619049.0653 | 1240960.0193
105 | 2619054.3216 | 1240947.1896
106 | 2619038.0486 | 1240945.825
107 | 2619112.2933 | 1240823.4034
108 | 2618944.0159 | 1240684.0124
109 | 2618932.456 | 1240664.0281
110 | 2618928.9485 | 1240659.099
111 | 2618917.7999 | 1240645.999
112 | 2618929.5667 | 1240637.0156
113 | 2619004.6922 | 1240904.7015
114 | 2619009.3847 | 1240905.4432
115 | 2619025.2488 | 1240907.9505
116 | 2618993.5764 | 1240675.7038
117 | 2618988.431 | 1240667.0305
118 | 2619045.3982 | 1240662.0047
119 | 2618954.6105 | 1240776.963
120 | 2618865.4594 | 1240673.5147
121 | 2618880.1114 | 1240683.5897
122 | 2619023.6043 | 1240821.6016

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98452 | -0.1085 | 0.0015207 | 0.00038112
1 | 0.98449 | -0.10873 | 0.0015205 | 0.00038107
2 | 0.98453 | -0.1084 | 0.0013884 | 0.00034795
3 | 0.98437 | -0.10955 | 0.0021791 | 0.00054615
4 | 0.98465 | -0.10757 | 0.0010714 | 0.00026851
5 | 0.98434 | -0.10977 | 0 | 0
6 | 0.98478 | -0.10666 | 0 | 0
7 | 0.98416 | -0.11111 | 0 | 0
8 | 0.98522 | -0.10352 | 0 | 0
9 | 0.98435 | -0.10972 | 0.0037897 | 0.00094979
10 | 0.98738 | -0.088016 | 0.0013296 | 0.00033323
11 | 0.98651 | -0.094173 | 0.0020965 | 0.00052544
12 | 0.98868 | -0.078784 | 0.002397 | 0.00060075
13 | 0.98575 | -0.099529 | 0.0036894 | 0.00092465
14 | 0.98959 | -0.072393 | 0 | 0
15 | 0.98493 | -0.10538 | 0.0024572 | 0.00061584
16 | 0.99353 | -0.044847 | 0 | 0
17 | 0.98921 | -0.075091 | 0.0032489 | 0.00081426
18 | 0.98904 | -0.076285 | 0.002106 | 0.00052783
19 | 0.98465 | -0.10732 | 0 | 0
20 | 0.99188 | -0.056454 | 0.0023031 | 0.00057721
21 | 1 | 0 | -0.22137 | -0.055696
22 | 0.98908 | -0.076039 | 0.001715 | 0.00042983
23 | 0.9882 | -0.082152 | 0.0022112 | 0.00055417
24 | 0.99901 | -0.0068905 | 0.0015585 | 0.0003906
25 | 0.99826 | -0.012192 | 0.0018017 | 0.00045156
26 | 0.99795 | -0.014361 | 0.002973 | 0.0007451
27 | 0.99741 | -0.01817 | 0.0017448 | 0.00043729
28 | 0.98957 | -0.072703 | 0 | 0
29 | 0.99698 | -0.021179 | 0.0013305 | 0.00033345
30 | 0.98468 | -0.10736 | 0.0018436 | 0.00046204
31 | 0.98469 | -0.10732 | 0.0031083 | 0.00077902
32 | 0.98484 | -0.10623 | 0.0021731 | 0.00054463
33 | 0.98517 | -0.10385 | 0.0026421 | 0.00066216
34 | 0.98421 | -0.11073 | 0 | 0
35 | 0.98409 | -0.11158 | 0.0027566 | 0.00069087
36 | 0.98398 | -0.11233 | 0.0025008 | 0.00062676
37 | 0.98417 | -0.11072 | 0 | 0
38 | 0.98814 | -0.082852 | 0.0029969 | 0.00075108
39 | 0.98821 | -0.08235 | 0.002769 | 0.00069398
40 | 0.9889 | -0.077305 | 0.0017909 | 0.00044883
41 | 0.98622 | -0.096043 | 0 | 0
42 | 0.97067 | -0.20697 | 0.00064336 | 0.00016124
43 | 0.97068 | -0.20695 | 0.00080822 | 0.00020256
44 | 0.97077 | -0.20629 | 0.00055656 | 0.00013949
45 | 0.97115 | -0.20349 | 0.001116 | 0.00027969
46 | 0.97123 | -0.20291 | 0.0011349 | 0.00028444
47 | 0.98451 | -0.10812 | 0.0027163 | 0.00068078
48 | 0.98546 | -0.10144 | 0.0014688 | 0.00036811
49 | 0.98293 | -0.11927 | 0.0019376 | 0.00048561
50 | 0.98223 | -0.12426 | 0.0010295 | 0.00025802
51 | 0.98604 | -0.09734 | 0.0027582 | 0.00069127
52 | 0.9861 | -0.096928 | 0.0021658 | 0.00054279
53 | 0.98065 | -0.13542 | 0.0022413 | 0.00056171
54 | 0.98593 | -0.098151 | 0.0013938 | 0.00034932
55 | 0.97895 | -0.14749 | 0.0020222 | 0.00050682
56 | 0.9892 | -0.075324 | 0.0029812 | 0.00074715
57 | 0.98891 | -0.077366 | 0 | 0
58 | 0.98872 | -0.078714 | 0.0048982 | 0.0012276
59 | 0.98853 | -0.080082 | 0.001741 | 0.00043634
60 | 0.98738 | -0.088174 | 0.0017628 | 0.00044179
61 | 0.98854 | -0.079985 | 0.0024902 | 0.00062412
62 | 0.9879 | -0.084559 | 0.0023401 | 0.00058648
63 | 0.98643 | -0.09492 | 0.0020992 | 0.00052611
64 | 0.98077 | -0.13497 | 0.0011898 | 0.00029819
65 | 0.98057 | -0.1364 | 0.002022 | 0.00050677
66 | 0.98103 | -0.13308 | 0 | 0
67 | 0.98056 | -0.13648 | 0.0029362 | 0.00073589
68 | 0.98111 | -0.13256 | 0.0028337 | 0.00071019
69 | 0.98053 | -0.13667 | 0 | 0
70 | 0.9813 | -0.13121 | 0.00097149 | 0.00024348
71 | 0.98051 | -0.13682 | 0 | 0
72 | 0.98167 | -0.12855 | 0.0020852 | 0.00052259
73 | 0.98314 | -0.11805 | 0.0018617 | 0.00046658
74 | 0.98509 | -0.10412 | 0.0017289 | 0.0004333
75 | 0.9851 | -0.10405 | 0.0025137 | 0.00063
76 | 0.98292 | -0.11963 | 0.0010492 | 0.00026294
77 | 0.9805 | -0.13686 | 0.0011939 | 0.00029922
78 | 0.98886 | -0.077583 | 0.0019442 | 0.00048725
79 | 0.98876 | -0.078272 | 0.0017824 | 0.00044671
80 | 0.97283 | -0.19141 | 0.0006127 | 0.00015356
81 | 0.97287 | -0.1911 | 0.00054977 | 0.00013779
82 | 0.97247 | -0.19396 | 0.00052386 | 0.00013129
83 | 0.97327 | -0.1882 | 0.0032751 | 0.00082083
84 | 0.97219 | -0.19602 | 0.0012247 | 0.00030695
85 | 0.97339 | -0.18731 | 0.0059993 | 0.0015036
86 | 0.97208 | -0.19678 | 0.00097504 | 0.00024437
87 | 0.97487 | -0.17667 | 0 | 0
88 | 0.972 | -0.19734 | 0.00065033 | 0.00016299
89 | 0.97464 | -0.17834 | 0.0025047 | 0.00062773
90 | 0.97461 | -0.17854 | 0.00071607 | 0.00017946
91 | 0.97471 | -0.17789 | 0.0040045 | 0.0010036
92 | 0.97423 | -0.18131 | 0.002214 | 0.00055487
93 | 0.97606 | -0.1682 | 0.0062971 | 0.0015782
94 | 0.97403 | -0.18271 | 0 | 0
95 | 0.97607 | -0.16809 | 0.0034003 | 0.0008522
96 | 0.97154 | -0.20072 | 0.0012406 | 0.00031093
97 | 0.97148 | -0.20111 | 0.0007978 | 0.00019995
98 | 0.97171 | -0.19947 | 0.001162 | 0.00029122
99 | 0.98788 | -0.08465 | 0.0019255 | 0.00048257
100 | 0.98735 | -0.088453 | 0.0014569 | 0.00036514
101 | 0.98725 | -0.089119 | 0.0021097 | 0.00052873
102 | 0.98703 | -0.090699 | 0.0010216 | 0.00025603
103 | 0.9868 | -0.092314 | 0.0022183 | 0.00055596
104 | 0.98261 | -0.12183 | 0.0013108 | 0.00032852
105 | 0.98264 | -0.12164 | 0 | 0
106 | 0.9823 | -0.12405 | 0.00099142 | 0.00024847
107 | 0.98831 | -0.081626 | 0.0029528 | 0.00074005
108 | 0.9968 | -0.022411 | 0.0038241 | 0.00095842
109 | 0.99645 | -0.024856 | 0.0024457 | 0.00061295
110 | 0.99638 | -0.02535 | 0.0050732 | 0.0012715
111 | 0.99631 | -0.025872 | 0 | 0
112 | 0.99624 | -0.026322 | 0.0030173 | 0.00075621
113 | 0.98539 | -0.10199 | 0.001876 | 0.00047017
114 | 0.98533 | -0.10241 | 0.0022462 | 0.00056294
115 | 0.98518 | -0.10343 | 0.0019674 | 0.00049307
116 | 0.98671 | -0.092941 | 0.0022892 | 0.00057372
117 | 0.98668 | -0.093199 | 0.0024984 | 0.00062617
118 | 0.98403 | -0.112 | 0.0013329 | 0.00033405
119 | 0.98876 | -0.078298 | 0.0013762 | 0.00034492
120 | 0.97395 | -0.18335 | 0.0034303 | 0.00085971
121 | 0.97402 | -0.18285 | 0.0042726 | 0.0010708
122 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0050335 | 0.0012591 | -0.0050334 | -0.0012591 | 1.549e-07 | 5.0262e-09 | 0.0076069 | 0.0076069 | 0.0076069 | 0.98452 | -0.1085 | 0.98449 | -0.10873 | 2.8174
1 | -0.0065542 | -0.0016402 | 0.0065543 | 0.0016402 | 9.3065e-08 | 1.6464e-08 | 0.0099053 | 0.0099053 | 0.0099053 | 0.98452 | -0.1085 | 0.98453 | -0.1084 | 3.6686
2 | 0.0035129 | 0.00087799 | -0.0035125 | -0.00087812 | 3.9895e-07 | -1.3498e-07 | 0.0053087 | 0.0053088 | 0.0053088 | 0.98449 | -0.10873 | 0.98437 | -0.10955 | 1.9662
3 | -0.0079427 | -0.0019882 | 0.0079436 | 0.0019884 | 9.0965e-07 | 2.2119e-07 | 0.012004 | 0.012004 | 0.012004 | 0.98453 | -0.1084 | 0.98465 | -0.10757 | 4.4458
4 | 0.0013333 | 0.00033197 | -0.0013333 | -0.00033216 | 4.0388e-08 | -1.8716e-07 | 0.0020147 | 0.0020148 | 0.0020148 | 0.98437 | -0.10955 | 0.98434 | -0.10977 | 0.74622
5 | -0.0090149 | -0.0022569 | 0.0090161 | 0.0022572 | 1.1412e-06 | 3.1354e-07 | 0.013623 | 0.013623 | 0.013623 | 0.98465 | -0.10757 | 0.98478 | -0.10666 | 5.0454
6 | 0.0013333 | 0.00033216 | -0.001333 | -0.00033329 | 2.4407e-07 | -1.1304e-06 | 0.0020148 | 0.0020152 | 0.0020152 | 0.98434 | -0.10977 | 0.98416 | -0.11111 | 0.74638
7 | -0.018069 | -0.0045255 | 0.018077 | 0.0045283 | 7.8312e-06 | 2.7977e-06 | 0.027301 | 0.027301 | 0.027301 | 0.98478 | -0.10666 | 0.98522 | -0.10352 | 10.1115
8 | 0.0090526 | 0.0022683 | -0.0090488 | -0.0022672 | 3.8394e-06 | 1.0585e-06 | 0.013678 | 0.013679 | 0.013679 | 0.98478 | -0.10666 | 0.98435 | -0.10972 | 5.0661
9 | 0.001333 | 0.00033329 | -0.0013329 | -0.00033405 | 1.6384e-07 | -7.5828e-07 | 0.0020152 | 0.0020155 | 0.0020155 | 0.98416 | -0.11111 | 0.98403 | -0.112 | 0.74649
10 | -0.027847 | -0.0069768 | 0.02788 | 0.0069891 | 3.3178e-05 | 1.2378e-05 | 0.042058 | 0.042058 | 0.042058 | 0.98522 | -0.10352 | 0.98643 | -0.09492 | 15.5769
11 | 0.0097706 | 0.0024485 | -0.0097702 | -0.0024483 | 4.4884e-07 | 1.3057e-07 | 0.014757 | 0.014757 | 0.014757 | 0.98522 | -0.10352 | 0.98517 | -0.10385 | 5.4655
12 | 0.005259 | 0.0013174 | -0.0052583 | -0.0013174 | 7.3123e-07 | 4.5572e-08 | 0.0079498 | 0.0079498 | 0.0079498 | 0.98435 | -0.10972 | 0.98421 | -0.11073 | 2.9444
13 | 0.02681 | 0.0067312 | -0.026787 | -0.0067226 | 2.2915e-05 | 8.5262e-06 | 0.040408 | 0.040408 | 0.040408 | 0.98738 | -0.088016 | 0.98651 | -0.094173 | 14.966
14 | -0.02814 | -0.0070644 | 0.028176 | 0.0070779 | 3.613e-05 | 1.3484e-05 | 0.042412 | 0.042412 | 0.042412 | 0.98738 | -0.088016 | 0.98868 | -0.078784 | 15.7081
15 | 0.024691 | 0.0061972 | -0.024672 | -0.0061904 | 1.8346e-05 | 6.7858e-06 | 0.037246 | 0.037246 | 0.037246 | 0.98651 | -0.094173 | 0.98575 | -0.099529 | 13.7948
16 | -0.030573 | -0.0076786 | 0.0306 | 0.0076888 | 2.7189e-05 | 1.0193e-05 | 0.046019 | 0.046019 | 0.046019 | 0.98868 | -0.078784 | 0.98959 | -0.072393 | 17.0442
17 | 0.020983 | 0.0052658 | -0.020966 | -0.0052596 | 1.7024e-05 | 6.2014e-06 | 0.031677 | 0.031677 | 0.031677 | 0.98575 | -0.099529 | 0.98493 | -0.10538 | 11.7322
18 | -0.12386 | -0.031171 | 0.12434 | 0.031353 | 0.00047811 | 0.00018275 | 0.1863 | 0.1863 | 0.1863 | 0.98959 | -0.072393 | 0.99353 | -0.044847 | 34.4994
19 | 0.011865 | 0.0029736 | -0.01186 | -0.0029722 | 4.4308e-06 | 1.4177e-06 | 0.017841 | 0.017841 | 0.017841 | 0.98959 | -0.072393 | 0.98921 | -0.075091 | 6.6078
20 | 0.0814 | 0.020508 | -0.081356 | -0.020491 | 4.4296e-05 | 1.6794e-05 | 0.12244 | 0.12244 | 0.12244 | 0.98959 | -0.072393 | 0.98904 | -0.076285 | 22.6735
21 | 0.018509 | 0.0046437 | -0.018504 | -0.0046419 | 4.9903e-06 | 1.7892e-06 | 0.027964 | 0.027964 | 0.027964 | 0.98493 | -0.10538 | 0.98465 | -0.10732 | 10.3572
22 | 0.071159 | 0.017888 | -0.071044 | -0.017844 | 0.00011485 | 4.3963e-05 | 0.10659 | 0.10659 | 0.10659 | 0.99353 | -0.044847 | 0.99188 | -0.056454 | 39.4791
23 | -0.1955 | -0.049242 | 0.19674 | 0.049715 | 0.0012339 | 0.00047337 | 0.29289 | 0.29289 | 0.29289 | 0.99353 | -0.044847 | 1 | 0 | 54.2389
24 | 0.0086115 | 0.0021579 | -0.0086104 | -0.0021576 | 1.1299e-06 | 2.9606e-07 | 0.012954 | 0.012954 | 0.012954 | 0.98921 | -0.075091 | 0.98908 | -0.076039 | 4.7977
25 | 0.07925 | 0.019964 | -0.079185 | -0.019939 | 6.4976e-05 | 2.4615e-05 | 0.11927 | 0.11927 | 0.11927 | 0.98904 | -0.076285 | 0.9882 | -0.082152 | 22.0867
26 | 0.018504 | 0.0046419 | -0.018495 | -0.0046388 | 8.706e-06 | 3.1216e-06 | 0.027964 | 0.027965 | 0.027965 | 0.98465 | -0.10732 | 0.98417 | -0.11072 | 10.3572
27 | 0.068741 | 0.017267 | -0.068586 | -0.017208 | 0.00015497 | 5.9302e-05 | 0.10314 | 0.10314 | 0.10314 | 0.99188 | -0.056454 | 0.98957 | -0.072703 | 38.1995
28 | 0.023837 | 0.0059809 | -0.023814 | -0.0059725 | 2.2769e-05 | 8.3773e-06 | 0.035472 | 0.035472 | 0.035472 | 1 | 0 | 0.99901 | -0.0068905 | 13.1378
29 | 0.0068954 | 0.0017278 | -0.0068942 | -0.0017275 | 1.207e-06 | 2.3358e-07 | 0.010374 | 0.010374 | 0.010374 | 0.98908 | -0.076039 | 0.9889 | -0.077305 | 3.8421
30 | 0.076974 | 0.019385 | -0.076824 | -0.019328 | 0.00014918 | 5.6466e-05 | 0.11594 | 0.11594 | 0.11594 | 0.9882 | -0.082152 | 0.98622 | -0.096043 | 21.4702
31 | 0.022256 | 0.0055819 | -0.022239 | -0.005576 | 1.6347e-05 | 5.9756e-06 | 0.033151 | 0.033151 | 0.033151 | 0.99901 | -0.0068905 | 0.99826 | -0.012192 | 12.2781
32 | 0.020437 | 0.0051244 | -0.020431 | -0.0051222 | 6.1407e-06 | 2.2232e-06 | 0.030465 | 0.030465 | 0.030465 | 0.99826 | -0.012192 | 0.99795 | -0.014361 | 11.2834
33 | 0.017458 | 0.0043771 | -0.017449 | -0.0043738 | 9.2075e-06 | 3.257e-06 | 0.026032 | 0.026032 | 0.026032 | 0.99795 | -0.014361 | 0.99741 | -0.01817 | 9.6416
34 | 0.015704 | 0.0039365 | -0.015698 | -0.0039343 | 6.5425e-06 | 2.2672e-06 | 0.023429 | 0.023429 | 0.023429 | 0.99741 | -0.01817 | 0.99698 | -0.021179 | 8.6775
35 | 0.019108 | 0.0047902 | -0.019101 | -0.0047877 | 6.9351e-06 | 2.4945e-06 | 0.028732 | 0.028733 | 0.028733 | 0.98957 | -0.072703 | 0.9892 | -0.075324 | 10.6417
36 | 0.049478 | 0.012417 | -0.049446 | -0.012405 | 3.2011e-05 | 1.2193e-05 | 0.074406 | 0.074406 | 0.074406 | 0.98957 | -0.072703 | 0.98891 | -0.077366 | 27.5579
37 | 0.014367 | 0.0036008 | -0.014365 | -0.0036 | 2.4488e-06 | 8.3059e-07 | 0.021444 | 0.021444 | 0.021444 | 0.99698 | -0.021179 | 0.9968 | -0.022411 | 7.9421
38 | -0.0018436 | -0.00046204 | 0.0018436 | 0.00046202 | 1.1014e-08 | -2.4691e-08 | 0.002786 | 0.0027859 | 0.002786 | 0.98468 | -0.10736 | 0.98469 | -0.10732 | 1.0318
39 | -0.0049519 | -0.001241 | 0.0049527 | 0.0012411 | 7.4886e-07 | 1.5357e-08 | 0.0074831 | 0.007483 | 0.0074831 | 0.98469 | -0.10732 | 0.98484 | -0.10623 | 2.7715
40 | -0.0071258 | -0.0017857 | 0.0071281 | 0.0017862 | 2.34e-06 | 4.8819e-07 | 0.010766 | 0.010766 | 0.010766 | 0.98484 | -0.10623 | 0.98517 | -0.10385 | 3.9876
41 | 0.0052583 | 0.0013174 | -0.0052577 | -0.0013174 | 6.2246e-07 | 3.8851e-08 | 0.0079498 | 0.0079499 | 0.0079499 | 0.98421 | -0.11073 | 0.98409 | -0.11158 | 2.9444
42 | 0.0025011 | 0.00062649 | -0.0025008 | -0.00062676 | 2.5986e-07 | -2.6997e-07 | 0.0037817 | 0.0037818 | 0.0037818 | 0.98409 | -0.11158 | 0.98398 | -0.11233 | 1.4007
43 | 0.018495 | 0.0046388 | -0.018476 | -0.0046321 | 1.8789e-05 | 6.7378e-06 | 0.027965 | 0.027965 | 0.027965 | 0.98417 | -0.11072 | 0.98314 | -0.11805 | 10.3573
44 | -0.0029969 | -0.00075108 | 0.0029971 | 0.00075095 | 2.0828e-07 | -1.2985e-07 | 0.0045129 | 0.0045128 | 0.0045129 | 0.98814 | -0.082852 | 0.98821 | -0.08235 | 1.6714
45 | -0.0057661 | -0.0014449 | 0.0057667 | 0.001445 | 5.7788e-07 | 6.485e-08 | 0.0086823 | 0.0086823 | 0.0086823 | 0.98821 | -0.08235 | 0.98831 | -0.081626 | 3.2157
46 | 0.0051033 | 0.0012787 | -0.0051031 | -0.0012787 | 1.9694e-07 | 7.0803e-09 | 0.007679 | 0.007679 | 0.007679 | 0.9889 | -0.077305 | 0.98886 | -0.077583 | 2.8441
47 | 0.0027587 | 0.00069087 | -0.0027582 | -0.00069127 | 4.9499e-07 | -3.9379e-07 | 0.0041621 | 0.0041623 | 0.0041623 | 0.98622 | -0.096043 | 0.98604 | -0.09734 | 1.5416
48 | 0.013903 | 0.0034846 | -0.013901 | -0.0034841 | 1.703e-06 | 5.7586e-07 | 0.020976 | 0.020976 | 0.020976 | 0.98622 | -0.096043 | 0.9861 | -0.096928 | 7.7691
49 | 0.060163 | 0.015153 | -0.060118 | -0.015136 | 4.5357e-05 | 1.6995e-05 | 0.090801 | 0.090801 | 0.090801 | 0.98622 | -0.096043 | 0.98546 | -0.10144 | 16.8149
50 | -0.00064336 | -0.00016124 | 0.00064336 | 0.00016119 | 2.6385e-09 | -5.2721e-08 | 0.00098625 | 0.00098623 | 0.00098625 | 0.97067 | -0.20697 | 0.97068 | -0.20695 | 0.36528
51 | -0.0014516 | -0.00036375 | 0.0014517 | 0.00036327 | 1.3212e-07 | -4.7784e-07 | 0.0022252 | 0.002225 | 0.0022252 | 0.97068 | -0.20695 | 0.97077 | -0.20629 | 0.82415
52 | -0.0020083 | -0.00050276 | 0.002009 | 0.00050143 | 7.7493e-07 | -1.3234e-06 | 0.0030781 | 0.0030775 | 0.0030781 | 0.97077 | -0.20629 | 0.97115 | -0.20349 | 1.14
53 | -0.003125 | -0.00078112 | 0.0031253 | 0.000781 | 2.49e-07 | -1.1968e-07 | 0.0047874 | 0.0047873 | 0.0047874 | 0.97115 | -0.20349 | 0.97123 | -0.20291 | 1.7731
54 | -0.0042602 | -0.0010654 | 0.0042612 | 0.0010654 | 1.0538e-06 | -8.5534e-08 | 0.0065262 | 0.006526 | 0.0065262 | 0.97123 | -0.20291 | 0.97148 | -0.20111 | 2.4171
55 | -0.058594 | -0.014747 | 0.058649 | 0.014768 | 5.4677e-05 | 2.0461e-05 | 0.088583 | 0.088583 | 0.088583 | 0.98451 | -0.10812 | 0.98546 | -0.10144 | 16.4043
56 | 0.055878 | 0.014067 | -0.055791 | -0.014034 | 8.6934e-05 | 3.2445e-05 | 0.084478 | 0.084478 | 0.084478 | 0.98451 | -0.10812 | 0.98293 | -0.11927 | 15.6441
57 | 0.053853 | 0.013549 | -0.053816 | -0.013535 | 3.7467e-05 | 1.3953e-05 | 0.081545 | 0.081545 | 0.081545 | 0.98293 | -0.11927 | 0.98223 | -0.12426 | 15.1009
58 | 0.052786 | 0.013277 | -0.052704 | -0.013245 | 8.1942e-05 | 3.1257e-05 | 0.079985 | 0.079985 | 0.079985 | 0.98223 | -0.12426 | 0.98065 | -0.13542 | 29.6241
59 | 0.011735 | 0.0029413 | -0.011733 | -0.0029406 | 1.9861e-06 | 6.3444e-07 | 0.017708 | 0.017708 | 0.017708 | 0.9861 | -0.096928 | 0.98593 | -0.098151 | 6.5587
60 | 0.050463 | 0.012684 | -0.050378 | -0.012651 | 8.4699e-05 | 3.2285e-05 | 0.076584 | 0.076584 | 0.076584 | 0.98065 | -0.13542 | 0.97895 | -0.14749 | 28.3646
61 | 0.010339 | 0.0025913 | -0.010334 | -0.0025897 | 5.4978e-06 | 1.6534e-06 | 0.015605 | 0.015605 | 0.015605 | 0.98593 | -0.098151 | 0.98539 | -0.10199 | 5.7796
62 | 0.048356 | 0.012144 | -0.048218 | -0.012092 | 0.00013806 | 5.2586e-05 | 0.073511 | 0.073511 | 0.073511 | 0.97895 | -0.14749 | 0.97607 | -0.16809 | 27.2262
63 | 0.016119 | 0.0040406 | -0.016112 | -0.0040379 | 7.5633e-06 | 2.6445e-06 | 0.024248 | 0.024248 | 0.024248 | 0.9892 | -0.075324 | 0.98872 | -0.078714 | 8.9808
64 | 0.017628 | 0.0044198 | -0.017622 | -0.0044175 | 6.6301e-06 | 2.3564e-06 | 0.026526 | 0.026526 | 0.026526 | 0.98891 | -0.077366 | 0.98853 | -0.080082 | 9.8244
65 | 0.031818 | 0.0079855 | -0.03177 | -0.0079675 | 4.7667e-05 | 1.7907e-05 | 0.04788 | 0.047881 | 0.047881 | 0.98891 | -0.077366 | 0.98738 | -0.088174 | 17.7336
66 | 0.011214 | 0.0028103 | -0.011212 | -0.0028097 | 1.9735e-06 | 6.1665e-07 | 0.016876 | 0.016876 | 0.016876 | 0.98872 | -0.078714 | 0.98854 | -0.079985 | 6.2505
67 | 0.015881 | 0.0039812 | -0.015871 | -0.0039777 | 9.8426e-06 | 3.432e-06 | 0.023905 | 0.023905 | 0.023905 | 0.98853 | -0.080082 | 0.9879 | -0.084559 | 8.8538
68 | 0.030008 | 0.0075258 | -0.02998 | -0.0075153 | 2.8037e-05 | 1.0503e-05 | 0.045224 | 0.045224 | 0.045224 | 0.98738 | -0.088174 | 0.98643 | -0.09492 | 16.7497
69 | 0.0087215 | 0.0021856 | -0.0087195 | -0.002185 | 1.9803e-06 | 5.2564e-07 | 0.013128 | 0.013128 | 0.013128 | 0.98854 | -0.079985 | 0.98831 | -0.081626 | 4.8623
70 | 0.013531 | 0.0033912 | -0.01353 | -0.0033912 | 1.7011e-07 | 5.7025e-08 | 0.02038 | 0.02038 | 0.02038 | 0.9879 | -0.084559 | 0.98788 | -0.08465 | 7.5483
71 | 0.0061535 | 0.0015417 | -0.0061523 | -0.0015415 | 1.2172e-06 | 1.8579e-07 | 0.0093359 | 0.009336 | 0.009336 | 0.98077 | -0.13497 | 0.98057 | -0.1364 | 3.4578
72 | -0.0073433 | -0.0018399 | 0.0073452 | 0.0018403 | 1.9218e-06 | 4.2594e-07 | 0.011141 | 0.011141 | 0.011141 | 0.98077 | -0.13497 | 0.98103 | -0.13308 | 4.1263
73 | 0.0041303 | 0.0010347 | -0.0041302 | -0.0010347 | 4.4265e-08 | -5.7545e-09 | 0.0062675 | 0.0062675 | 0.0062675 | 0.98057 | -0.1364 | 0.98056 | -0.13648 | 2.3213
74 | -0.0073452 | -0.0018403 | 0.0073457 | 0.0018404 | 5.3201e-07 | 1.1788e-07 | 0.011141 | 0.011141 | 0.011141 | 0.98103 | -0.13308 | 0.98111 | -0.13256 | 4.1262
75 | 0.001194 | 0.00029886 | -0.001194 | -0.00029904 | 3.178e-08 | -1.8348e-07 | 0.0018118 | 0.0018118 | 0.0018118 | 0.98056 | -0.13648 | 0.98053 | -0.13667 | 0.67105
76 | -0.010179 | -0.0025506 | 0.010181 | 0.0025512 | 1.8968e-06 | 5.6846e-07 | 0.015439 | 0.015439 | 0.015439 | 0.98111 | -0.13256 | 0.9813 | -0.13121 | 5.718
77 | 0.001194 | 0.00029904 | -0.0011939 | -0.00029919 | 2.4696e-08 | -1.4257e-07 | 0.0018118 | 0.0018119 | 0.0018119 | 0.98053 | -0.13667 | 0.98051 | -0.13682 | 0.67107
78 | -0.011153 | -0.0027947 | 0.011157 | 0.0027959 | 4.1048e-06 | 1.2881e-06 | 0.016912 | 0.016912 | 0.016912 | 0.9813 | -0.13121 | 0.98167 | -0.12855 | 6.2636
79 | 0.0011939 | 0.00029919 | -0.0011939 | -0.00029922 | 6.7434e-09 | -3.8925e-08 | 0.0018119 | 0.0018119 | 0.0018119 | 0.98051 | -0.13682 | 0.9805 | -0.13686 | 0.67107
80 | -0.013242 | -0.0033185 | 0.01325 | 0.0033213 | 8.2653e-06 | 2.763e-06 | 0.020072 | 0.020072 | 0.020072 | 0.98167 | -0.12855 | 0.9823 | -0.12405 | 7.4342
81 | 0.016614 | 0.0041655 | -0.016611 | -0.0041642 | 3.6333e-06 | 1.2807e-06 | 0.025147 | 0.025147 | 0.025147 | 0.98314 | -0.11805 | 0.98292 | -0.11963 | 9.3137
82 | -0.0017289 | -0.0004333 | 0.0017289 | 0.00043326 | 1.8087e-08 | -4.715e-08 | 0.0026116 | 0.0026116 | 0.0026116 | 0.98509 | -0.10412 | 0.9851 | -0.10405 | 0.96725
83 | -0.0042427 | -0.0010633 | 0.004243 | 0.0010632 | 3.6042e-07 | -4.044e-08 | 0.0064086 | 0.0064086 | 0.0064086 | 0.9851 | -0.10405 | 0.98518 | -0.10343 | 2.3736
84 | 0.015562 | 0.0039013 | -0.015557 | -0.0038998 | 4.3362e-06 | 1.5091e-06 | 0.023559 | 0.023559 | 0.023559 | 0.98292 | -0.11963 | 0.98264 | -0.12164 | 8.7255
85 | 0.003159 | 0.00079145 | -0.0031587 | -0.00079161 | 3.0083e-07 | -1.5798e-07 | 0.0047534 | 0.0047535 | 0.0047535 | 0.98886 | -0.077583 | 0.98876 | -0.078272 | 1.7606
86 | 0.0013763 | 0.0003449 | -0.0013762 | -0.00034492 | 5.0396e-09 | -2.221e-08 | 0.0020712 | 0.0020712 | 0.0020712 | 0.98876 | -0.078272 | 0.98876 | -0.078298 | 0.7671
87 | -0.01146 | -0.0028698 | 0.011461 | 0.00287 | 4.9138e-07 | 1.5717e-07 | 0.017528 | 0.017528 | 0.017528 | 0.97283 | -0.19141 | 0.97287 | -0.1911 | 6.492
88 | 0.010848 | 0.0027163 | -0.010844 | -0.0027151 | 3.8349e-06 | 1.1979e-06 | 0.016591 | 0.016591 | 0.016591 | 0.97283 | -0.19141 | 0.97247 | -0.19396 | 6.145
89 | -0.01201 | -0.0030078 | 0.012015 | 0.0030094 | 4.8157e-06 | 1.5681e-06 | 0.018369 | 0.018369 | 0.018369 | 0.97287 | -0.1911 | 0.97327 | -0.1882 | 6.8035
90 | 0.01032 | 0.0025838 | -0.010317 | -0.0025829 | 2.9321e-06 | 8.9398e-07 | 0.01579 | 0.01579 | 0.01579 | 0.97247 | -0.19396 | 0.97219 | -0.19602 | 5.8481
91 | -0.01529 | -0.0038302 | 0.015292 | 0.0038308 | 1.8728e-06 | 6.5203e-07 | 0.023377 | 0.023377 | 0.023377 | 0.97327 | -0.1882 | 0.97339 | -0.18731 | 8.658
92 | 0.0090922 | 0.0022759 | -0.0090912 | -0.0022757 | 9.5855e-07 | 2.7032e-07 | 0.013915 | 0.013915 | 0.013915 | 0.97219 | -0.19602 | 0.97208 | -0.19678 | 5.1538
93 | -0.021292 | -0.0053344 | 0.021323 | 0.0053459 | 3.1384e-05 | 1.148e-05 | 0.032548 | 0.032547 | 0.032548 | 0.97339 | -0.18731 | 0.97487 | -0.17667 | 12.0547
94 | 0.0081162 | 0.0020313 | -0.0081155 | -0.0020311 | 6.2482e-07 | 1.5989e-07 | 0.012423 | 0.012423 | 0.012423 | 0.97208 | -0.19678 | 0.972 | -0.19734 | 4.6011
95 | 0.0099251 | 0.0024875 | -0.0099187 | -0.0024856 | 6.3713e-06 | 1.8962e-06 | 0.015149 | 0.01515 | 0.01515 | 0.97487 | -0.17667 | 0.97423 | -0.18131 | 5.6109
96 | -0.038475 | -0.0096441 | 0.03852 | 0.0096612 | 4.5188e-05 | 1.7118e-05 | 0.058727 | 0.058727 | 0.058727 | 0.97487 | -0.17667 | 0.97606 | -0.1682 | 21.7508
97 | 0.0072267 | 0.0018107 | -0.0072255 | -0.0018104 | 1.2169e-06 | 2.6823e-07 | 0.01103 | 0.01103 | 0.01103 | 0.97487 | -0.17667 | 0.97471 | -0.17789 | 4.0854
98 | 0.0074652 | 0.0018682 | -0.007463 | -0.0018677 | 2.1882e-06 | 5.0885e-07 | 0.011427 | 0.011427 | 0.011427 | 0.972 | -0.19734 | 0.97171 | -0.19947 | 4.2324
99 | 0.00071609 | 0.00017913 | -0.00071607 | -0.00017946 | 2.0233e-08 | -3.3033e-07 | 0.0010932 | 0.0010933 | 0.0010933 | 0.97464 | -0.17834 | 0.97461 | -0.17854 | 0.40492
100 | -0.0032208 | -0.00080686 | 0.003221 | 0.00080677 | 2.0024e-07 | -8.8403e-08 | 0.0049171 | 0.004917 | 0.0049171 | 0.97464 | -0.17834 | 0.97471 | -0.17789 | 1.8211
101 | 0.0077047 | 0.0019308 | -0.0077032 | -0.0019304 | 1.4915e-06 | 3.5878e-07 | 0.011768 | 0.011768 | 0.011768 | 0.97423 | -0.18131 | 0.97403 | -0.18271 | 4.3585
102 | -0.044817 | -0.011239 | 0.044818 | 0.01124 | 6.891e-07 | 2.6208e-07 | 0.068327 | 0.068327 | 0.068327 | 0.97606 | -0.1682 | 0.97607 | -0.16809 | 25.3063
103 | 0.0034306 | 0.0008596 | -0.0034303 | -0.00085971 | 3.0568e-07 | -1.0441e-07 | 0.0052408 | 0.0052409 | 0.0052409 | 0.97403 | -0.18271 | 0.97395 | -0.18335 | 1.9411
104 | 0.0042726 | 0.0010708 | -0.0042726 | -0.0010708 | 8.1783e-08 | -6.8336e-09 | 0.0065272 | 0.0065273 | 0.0065273 | 0.97403 | -0.18271 | 0.97402 | -0.18285 | 2.4175
105 | 0.0050593 | 0.0012653 | -0.005059 | -0.0012653 | 2.7404e-07 | 1.4815e-08 | 0.007748 | 0.007748 | 0.007748 | 0.97154 | -0.20072 | 0.97148 | -0.20111 | 2.8696
106 | -0.0062999 | -0.0015762 | 0.006301 | 0.0015764 | 1.0891e-06 | 1.8666e-07 | 0.0096481 | 0.009648 | 0.0096481 | 0.97154 | -0.20072 | 0.97171 | -0.19947 | 3.5734
107 | 0.011605 | 0.0029086 | -0.011599 | -0.0029067 | 6.1075e-06 | 1.9391e-06 | 0.01748 | 0.01748 | 0.01748 | 0.98788 | -0.08465 | 0.98735 | -0.088453 | 6.4742
108 | 0.010142 | 0.0025415 | -0.010141 | -0.0025413 | 9.36e-07 | 2.7789e-07 | 0.015285 | 0.015285 | 0.015285 | 0.98735 | -0.088453 | 0.98725 | -0.089119 | 5.661
109 | 0.0080313 | 0.0020125 | -0.0080295 | -0.0020121 | 1.7555e-06 | 4.2975e-07 | 0.012105 | 0.012105 | 0.012105 | 0.98725 | -0.089119 | 0.98703 | -0.090699 | 4.4833
110 | 0.007008 | 0.0017561 | -0.0070064 | -0.0017557 | 1.5664e-06 | 3.1507e-07 | 0.010565 | 0.010565 | 0.010565 | 0.98703 | -0.090699 | 0.9868 | -0.092314 | 3.913
111 | 0.0047881 | 0.0011998 | -0.0047877 | -0.0011998 | 4.1526e-07 | -3.3611e-09 | 0.00722 | 0.00722 | 0.00722 | 0.9868 | -0.092314 | 0.98671 | -0.092941 | 2.6741
112 | -0.0013108 | -0.00032852 | 0.0013108 | 0.00032836 | 3.4089e-08 | -1.6252e-07 | 0.001985 | 0.001985 | 0.001985 | 0.98261 | -0.12183 | 0.98264 | -0.12164 | 0.7352
113 | 0.014246 | 0.0035714 | -0.014242 | -0.0035698 | 4.7429e-06 | 1.6174e-06 | 0.021574 | 0.021574 | 0.021574 | 0.98264 | -0.12164 | 0.9823 | -0.12405 | 7.9904
114 | 0.010541 | 0.0026416 | -0.010537 | -0.0026405 | 3.5669e-06 | 1.071e-06 | 0.015735 | 0.015735 | 0.015735 | 0.9968 | -0.022411 | 0.99645 | -0.024856 | 5.8278
115 | 0.0080914 | 0.0020275 | -0.0080909 | -0.0020274 | 5.5339e-07 | 1.3372e-07 | 0.012083 | 0.012083 | 0.012083 | 0.99645 | -0.024856 | 0.99638 | -0.02535 | 4.4752
116 | 0.0030177 | 0.00075595 | -0.0030175 | -0.00075609 | 2.18e-07 | -1.4018e-07 | 0.0045066 | 0.0045067 | 0.0045067 | 0.99638 | -0.02535 | 0.99631 | -0.025872 | 1.6691
117 | 0.0030175 | 0.00075609 | -0.0030173 | -0.00075621 | 1.8762e-07 | -1.2061e-07 | 0.0045067 | 0.0045068 | 0.0045068 | 0.99631 | -0.025872 | 0.99624 | -0.026322 | 1.6692
118 | 0.0084579 | 0.0021195 | -0.0084574 | -0.0021194 | 4.8358e-07 | 1.2548e-07 | 0.012772 | 0.012772 | 0.012772 | 0.98539 | -0.10199 | 0.98533 | -0.10241 | 4.7304
119 | 0.0062113 | 0.0015564 | -0.0062104 | -0.0015563 | 8.8179e-07 | 1.3461e-07 | 0.00938 | 0.00938 | 0.00938 | 0.98533 | -0.10241 | 0.98518 | -0.10343 | 3.4741
120 | 0.0024985 | 0.00062607 | -0.0024984 | -0.00062617 | 8.9339e-08 | -9.4445e-08 | 0.0037679 | 0.0037679 | 0.0037679 | 0.98671 | -0.092941 | 0.98668 | -0.093199 | 1.3955

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22395 | 0.056342

## res_load
| p_mw | q_mvar
0 | 0.0015207 | 0.00038112
1 | 0.0015205 | 0.00038107
2 | 0.0013884 | 0.00034795
3 | 0.0021791 | 0.00054615
4 | 0.0010714 | 0.00026851
5 | 0.0037897 | 0.00094979
6 | 0.0013296 | 0.00033323
7 | 0.0020965 | 0.00052544
8 | 0.002397 | 0.00060075
9 | 0.0036894 | 0.00092465
10 | 0.0024572 | 0.00061584
11 | 0.0032489 | 0.00081426
12 | 0.002106 | 0.00052783
13 | 0.0023031 | 0.00057721
14 | 0.0025762 | 0.00064566
15 | 0.001715 | 0.00042983
16 | 0.0022112 | 0.00055417
17 | 0.0015585 | 0.0003906
18 | 0.0018017 | 0.00045156
19 | 0.002973 | 0.0007451
20 | 0.0017448 | 0.00043729
21 | 0.0013305 | 0.00033345
22 | 0.0018436 | 0.00046204
23 | 0.0031083 | 0.00077902
24 | 0.0021731 | 0.00054463
25 | 0.0026421 | 0.00066216
26 | 0.0027566 | 0.00069087
27 | 0.0025008 | 0.00062676
28 | 0.0029969 | 0.00075108
29 | 0.002769 | 0.00069398
30 | 0.0017909 | 0.00044883
31 | 0.00064336 | 0.00016124
32 | 0.00080822 | 0.00020256
33 | 0.00055656 | 0.00013949
34 | 0.001116 | 0.00027969
35 | 0.0011349 | 0.00028444
36 | 0.0027163 | 0.00068078
37 | 0.0014688 | 0.00036811
38 | 0.0019376 | 0.00048561
39 | 0.0010295 | 0.00025802
40 | 0.0027582 | 0.00069127
41 | 0.0021658 | 0.00054279
42 | 0.0022413 | 0.00056171
43 | 0.0013938 | 0.00034932
44 | 0.0020222 | 0.00050682
45 | 0.0029812 | 0.00074715
46 | 0.0048982 | 0.0012276
47 | 0.001741 | 0.00043634
48 | 0.0017628 | 0.00044179
49 | 0.0024902 | 0.00062412
50 | 0.0023401 | 0.00058648
51 | 0.0020992 | 0.00052611
52 | 0.0011898 | 0.00029819
53 | 0.002022 | 0.00050677
54 | 0.0029362 | 0.00073589
55 | 0.0028337 | 0.00071019
56 | 0.00097149 | 0.00024348
57 | 0.0020852 | 0.00052259
58 | 0.0018617 | 0.00046658
59 | 0.0017289 | 0.0004333
60 | 0.0025137 | 0.00063
61 | 0.0010492 | 0.00026294
62 | 0.0011939 | 0.00029922
63 | 0.0019442 | 0.00048725
64 | 0.0017824 | 0.00044671
65 | 0.0006127 | 0.00015356
66 | 0.00054977 | 0.00013779
67 | 0.00052386 | 0.00013129
68 | 0.0032751 | 0.00082083
69 | 0.0012247 | 0.00030695
70 | 0.0059993 | 0.0015036
71 | 0.00097504 | 0.00024437
72 | 0.00065033 | 0.00016299
73 | 0.0025047 | 0.00062773
74 | 0.00071607 | 0.00017946
75 | 0.0040045 | 0.0010036
76 | 0.002214 | 0.00055487
77 | 0.0062971 | 0.0015782
78 | 0.0034003 | 0.0008522
79 | 0.0012406 | 0.00031093
80 | 0.0007978 | 0.00019995
81 | 0.001162 | 0.00029122
82 | 0.0019255 | 0.00048257
83 | 0.0014569 | 0.00036514
84 | 0.0021097 | 0.00052873
85 | 0.0010216 | 0.00025603
86 | 0.0022183 | 0.00055596
87 | 0.0013108 | 0.00032852
88 | 0.00099142 | 0.00024847
89 | 0.0029528 | 0.00074005
90 | 0.0038241 | 0.00095842
91 | 0.0024457 | 0.00061295
92 | 0.0050732 | 0.0012715
93 | 0.0030173 | 0.00075621
94 | 0.001876 | 0.00047017
95 | 0.0022462 | 0.00056294
96 | 0.0019674 | 0.00049307
97 | 0.0022892 | 0.00057372
98 | 0.0024984 | 0.00062617
99 | 0.0013329 | 0.00033405
100 | 0.0013762 | 0.00034492
101 | 0.0034303 | 0.00085971
102 | 0.0042726 | 0.0010708

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1