## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2422-15_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2422-15_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2422-15_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2422-15_0_2_node_73 | 0.4 | n |  | TRUE
4 | bus_LV_2422-15_0_2_node_20 | 0.4 | n |  | TRUE
5 | bus_LV_2422-15_0_2_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_2422-15_0_2_node_72 | 0.4 | n |  | TRUE
7 | bus_LV_2422-15_0_2_node_112 | 0.4 | n |  | TRUE
8 | bus_LV_2422-15_0_2_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_2422-15_0_2_node_111 | 0.4 | n |  | TRUE
10 | bus_LV_2422-15_0_2_node_114 | 0.4 | n |  | TRUE
11 | bus_LV_2422-15_0_2_node_4 | 0.4 | n |  | TRUE
12 | bus_LV_2422-15_0_2_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_2422-15_0_2_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_2422-15_0_2_node_71 | 0.4 | n |  | TRUE
15 | bus_LV_2422-15_0_2_node_107 | 0.4 | n |  | TRUE
16 | bus_LV_2422-15_0_2_node_78 | 0.4 | n |  | TRUE
17 | bus_LV_2422-15_0_2_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_2422-15_0_2_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_2422-15_0_2_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_2422-15_0_2_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_2422-15_0_2_node_60 | 0.4 | n |  | TRUE
22 | bus_LV_2422-15_0_2_node_44 | 0.4 | n |  | TRUE
23 | bus_LV_2422-15_0_2_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_2422-15_0_2_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_2422-15_0_2_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_2422-15_0_2_node_80 | 0.4 | n |  | TRUE
27 | bus_LV_2422-15_0_2_node_56 | 0.4 | n |  | TRUE
28 | bus_LV_2422-15_0_2_node_57 | 0.4 | n |  | TRUE
29 | bus_LV_2422-15_0_2_node_58 | 0.4 | n |  | TRUE
30 | bus_LV_2422-15_0_2_node_59 | 0.4 | n |  | TRUE
31 | bus_LV_2422-15_0_2_node_113 | 0.4 | n |  | TRUE
32 | bus_LV_2422-15_0_2_node_85 | 0.4 | n |  | TRUE
33 | bus_LV_2422-15_0_2_node_109 | 0.4 | n |  | TRUE
34 | bus_LV_2422-15_0_2_node_79 | 0.4 | n |  | TRUE
35 | bus_LV_2422-15_0_2_node_81 | 0.4 | n |  | TRUE
36 | bus_LV_2422-15_0_2_node_100 | 0.4 | n |  | TRUE
37 | bus_LV_2422-15_0_2_node_84 | 0.4 | n |  | TRUE
38 | bus_LV_2422-15_0_2_node_97 | 0.4 | n |  | TRUE
39 | bus_LV_2422-15_0_2_node_98 | 0.4 | n |  | TRUE
40 | bus_LV_2422-15_0_2_node_99 | 0.4 | n |  | TRUE
41 | bus_LV_2422-15_0_2_node_101 | 0.4 | n |  | TRUE
42 | bus_LV_2422-15_0_2_node_104 | 0.4 | n |  | TRUE
43 | bus_LV_2422-15_0_2_node_108 | 0.4 | n |  | TRUE
44 | bus_LV_2422-15_0_2_node_110 | 0.4 | n |  | TRUE
45 | bus_LV_2422-15_0_2_node_96 | 0.4 | n |  | TRUE
46 | bus_LV_2422-15_0_2_node_42 | 0.4 | n |  | TRUE
47 | bus_LV_2422-15_0_2_node_11 | 0.4 | n |  | TRUE
48 | bus_LV_2422-15_0_2_node_12 | 0.4 | n |  | TRUE
49 | bus_LV_2422-15_0_2_node_13 | 0.4 | n |  | TRUE
50 | bus_LV_2422-15_0_2_node_14 | 0.4 | n |  | TRUE
51 | bus_LV_2422-15_0_2_node_15 | 0.4 | n |  | TRUE
52 | bus_LV_2422-15_0_2_node_16 | 0.4 | n |  | TRUE
53 | bus_LV_2422-15_0_2_node_17 | 0.4 | n |  | TRUE
54 | bus_LV_2422-15_0_2_node_63 | 0.4 | n |  | TRUE
55 | bus_LV_2422-15_0_2_node_117 | 0.4 | n |  | TRUE
56 | bus_LV_2422-15_0_2_node_86 | 0.4 | n |  | TRUE
57 | bus_LV_2422-15_0_2_node_18 | 0.4 | n |  | TRUE
58 | bus_LV_2422-15_0_2_node_105 | 0.4 | n |  | TRUE
59 | bus_LV_2422-15_0_2_node_62 | 0.4 | n |  | TRUE
60 | bus_LV_2422-15_0_2_node_116 | 0.4 | n |  | TRUE
61 | bus_LV_2422-15_0_2_node_87 | 0.4 | n |  | TRUE
62 | bus_LV_2422-15_0_2_node_19 | 0.4 | n |  | TRUE
63 | bus_LV_2422-15_0_2_node_69 | 0.4 | n |  | TRUE
64 | bus_LV_2422-15_0_2_node_21 | 0.4 | n |  | TRUE
65 | bus_LV_2422-15_0_2_node_22 | 0.4 | n |  | TRUE
66 | bus_LV_2422-15_0_2_node_23 | 0.4 | n |  | TRUE
67 | bus_LV_2422-15_0_2_node_25 | 0.4 | n |  | TRUE
68 | bus_LV_2422-15_0_2_node_52 | 0.4 | n |  | TRUE
69 | bus_LV_2422-15_0_2_node_53 | 0.4 | n |  | TRUE
70 | bus_LV_2422-15_0_2_node_29 | 0.4 | n |  | TRUE
71 | bus_LV_2422-15_0_2_node_30 | 0.4 | n |  | TRUE
72 | bus_LV_2422-15_0_2_node_31 | 0.4 | n |  | TRUE
73 | bus_LV_2422-15_0_2_node_32 | 0.4 | n |  | TRUE
74 | bus_LV_2422-15_0_2_node_33 | 0.4 | n |  | TRUE
75 | bus_LV_2422-15_0_2_node_34 | 0.4 | n |  | TRUE
76 | bus_LV_2422-15_0_2_node_70 | 0.4 | n |  | TRUE
77 | bus_LV_2422-15_0_2_node_54 | 0.4 | n |  | TRUE
78 | bus_LV_2422-15_0_2_node_82 | 0.4 | n |  | TRUE
79 | bus_LV_2422-15_0_2_node_88 | 0.4 | n |  | TRUE
80 | bus_LV_2422-15_0_2_node_106 | 0.4 | n |  | TRUE
81 | bus_LV_2422-15_0_2_node_83 | 0.4 | n |  | TRUE
82 | bus_LV_2422-15_0_2_node_35 | 0.4 | n |  | TRUE
83 | bus_LV_2422-15_0_2_node_36 | 0.4 | n |  | TRUE
84 | bus_LV_2422-15_0_2_node_37 | 0.4 | n |  | TRUE
85 | bus_LV_2422-15_0_2_node_38 | 0.4 | n |  | TRUE
86 | bus_LV_2422-15_0_2_node_39 | 0.4 | n |  | TRUE
87 | bus_LV_2422-15_0_2_node_61 | 0.4 | n |  | TRUE
88 | bus_LV_2422-15_0_2_node_40 | 0.4 | n |  | TRUE
89 | bus_LV_2422-15_0_2_node_41 | 0.4 | n |  | TRUE
90 | bus_LV_2422-15_0_2_node_43 | 0.4 | n |  | TRUE
91 | bus_LV_2422-15_0_2_node_45 | 0.4 | n |  | TRUE
92 | bus_LV_2422-15_0_2_node_91 | 0.4 | n |  | TRUE
93 | bus_LV_2422-15_0_2_node_55 | 0.4 | n |  | TRUE
94 | bus_LV_2422-15_0_2_node_93 | 0.4 | n |  | TRUE
95 | bus_LV_2422-15_0_2_node_89 | 0.4 | n |  | TRUE
96 | bus_LV_2422-15_0_2_node_46 | 0.4 | n |  | TRUE
97 | bus_LV_2422-15_0_2_node_47 | 0.4 | n |  | TRUE
98 | bus_LV_2422-15_0_2_node_48 | 0.4 | n |  | TRUE
99 | bus_LV_2422-15_0_2_node_49 | 0.4 | n |  | TRUE
100 | bus_LV_2422-15_0_2_node_50 | 0.4 | n |  | TRUE
101 | bus_LV_2422-15_0_2_node_51 | 0.4 | n |  | TRUE
102 | bus_LV_2422-15_0_2_node_94 | 0.4 | n |  | TRUE
103 | bus_LV_2422-15_0_2_node_115 | 0.4 | n |  | TRUE
104 | bus_LV_2422-15_0_2_node_102 | 0.4 | n |  | TRUE
105 | bus_LV_2422-15_0_2_node_95 | 0.4 | n |  | TRUE
106 | bus_LV_2422-15_0_2_node_65 | 0.4 | n |  | TRUE
107 | bus_LV_2422-15_0_2_node_103 | 0.4 | n |  | TRUE
108 | bus_LV_2422-15_0_2_node_64 | 0.4 | n |  | TRUE
109 | bus_LV_2422-15_0_2_node_66 | 0.4 | n |  | TRUE
110 | bus_LV_2422-15_0_2_node_67 | 0.4 | n |  | TRUE
111 | bus_LV_2422-15_0_2_node_68 | 0.4 | n |  | TRUE
112 | bus_LV_2422-15_0_2_node_74 | 0.4 | n |  | TRUE
113 | bus_LV_2422-15_0_2_node_75 | 0.4 | n |  | TRUE
114 | bus_LV_2422-15_0_2_node_76 | 0.4 | n |  | TRUE
115 | bus_LV_2422-15_0_2_node_77 | 0.4 | n |  | TRUE
116 | bus_LV_2422-15_0_2_node_90 | 0.4 | n |  | TRUE
117 | bus_LV_2422-15_0_2_node_92 | 0.4 | n |  | TRUE
118 | bus_LV_2422-15_0_2_node_118 | 0.4 | n |  | TRUE
119 | bus_LV_2422-15_0_2_node_119 | 0.4 | n |  | TRUE
120 | bus_LV_2422-15_0_2_node_120 | 0.4 | n |  | TRUE
121 | bus_LV_2422-15_0_2_node_121 | 0.4 | n |  | TRUE
122 | bus_LV_2422-15_0_2_node_122 | 0.4 | n |  | TRUE
123 | bus_LV_2422-15_0_2_node_123 | 0.4 | n |  | TRUE
124 | bus_LV_2422-15_0_2_node_124 | 0.4 | n |  | TRUE
125 | bus_MV_333_0_node_16 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2422-15_0_2_load_0 | 0 | 0.0016055 | 0.00040239 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2422-15_0_2_load_1 | 1 | 0.0010281 | 0.00025767 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2422-15_0_2_load_2 | 2 | 0.0009487 | 0.00023777 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2422-15_0_2_load_73 | 3 | 0.00083479 | 0.00020922 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2422-15_0_2_load_20 | 4 | 0.0025942 | 0.00065017 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2422-15_0_2_load_3 | 5 | 0.00078031 | 0.00019556 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2422-15_0_2_load_24 | 8 | 0.00055972 | 0.00014028 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2422-15_0_2_load_111 | 9 | 0.002047 | 0.00051303 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2422-15_0_2_load_114 | 10 | 0.0035383 | 0.00088677 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2422-15_0_2_load_4 | 11 | 0.00094094 | 0.00023582 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2422-15_0_2_load_5 | 12 | 0.00086204 | 0.00021605 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2422-15_0_2_load_6 | 13 | 0.00083646 | 0.00020964 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2422-15_0_2_load_71 | 14 | 0.00099307 | 0.00024889 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2422-15_0_2_load_107 | 15 | 0.00089202 | 0.00022356 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2422-15_0_2_load_78 | 16 | 0.0010155 | 0.0002545 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2422-15_0_2_load_7 | 17 | 0.0014024 | 0.00035148 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2422-15_0_2_load_8 | 18 | 0.0014436 | 0.00036179 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2422-15_0_2_load_9 | 19 | 0.0011417 | 0.00028613 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2422-15_0_2_load_10 | 20 | 0.0016601 | 0.00041606 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2422-15_0_2_load_44 | 22 | 0.0013379 | 0.00033531 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2422-15_0_2_load_26 | 23 | 0.0020541 | 0.0005148 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2422-15_0_2_load_27 | 24 | 0.0021008 | 0.00052652 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2422-15_0_2_load_56 | 27 | 0.00097913 | 0.00024539 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2422-15_0_2_load_58 | 29 | 0.0019405 | 0.00048635 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2422-15_0_2_load_59 | 30 | 0.0014987 | 0.0003756 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2422-15_0_2_load_113 | 31 | 0.0012019 | 0.00030123 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2422-15_0_2_load_85 | 32 | 0.0012856 | 0.0003222 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2422-15_0_2_load_109 | 33 | 0.0012125 | 0.00030388 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2422-15_0_2_load_79 | 34 | 0.0015259 | 0.00038243 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2422-15_0_2_load_81 | 35 | 0.0014256 | 0.00035729 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2422-15_0_2_load_100 | 36 | 0.0013351 | 0.0003346 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2422-15_0_2_load_84 | 37 | 0.0006981 | 0.00017496 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2422-15_0_2_load_97 | 38 | 0.0019191 | 0.00048098 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2422-15_0_2_load_98 | 39 | 0.0013306 | 0.00033347 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2422-15_0_2_load_99 | 40 | 0.0016811 | 0.00042132 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2422-15_0_2_load_101 | 41 | 0.0021045 | 0.00052743 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2422-15_0_2_load_104 | 42 | 0.0015215 | 0.00038132 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2422-15_0_2_load_108 | 43 | 0.0028207 | 0.00070694 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2422-15_0_2_load_110 | 44 | 0.0010003 | 0.0002507 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2422-15_0_2_load_96 | 45 | 0.0037961 | 0.00095139 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2422-15_0_2_load_11 | 47 | 0.0017642 | 0.00044215 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2422-15_0_2_load_15 | 51 | 0.0021679 | 0.00054332 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2422-15_0_2_load_16 | 52 | 0.0027005 | 0.00067681 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2422-15_0_2_load_17 | 53 | 0.002019 | 0.000506 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2422-15_0_2_load_63 | 54 | 0.0014515 | 0.00036378 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2422-15_0_2_load_117 | 55 | 0.0011523 | 0.0002888 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2422-15_0_2_load_86 | 56 | 0.002039 | 0.00051101 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2422-15_0_2_load_18 | 57 | 0.0030821 | 0.00077244 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2422-15_0_2_load_105 | 58 | 0.0019694 | 0.00049358 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2422-15_0_2_load_62 | 59 | 0.0034086 | 0.00085428 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2422-15_0_2_load_116 | 60 | 0.0016834 | 0.0004219 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2422-15_0_2_load_87 | 61 | 0.0031489 | 0.00078919 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2422-15_0_2_load_19 | 62 | 0.0017067 | 0.00042775 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2422-15_0_2_load_21 | 64 | 0.0023899 | 0.00059897 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2422-15_0_2_load_22 | 65 | 0.0027833 | 0.00069757 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2422-15_0_2_load_23 | 66 | 0.0043173 | 0.001082 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2422-15_0_2_load_25 | 67 | 0.00070237 | 0.00017603 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2422-15_0_2_load_52 | 68 | 0.0011362 | 0.00028476 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2422-15_0_2_load_29 | 70 | 0.0013827 | 0.00034653 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2422-15_0_2_load_30 | 71 | 0.0010191 | 0.00025541 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2422-15_0_2_load_33 | 74 | 0.0018582 | 0.00046572 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2422-15_0_2_load_34 | 75 | 0.0012662 | 0.00031734 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2422-15_0_2_load_70 | 76 | 0.0012053 | 0.00030208 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2422-15_0_2_load_54 | 77 | 0.0011953 | 0.00029956 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2422-15_0_2_load_82 | 78 | 0.002164 | 0.00054234 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2422-15_0_2_load_88 | 79 | 0.0026074 | 0.00065348 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2422-15_0_2_load_106 | 80 | 0.0022167 | 0.00055555 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2422-15_0_2_load_83 | 81 | 0.0013402 | 0.00033589 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2422-15_0_2_load_35 | 82 | 0.0012025 | 0.00030137 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2422-15_0_2_load_36 | 83 | 0.003963 | 0.00099322 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2422-15_0_2_load_37 | 84 | 0.0019111 | 0.00047896 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2422-15_0_2_load_38 | 85 | 0.0029277 | 0.00073375 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2422-15_0_2_load_39 | 86 | 0.0013936 | 0.00034927 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2422-15_0_2_load_61 | 87 | 0.0019506 | 0.00048886 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2422-15_0_2_load_40 | 88 | 0.0016074 | 0.00040286 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2422-15_0_2_load_41 | 89 | 0.00098751 | 0.00024749 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2422-15_0_2_load_43 | 90 | 0.0011515 | 0.0002886 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2422-15_0_2_load_45 | 91 | 0.00089695 | 0.0002248 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2422-15_0_2_load_55 | 93 | 0.0029218 | 0.00073228 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2422-15_0_2_load_93 | 94 | 0.0017999 | 0.00045111 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2422-15_0_2_load_89 | 95 | 0.0010222 | 0.00025619 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2422-15_0_2_load_46 | 96 | 0.00093373 | 0.00023401 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2422-15_0_2_load_49 | 99 | 0.0016548 | 0.00041472 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2422-15_0_2_load_50 | 100 | 0.0010615 | 0.00026604 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2422-15_0_2_load_51 | 101 | 0.0020979 | 0.00052577 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2422-15_0_2_load_94 | 102 | 0.0029281 | 0.00073384 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2422-15_0_2_load_115 | 103 | 0.0029311 | 0.00073461 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2422-15_0_2_load_102 | 104 | 0.0024392 | 0.00061132 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2422-15_0_2_load_95 | 105 | 0.0016885 | 0.00042319 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2422-15_0_2_load_65 | 106 | 0.0015377 | 0.00038538 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2422-15_0_2_load_103 | 107 | 0.0017857 | 0.00044753 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2422-15_0_2_load_64 | 108 | 0.0012439 | 0.00031175 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2422-15_0_2_load_66 | 109 | 0.002429 | 0.00060876 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2422-15_0_2_load_67 | 110 | 0.0028104 | 0.00070435 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2422-15_0_2_load_68 | 111 | 0.0043094 | 0.00108 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2422-15_0_2_load_74 | 112 | 0.0012566 | 0.00031492 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2422-15_0_2_load_75 | 113 | 0.0015775 | 0.00039536 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2422-15_0_2_load_76 | 114 | 0.0014327 | 0.00035906 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2422-15_0_2_load_77 | 115 | 0.0012948 | 0.00032451 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2422-15_0_2_load_90 | 116 | 0.00093969 | 0.00023551 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2422-15_0_2_load_92 | 117 | 0.0016189 | 0.00040574 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2422-15_0_2_load_119 | 119 | 0.0022076 | 0.00055327 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2422-15_0_2_load_120 | 120 | 0.001126 | 0.0002822 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2422-15_0_2_load_121 | 121 | 0.0011616 | 0.00029112 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2422-15_0_2_load_122 | 122 | 0.0013828 | 0.00034656 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2422-15_0_2_load_123 | 123 | 0.0019916 | 0.00049914 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2422-15_0_2_load_124 | 124 | 0.0010628 | 0.00026635 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 93 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2422-15_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.003244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2422-15_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.032542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2422-15_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.0045939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2422-15_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.02623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2422-15_0_2_line_4 | NAYY 4x150 SE | 4 | 62 | 0.019999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2422-15_0_2_line_5 | NAYY 4x150 SE | 5 | 6 | 0.06408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2422-15_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.072667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2422-15_0_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.019458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2422-15_0_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.033036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2422-15_0_2_line_9 | NAYY 4x150 SE | 8 | 65 | 0.00048581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2422-15_0_2_line_10 | NAYY 4x150 SE | 9 | 10 | 0.053342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2422-15_0_2_line_11 | NAYY 4x150 SE | 11 | 12 | 0.00053503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2422-15_0_2_line_12 | NAYY 4x150 SE | 12 | 13 | 0.021894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2422-15_0_2_line_13 | NAYY 4x150 SE | 12 | 14 | 0.049772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2422-15_0_2_line_14 | NAYY 4x150 SE | 13 | 15 | 0.00065277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2422-15_0_2_line_15 | NAYY 4x150 SE | 15 | 16 | 0.022017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2422-15_0_2_line_16 | NAYY 4x150 SE | 16 | 114 | 0.0013191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2422-15_0_2_line_17 | NAYY 4x150 SE | 17 | 18 | 0.0013349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2422-15_0_2_line_18 | NAYY 4x150 SE | 17 | 19 | 0.0038134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2422-15_0_2_line_19 | NAYY 4x150 SE | 18 | 20 | 0.017148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2422-15_0_2_line_20 | NAYY 4x150 SE | 19 | 21 | 0.045287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2422-15_0_2_line_21 | NAYY 4x150 SE | 20 | 22 | 0.022532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2422-15_0_2_line_22 | NAYY 4x150 SE | 21 | 32 | 0.019061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2422-15_0_2_line_23 | NAYY 4x150 SE | 21 | 33 | 0.016004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2422-15_0_2_line_24 | NAYY 4x150 SE | 21 | 28 | 0.024358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2422-15_0_2_line_25 | NAYY 4x150 SE | 22 | 46 | 0.009689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2422-15_0_2_line_26 | NAYY 4x150 SE | 23 | 24 | 0.029368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2422-15_0_2_line_27 | NAYY 4x150 SE | 24 | 25 | 0.021453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2422-15_0_2_line_28 | NAYY 4x150 SE | 25 | 26 | 0.011492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2422-15_0_2_line_29 | NAYY 4x150 SE | 26 | 35 | 0.021373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2422-15_0_2_line_30 | NAYY 4x150 SE | 26 | 34 | 0.0098821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2422-15_0_2_line_31 | NAYY 4x150 SE | 27 | 28 | 0.013075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2422-15_0_2_line_32 | NAYY 4x150 SE | 27 | 29 | 0.02868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2422-15_0_2_line_33 | NAYY 4x150 SE | 28 | 30 | 0.0090247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2422-15_0_2_line_34 | NAYY 4x150 SE | 30 | 31 | 0.019668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2422-15_0_2_line_35 | NAYY 4x150 SE | 31 | 42 | 5.1853e-06 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2422-15_0_2_line_36 | NAYY 4x150 SE | 32 | 37 | 0.032635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2422-15_0_2_line_37 | NAYY 4x150 SE | 33 | 43 | 0.029881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2422-15_0_2_line_38 | NAYY 4x150 SE | 35 | 36 | 0.0031688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2422-15_0_2_line_39 | NAYY 4x150 SE | 36 | 39 | 0.016394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2422-15_0_2_line_40 | NAYY 4x150 SE | 38 | 39 | 0.004818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2422-15_0_2_line_41 | NAYY 4x150 SE | 38 | 40 | 0.015248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2422-15_0_2_line_42 | NAYY 4x150 SE | 40 | 41 | 0.0019446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2422-15_0_2_line_43 | NAYY 4x150 SE | 41 | 42 | 0.023541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2422-15_0_2_line_44 | NAYY 4x150 SE | 43 | 44 | 0.0097318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2422-15_0_2_line_45 | NAYY 4x150 SE | 44 | 45 | 0.21987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2422-15_0_2_line_46 | NAYY 4x150 SE | 46 | 91 | 0.011476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2422-15_0_2_line_47 | NAYY 4x150 SE | 46 | 88 | 0.011968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2422-15_0_2_line_48 | NAYY 4x150 SE | 47 | 48 | 0.017182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2422-15_0_2_line_49 | NAYY 4x150 SE | 47 | 49 | 0.014608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2422-15_0_2_line_50 | NAYY 4x150 SE | 48 | 50 | 0.020203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2422-15_0_2_line_51 | NAYY 4x150 SE | 48 | 51 | 0.013255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2422-15_0_2_line_52 | NAYY 4x150 SE | 49 | 52 | 0.010259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2422-15_0_2_line_53 | NAYY 4x150 SE | 49 | 53 | 0.007445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2422-15_0_2_line_54 | NAYY 4x150 SE | 50 | 54 | 0.010021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2422-15_0_2_line_55 | NAYY 4x150 SE | 50 | 55 | 0.014979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2422-15_0_2_line_56 | NAYY 4x150 SE | 51 | 56 | 0.017607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2422-15_0_2_line_57 | NAYY 4x150 SE | 52 | 57 | 0.033899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2422-15_0_2_line_58 | NAYY 4x150 SE | 53 | 58 | 0.027602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2422-15_0_2_line_59 | NAYY 4x150 SE | 54 | 59 | 0.0076553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2422-15_0_2_line_60 | NAYY 4x150 SE | 55 | 60 | 0.0062973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2422-15_0_2_line_61 | NAYY 4x150 SE | 56 | 61 | 0.0057707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2422-15_0_2_line_62 | NAYY 4x150 SE | 57 | 62 | 0.008883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2422-15_0_2_line_63 | NAYY 4x150 SE | 58 | 63 | 0.0028094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2422-15_0_2_line_64 | NAYY 4x150 SE | 59 | 108 | 0.013631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2422-15_0_2_line_65 | NAYY 4x150 SE | 60 | 118 | 0.015974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2422-15_0_2_line_66 | NAYY 4x150 SE | 61 | 87 | 0.015226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2422-15_0_2_line_67 | NAYY 4x150 SE | 63 | 107 | 0.014556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2422-15_0_2_line_68 | NAYY 4x150 SE | 63 | 110 | 0.0172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2422-15_0_2_line_69 | NAYY 4x150 SE | 64 | 65 | 0.018777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2422-15_0_2_line_70 | NAYY 4x150 SE | 64 | 66 | 0.018247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2422-15_0_2_line_71 | NAYY 4x150 SE | 66 | 67 | 0.024696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2422-15_0_2_line_72 | NAYY 4x150 SE | 67 | 68 | 0.029367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2422-15_0_2_line_73 | NAYY 4x150 SE | 68 | 69 | 0.021898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2422-15_0_2_line_74 | NAYY 4x150 SE | 69 | 93 | 0.021795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2422-15_0_2_line_75 | NAYY 4x150 SE | 69 | 77 | 0.024069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2422-15_0_2_line_76 | NAYY 4x150 SE | 69 | 90 | 0.026659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2422-15_0_2_line_77 | NAYY 4x150 SE | 70 | 71 | 0.011664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2422-15_0_2_line_78 | NAYY 4x150 SE | 70 | 72 | 0.0090824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2422-15_0_2_line_79 | NAYY 4x150 SE | 71 | 73 | 0.022198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2422-15_0_2_line_80 | NAYY 4x150 SE | 72 | 74 | 0.033051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2422-15_0_2_line_81 | NAYY 4x150 SE | 72 | 75 | 0.011487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2422-15_0_2_line_82 | NAYY 4x150 SE | 73 | 76 | 0.011648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2422-15_0_2_line_83 | NAYY 4x150 SE | 73 | 77 | 0.0039734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2422-15_0_2_line_84 | NAYY 4x150 SE | 74 | 78 | 0.00057988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2422-15_0_2_line_85 | NAYY 4x150 SE | 75 | 79 | 0.055407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2422-15_0_2_line_86 | NAYY 4x150 SE | 76 | 80 | 0.014423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2422-15_0_2_line_87 | NAYY 4x150 SE | 78 | 81 | 0.0076388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2422-15_0_2_line_88 | NAYY 4x150 SE | 82 | 83 | 0.016509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2422-15_0_2_line_89 | NAYY 4x150 SE | 82 | 84 | 0.024564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2422-15_0_2_line_90 | NAYY 4x150 SE | 83 | 85 | 0.0060375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2422-15_0_2_line_91 | NAYY 4x150 SE | 84 | 86 | 0.017114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2422-15_0_2_line_92 | NAYY 4x150 SE | 85 | 87 | 0.014608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2422-15_0_2_line_93 | NAYY 4x150 SE | 88 | 89 | 0.019838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2422-15_0_2_line_94 | NAYY 4x150 SE | 89 | 90 | 0.02033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2422-15_0_2_line_95 | NAYY 4x150 SE | 91 | 92 | 0.012603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2422-15_0_2_line_96 | NAYY 4x150 SE | 92 | 94 | 0.026106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2422-15_0_2_line_97 | NAYY 4x150 SE | 92 | 95 | 0.0091875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2422-15_0_2_line_98 | NAYY 4x150 SE | 93 | 107 | 0.031662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2422-15_0_2_line_99 | NAYY 4x150 SE | 95 | 116 | 0.00024268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2422-15_0_2_line_100 | NAYY 4x150 SE | 96 | 97 | 0.015077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2422-15_0_2_line_101 | NAYY 4x150 SE | 96 | 98 | 0.013234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2422-15_0_2_line_102 | NAYY 4x150 SE | 97 | 99 | 0.011241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2422-15_0_2_line_103 | NAYY 4x150 SE | 97 | 100 | 0.010308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2422-15_0_2_line_104 | NAYY 4x150 SE | 98 | 101 | 0.023933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2422-15_0_2_line_105 | NAYY 4x150 SE | 99 | 102 | 0.0265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2422-15_0_2_line_106 | NAYY 4x150 SE | 100 | 103 | 0.0050511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2422-15_0_2_line_107 | NAYY 4x150 SE | 101 | 104 | 0.0055628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2422-15_0_2_line_108 | NAYY 4x150 SE | 102 | 105 | 0.0059436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2422-15_0_2_line_109 | NAYY 4x150 SE | 103 | 106 | 0.019521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2422-15_0_2_line_110 | NAYY 4x150 SE | 105 | 115 | 0.0091757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2422-15_0_2_line_111 | NAYY 4x150 SE | 106 | 108 | 0.004994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2422-15_0_2_line_112 | NAYY 4x150 SE | 109 | 110 | 0.019196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2422-15_0_2_line_113 | NAYY 4x150 SE | 109 | 111 | 0.0099208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2422-15_0_2_line_114 | NAYY 4x150 SE | 112 | 113 | 0.0056793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2422-15_0_2_line_115 | NAYY 4x150 SE | 112 | 114 | 0.024201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2422-15_0_2_line_116 | NAYY 4x150 SE | 113 | 115 | 0.020702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2422-15_0_2_line_117 | NAYY 4x150 SE | 116 | 117 | 0.0019472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2422-15_0_2_line_118 | NAYY 4x150 SE | 118 | 119 | 0.021725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2422-15_0_2_line_119 | NAYY 4x150 SE | 118 | 120 | 0.020274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2422-15_0_2_line_120 | NAYY 4x150 SE | 120 | 121 | 0.027077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2422-15_0_2_line_121 | NAYY 4x150 SE | 121 | 122 | 0.0014571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2422-15_0_2_line_122 | NAYY 4x150 SE | 122 | 123 | 0.027656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_2422-15_0_2_line_123 | NAYY 4x150 SE | 123 | 124 | 0.015448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2422-15_0_2_trafo_55 | 0.25 MVA 20/0.4 kV | 125 | 93 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2620556.6846 | 1240538.1777 | 2620554.2813 | 1240540.3566
1 | 2620554.2813 | 1240540.3566 | 2620530.1725 | 1240562.2136
2 | 2620530.1725 | 1240562.2136 | 2620526.7691 | 1240565.2992
3 | 2620507.3363 | 1240582.917 | 2620526.7691 | 1240565.2992
4 | 2620507.3363 | 1240582.917 | 2620498.2039 | 1240591.1964 | 2620491.9987 | 1240595.709
5 | 2620606.1405 | 1240546.2298 | 2620629.0508 | 1240486.3853
6 | 2620629.0508 | 1240486.3853 | 2620670.8535 | 1240426.9461
7 | 2620606.1405 | 1240546.2298 | 2620599.7893 | 1240546.2078 | 2620594.0018 | 1240549.3786 | 2620590.0963 | 1240554.5846
8 | 2620670.8535 | 1240426.9461 | 2620676.1158 | 1240413.9563 | 2620679.4458 | 1240395.2295
9 | 2620590.0963 | 1240554.5846 | 2620589.8047 | 1240554.9732
10 | 2620679.4458 | 1240395.2295 | 2620629.7435 | 1240375.8641
11 | 2620189.1352 | 1240557.7149 | 2620189.6545 | 1240557.8437
12 | 2620189.6545 | 1240557.8437 | 2620207.6001 | 1240562.2958 | 2620210.9967 | 1240562.5303
13 | 2620189.6545 | 1240557.8437 | 2620209.9458 | 1240512.3963
14 | 2620210.9967 | 1240562.5303 | 2620211.648 | 1240562.5753
15 | 2620211.648 | 1240562.5753 | 2620233.613 | 1240564.0919
16 | 2620234.9289 | 1240564.1827 | 2620233.613 | 1240564.0919
17 | 2620673.2243 | 1240691.5955 | 2620672.0021 | 1240691.0586
18 | 2620673.2243 | 1240691.5955 | 2620676.7157 | 1240693.1294
19 | 2620656.3021 | 1240684.1615 | 2620672.0021 | 1240691.0586
20 | 2620676.7157 | 1240693.1294 | 2620718.1785 | 1240711.3444
21 | 2620656.3021 | 1240684.1615 | 2620635.673 | 1240675.0989
22 | 2620718.1785 | 1240711.3444 | 2620726.4716 | 1240694.1823
23 | 2620718.1785 | 1240711.3444 | 2620716.4424 | 1240714.8739 | 2620713.0746 | 1240726.4654
24 | 2620718.1785 | 1240711.3444 | 2620741.0655 | 1240719.8628
25 | 2620626.8023 | 1240671.2019 | 2620635.673 | 1240675.0989
26 | 2620862.3114 | 1240775.8695 | 2620861.577 | 1240786.5257 | 2620863.2056 | 1240789.9447 | 2620868.7768 | 1240792.388 | 2620877.206 | 1240794.971
27 | 2620862.4 | 1240754.4974 | 2620863.2578 | 1240762.1385 | 2620862.3114 | 1240775.8695
28 | 2620852.5998 | 1240748.4482 | 2620862.4 | 1240754.4974
29 | 2620852.5998 | 1240748.4482 | 2620831.7857 | 1240743.5927
30 | 2620852.5998 | 1240748.4482 | 2620861.8276 | 1240744.9121
31 | 2620741.0655 | 1240719.8628 | 2620738.8115 | 1240726.6258 | 2620737.2314 | 1240732.3586
32 | 2620737.4818 | 1240758.8747 | 2620733.6476 | 1240754.8144 | 2620732.8539 | 1240748.2408 | 2620737.2314 | 1240732.3586
33 | 2620741.0655 | 1240719.8628 | 2620749.7194 | 1240722.4229
34 | 2620768.5799 | 1240728.0025 | 2620749.7194 | 1240722.4229
35 | 2620768.5848 | 1240728.0039 | 2620768.5799 | 1240728.0025
36 | 2620740.6707 | 1240664.7979 | 2620726.4716 | 1240694.1823
37 | 2620704.4397 | 1240755.0684 | 2620707.7263 | 1240744.8735 | 2620713.0746 | 1240726.4654
38 | 2620831.7857 | 1240743.5927 | 2620828.6997 | 1240742.8728
39 | 2620812.7344 | 1240739.1485 | 2620828.6997 | 1240742.8728
40 | 2620808.0424 | 1240738.054 | 2620812.7344 | 1240739.1485
41 | 2620808.0424 | 1240738.054 | 2620793.1933 | 1240734.59
42 | 2620793.1933 | 1240734.59 | 2620791.2996 | 1240734.1483
43 | 2620791.2996 | 1240734.1483 | 2620782.1007 | 1240732.0024 | 2620768.5848 | 1240728.0039
44 | 2620694.7097 | 1240754.8789 | 2620704.4397 | 1240755.0684 | 2620704.4397 | 1240755.0684
45 | 2620694.7097 | 1240754.8789 | 2620675.5851 | 1240973.9193
46 | 2620626.8023 | 1240671.2019 | 2620624.0863 | 1240682.3518
47 | 2620626.8023 | 1240671.2019 | 2620615.8743 | 1240666.3213
48 | 2620419.0983 | 1240616.3959 | 2620435.3144 | 1240622.0761
49 | 2620449.1015 | 1240626.9054 | 2620435.3144 | 1240622.0761
50 | 2620419.0983 | 1240616.3959 | 2620399.8396 | 1240610.1148
51 | 2620419.0983 | 1240616.3959 | 2620427.2018 | 1240605.906 | 2620427.2018 | 1240605.906
52 | 2620449.1015 | 1240626.9054 | 2620457.3986 | 1240620.8715
53 | 2620449.1015 | 1240626.9054 | 2620456.0843 | 1240629.4877
54 | 2620399.8396 | 1240610.1148 | 2620390.7386 | 1240605.9196
55 | 2620399.8396 | 1240610.1148 | 2620396.0388 | 1240622.6429 | 2620395.2876 | 1240624.374
56 | 2620427.2018 | 1240605.906 | 2620441.6825 | 1240595.891
57 | 2620457.3986 | 1240620.8715 | 2620484.8145 | 1240600.9336
58 | 2620481.9725 | 1240639.0613 | 2620456.0843 | 1240629.4877
59 | 2620383.7864 | 1240602.7148 | 2620390.7386 | 1240605.9196
60 | 2620395.2876 | 1240624.374 | 2620392.7808 | 1240630.1508
61 | 2620441.6825 | 1240595.891 | 2620446.4288 | 1240592.6085
62 | 2620484.8145 | 1240600.9336 | 2620491.9987 | 1240595.709
63 | 2620484.6075 | 1240640.0357 | 2620481.9725 | 1240639.0613
64 | 2620371.53 | 1240596.7711 | 2620374.2033 | 1240598.2974 | 2620383.7864 | 1240602.7148
65 | 2620385.2212 | 1240644.1416 | 2620389.2942 | 1240638.1851 | 2620392.7808 | 1240630.1508
66 | 2620458.9513 | 1240583.9479 | 2620446.4288 | 1240592.6085
67 | 2620484.6075 | 1240640.0357 | 2620490.432 | 1240641.4678 | 2620497.9274 | 1240642.9056 | 2620498.8484 | 1240643.0035
68 | 2620484.6075 | 1240640.0357 | 2620480.3357 | 1240656.6971
69 | 2620589.8047 | 1240554.9732 | 2620578.5363 | 1240569.9936
70 | 2620587.2666 | 1240585.7034 | 2620586.0072 | 1240580.7373 | 2620582.8804 | 1240575.3676 | 2620578.5363 | 1240569.9936 | 2620578.5363 | 1240569.9936
71 | 2620587.2666 | 1240585.7034 | 2620587.8048 | 1240587.8257 | 2620587.9936 | 1240592.2736 | 2620587.3716 | 1240597.219 | 2620586.1393 | 1240601.5619 | 2620583.4806 | 1240607.3119 | 2620582.1848 | 1240609.116
72 | 2620560.5933 | 1240628.8238 | 2620574.5249 | 1240617.087 | 2620579.2032 | 1240613.2675 | 2620582.1848 | 1240609.116
73 | 2620552.0054 | 1240648.6512 | 2620554.5701 | 1240639.4654 | 2620559.1998 | 1240629.9977 | 2620560.5933 | 1240628.8238
74 | 2620552.0054 | 1240648.6512 | 2620530.3328 | 1240646.3486
75 | 2620552.0054 | 1240648.6512 | 2620545.6499 | 1240671.8658
76 | 2620552.0054 | 1240648.6512 | 2620571.4667 | 1240650.9421 | 2620578.402 | 1240652.2787
77 | 2620538.4344 | 1240697.0227 | 2620537.4 | 1240700.6 | 2620538.939 | 1240708.3895
78 | 2620540.6993 | 1240717.2997 | 2620538.939 | 1240708.3895
79 | 2620544.6007 | 1240675.6982 | 2620538.4344 | 1240697.0227
80 | 2620540.6993 | 1240717.2997 | 2620573.2558 | 1240722.995
81 | 2620540.6993 | 1240717.2997 | 2620542.4161 | 1240723.7207 | 2620543.1352 | 1240728.5079
82 | 2620544.6007 | 1240675.6982 | 2620533.0565 | 1240674.1483
83 | 2620544.6007 | 1240675.6982 | 2620545.6499 | 1240671.8658
84 | 2620573.827 | 1240723.0949 | 2620573.2558 | 1240722.995
85 | 2620543.1352 | 1240728.5079 | 2620494.0659 | 1240754.2399
86 | 2620518.7623 | 1240672.2291 | 2620533.0565 | 1240674.1483
87 | 2620581.3516 | 1240724.4112 | 2620573.827 | 1240723.0949
88 | 2620475.9312 | 1240572.2046 | 2620489.5089 | 1240562.8143
89 | 2620508.3179 | 1240547.0839 | 2620495.6018 | 1240558.6004 | 2620489.5089 | 1240562.8143
90 | 2620475.9312 | 1240572.2046 | 2620470.9655 | 1240575.6389
91 | 2620521.0028 | 1240535.5957 | 2620508.3179 | 1240547.0839
92 | 2620470.9655 | 1240575.6389 | 2620458.9513 | 1240583.9479
93 | 2620615.8743 | 1240666.3213 | 2620597.7603 | 1240658.2314
94 | 2620578.402 | 1240652.2787 | 2620585.8 | 1240653.7045 | 2620594.7637 | 1240656.8931 | 2620597.7603 | 1240658.2314
95 | 2620621.1035 | 1240694.5968 | 2620624.0863 | 1240682.3518
96 | 2620621.1035 | 1240694.5968 | 2620595.1982 | 1240690.8047
97 | 2620621.1035 | 1240694.5968 | 2620628.5273 | 1240700.0094
98 | 2620530.3328 | 1240646.3486 | 2620498.8484 | 1240643.0035
99 | 2620628.7234 | 1240700.1523 | 2620628.5273 | 1240700.0094
100 | 2620336.9025 | 1240577.0009 | 2620339.1456 | 1240571.0938 | 2620340.3225 | 1240562.4151
101 | 2620342.1008 | 1240549.3013 | 2620340.3225 | 1240562.4151
102 | 2620336.9025 | 1240577.0009 | 2620326.3597 | 1240573.1011
103 | 2620336.9025 | 1240577.0009 | 2620345.8542 | 1240582.1118
104 | 2620342.1008 | 1240549.3013 | 2620345.1621 | 1240542.9411 | 2620352.293 | 1240536.0501 | 2620359.0718 | 1240534.4792
105 | 2620326.3597 | 1240573.1011 | 2620317.6993 | 1240569.8976 | 2620300.4746 | 1240568.7083
106 | 2620350.2407 | 1240584.6162 | 2620345.8542 | 1240582.1118
107 | 2620364.491 | 1240533.2234 | 2620359.0718 | 1240534.4792
108 | 2620294.5451 | 1240568.2989 | 2620300.4746 | 1240568.7083
109 | 2620350.2407 | 1240584.6162 | 2620367.1931 | 1240594.295
110 | 2620294.5451 | 1240568.2989 | 2620285.3912 | 1240567.6669
111 | 2620371.53 | 1240596.7711 | 2620367.1931 | 1240594.295
112 | 2620480.3357 | 1240656.6971 | 2620475.5682 | 1240675.2921
113 | 2620473.1043 | 1240684.9021 | 2620475.5682 | 1240675.2921
114 | 2620259.0727 | 1240565.8497 | 2620264.7386 | 1240566.2409
115 | 2620234.9289 | 1240564.1827 | 2620259.0727 | 1240565.8497
116 | 2620264.7386 | 1240566.2409 | 2620285.3912 | 1240567.6669
117 | 2620630.2968 | 1240701.2995 | 2620628.7234 | 1240700.1523
118 | 2620385.2212 | 1240644.1416 | 2620378.6555 | 1240664.8543
119 | 2620385.2212 | 1240644.1416 | 2620369.4943 | 1240639.8184 | 2620365.5953 | 1240639.1039
120 | 2620365.5953 | 1240639.1039 | 2620338.9617 | 1240634.2235
121 | 2620338.9617 | 1240634.2235 | 2620337.5284 | 1240633.9609
122 | 2620310.0343 | 1240631.3877 | 2620329.8625 | 1240632.5561 | 2620337.5284 | 1240633.9609
123 | 2620294.5679 | 1240630.4677 | 2620310.0343 | 1240631.3877

## bus_geodata
| x | y | coords
0 | 2620556.6846 | 1240538.1777
1 | 2620554.2813 | 1240540.3566
2 | 2620530.1725 | 1240562.2136
3 | 2620526.7691 | 1240565.2992
4 | 2620507.3363 | 1240582.917
5 | 2620629.0508 | 1240486.3853
6 | 2620606.1405 | 1240546.2298
7 | 2620670.8535 | 1240426.9461
8 | 2620590.0963 | 1240554.5846
9 | 2620679.4458 | 1240395.2295
10 | 2620629.7435 | 1240375.8641
11 | 2620189.1352 | 1240557.7149
12 | 2620189.6545 | 1240557.8437
13 | 2620210.9967 | 1240562.5303
14 | 2620209.9458 | 1240512.3963
15 | 2620211.648 | 1240562.5753
16 | 2620233.613 | 1240564.0919
17 | 2620673.2243 | 1240691.5955
18 | 2620672.0021 | 1240691.0586
19 | 2620676.7157 | 1240693.1293
20 | 2620656.3021 | 1240684.1615
21 | 2620718.1785 | 1240711.3444
22 | 2620635.673 | 1240675.0989
23 | 2620877.206 | 1240794.971
24 | 2620862.3114 | 1240775.8695
25 | 2620862.4 | 1240754.4974
26 | 2620852.5998 | 1240748.4482
27 | 2620737.2314 | 1240732.3586
28 | 2620741.0655 | 1240719.8628
29 | 2620737.4818 | 1240758.8747
30 | 2620749.7194 | 1240722.4229
31 | 2620768.5799 | 1240728.0025
32 | 2620726.4716 | 1240694.1823
33 | 2620713.0746 | 1240726.4654
34 | 2620861.8276 | 1240744.9121
35 | 2620831.7857 | 1240743.5927
36 | 2620828.6997 | 1240742.8728
37 | 2620740.6707 | 1240664.7979
38 | 2620808.0424 | 1240738.054
39 | 2620812.7344 | 1240739.1485
40 | 2620793.1933 | 1240734.59
41 | 2620791.2996 | 1240734.1483
42 | 2620768.5848 | 1240728.0039
43 | 2620704.4397 | 1240755.0684
44 | 2620694.7097 | 1240754.8789
45 | 2620675.5851 | 1240973.9193
46 | 2620626.8023 | 1240671.2019
47 | 2620435.3144 | 1240622.0761
48 | 2620419.0983 | 1240616.3959
49 | 2620449.1015 | 1240626.9054
50 | 2620399.8396 | 1240610.1148
51 | 2620427.2018 | 1240605.906
52 | 2620457.3986 | 1240620.8715
53 | 2620456.0843 | 1240629.4877
54 | 2620390.7386 | 1240605.9196
55 | 2620395.2876 | 1240624.374
56 | 2620441.6825 | 1240595.891
57 | 2620484.8145 | 1240600.9336
58 | 2620481.9725 | 1240639.0613
59 | 2620383.7864 | 1240602.7148
60 | 2620392.7808 | 1240630.1508
61 | 2620446.4288 | 1240592.6085
62 | 2620491.9987 | 1240595.7091
63 | 2620484.6075 | 1240640.0357
64 | 2620578.5363 | 1240569.9936
65 | 2620589.8047 | 1240554.9732
66 | 2620587.2666 | 1240585.7034
67 | 2620582.1848 | 1240609.116
68 | 2620560.5933 | 1240628.8238
69 | 2620552.0054 | 1240648.6512
70 | 2620538.939 | 1240708.3895
71 | 2620538.4344 | 1240697.0227
72 | 2620540.6993 | 1240717.2997
73 | 2620544.6007 | 1240675.6982
74 | 2620573.2558 | 1240722.995
75 | 2620543.1352 | 1240728.5079
76 | 2620533.0565 | 1240674.1483
77 | 2620545.6499 | 1240671.8658
78 | 2620573.827 | 1240723.0949
79 | 2620494.0659 | 1240754.2399
80 | 2620518.7623 | 1240672.2291
81 | 2620581.3516 | 1240724.4112
82 | 2620489.5089 | 1240562.8142
83 | 2620475.9312 | 1240572.2046
84 | 2620508.3179 | 1240547.0839
85 | 2620470.9655 | 1240575.6389
86 | 2620521.0028 | 1240535.5957
87 | 2620458.9513 | 1240583.9479
88 | 2620615.8743 | 1240666.3213
89 | 2620597.7603 | 1240658.2314
90 | 2620578.402 | 1240652.2787
91 | 2620624.0863 | 1240682.3518
92 | 2620621.1035 | 1240694.5968
93 | 2620530.3328 | 1240646.3486
94 | 2620595.1982 | 1240690.8047
95 | 2620628.5273 | 1240700.0094
96 | 2620340.3225 | 1240562.4151
97 | 2620336.9025 | 1240577.0009
98 | 2620342.1008 | 1240549.3013
99 | 2620326.3597 | 1240573.1011
100 | 2620345.8542 | 1240582.1118
101 | 2620359.0718 | 1240534.4792
102 | 2620300.4746 | 1240568.7083
103 | 2620350.2407 | 1240584.6162
104 | 2620364.491 | 1240533.2234
105 | 2620294.5451 | 1240568.2989
106 | 2620367.1931 | 1240594.295
107 | 2620498.8484 | 1240643.0035
108 | 2620371.53 | 1240596.7711
109 | 2620475.5682 | 1240675.2921
110 | 2620480.3357 | 1240656.6971
111 | 2620473.1043 | 1240684.9021
112 | 2620259.0727 | 1240565.8497
113 | 2620264.7386 | 1240566.2409
114 | 2620234.9289 | 1240564.1827
115 | 2620285.3912 | 1240567.6669
116 | 2620628.7234 | 1240700.1523
117 | 2620630.2968 | 1240701.2995
118 | 2620385.2212 | 1240644.1416
119 | 2620378.6555 | 1240664.8543
120 | 2620365.5953 | 1240639.1039
121 | 2620338.9617 | 1240634.2235
122 | 2620337.5284 | 1240633.9609
123 | 2620310.0343 | 1240631.3877
124 | 2620294.5679 | 1240630.4677
125 | 2620552.0054 | 1240648.6512

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98736 | -0.088374 | 0.0016055 | 0.00040239
1 | 0.98736 | -0.088321 | 0.0010281 | 0.00025767
2 | 0.98749 | -0.087443 | 0.0009487 | 0.00023777
3 | 0.98751 | -0.087274 | 0.00083479 | 0.00020922
4 | 0.98768 | -0.086087 | 0.0025942 | 0.00065017
5 | 0.99412 | -0.041216 | 0.00078031 | 0.00019556
6 | 0.9947 | -0.037087 | 0 | 0
7 | 0.99353 | -0.045325 | 0 | 0
8 | 0.99488 | -0.035833 | 0.00055972 | 0.00014028
9 | 0.99327 | -0.047194 | 0.002047 | 0.00051303
10 | 0.993 | -0.049105 | 0.0035383 | 0.00088677
11 | 0.97936 | -0.14522 | 0.00094094 | 0.00023582
12 | 0.97936 | -0.14521 | 0.00086204 | 0.00021605
13 | 0.97944 | -0.14457 | 0.00083646 | 0.00020964
14 | 0.97928 | -0.14573 | 0.00099307 | 0.00024889
15 | 0.97945 | -0.14455 | 0.00089202 | 0.00022356
16 | 0.97959 | -0.14351 | 0.0010155 | 0.0002545
17 | 0.98892 | -0.077599 | 0.0014024 | 0.00035148
18 | 0.98899 | -0.077108 | 0.0014436 | 0.00036179
19 | 0.98873 | -0.078947 | 0.0011417 | 0.00028613
20 | 0.98991 | -0.070556 | 0.0016601 | 0.00041606
21 | 0.98653 | -0.094465 | 0 | 0
22 | 0.99119 | -0.061585 | 0.0013379 | 0.00033531
23 | 0.98337 | -0.11693 | 0.0020541 | 0.0005148
24 | 0.98346 | -0.11631 | 0.0021008 | 0.00052652
25 | 0.98359 | -0.11539 | 0 | 0
26 | 0.98366 | -0.1149 | 0 | 0
27 | 0.98568 | -0.10052 | 0.00097913 | 0.00024539
28 | 0.98574 | -0.10013 | 0 | 0
29 | 0.9856 | -0.10109 | 0.0019405 | 0.00048635
30 | 0.98548 | -0.10195 | 0.0014987 | 0.0003756
31 | 0.98496 | -0.10564 | 0.0012019 | 0.00030123
32 | 0.98648 | -0.094854 | 0.0012856 | 0.0003222
33 | 0.98633 | -0.095919 | 0.0012125 | 0.00030388
34 | 0.98364 | -0.11505 | 0.0015259 | 0.00038243
35 | 0.98384 | -0.11364 | 0.0014256 | 0.00035729
36 | 0.98387 | -0.11341 | 0.0013351 | 0.0003346
37 | 0.98645 | -0.095088 | 0.0006981 | 0.00017496
38 | 0.98414 | -0.1115 | 0.0019191 | 0.00048098
39 | 0.98407 | -0.11198 | 0.0013306 | 0.00033347
40 | 0.98439 | -0.10966 | 0.0016811 | 0.00042132
41 | 0.98443 | -0.10939 | 0.0021045 | 0.00052743
42 | 0.98496 | -0.10564 | 0.0015215 | 0.00038132
43 | 0.986 | -0.098262 | 0.0028207 | 0.00070694
44 | 0.98593 | -0.098743 | 0.0010003 | 0.0002507
45 | 0.98472 | -0.10735 | 0.0037961 | 0.00095139
46 | 0.99175 | -0.057603 | 0 | 0
47 | 0.98733 | -0.088519 | 0.0017642 | 0.00044215
48 | 0.98566 | -0.10033 | 0 | 0
49 | 0.98878 | -0.078247 | 0 | 0
50 | 0.9843 | -0.10995 | 0 | 0
51 | 0.98526 | -0.10315 | 0.0021679 | 0.00054332
52 | 0.98857 | -0.079768 | 0.0027005 | 0.00067681
53 | 0.98968 | -0.071923 | 0.002019 | 0.000506
54 | 0.9838 | -0.11351 | 0.0014515 | 0.00036378
55 | 0.98405 | -0.11177 | 0.0011523 | 0.0002888
56 | 0.98479 | -0.10651 | 0.002039 | 0.00051101
57 | 0.98799 | -0.083859 | 0.0030821 | 0.00077244
58 | 0.99309 | -0.048012 | 0.0019694 | 0.00049358
59 | 0.98343 | -0.11612 | 0.0034086 | 0.00085428
60 | 0.98395 | -0.11246 | 0.0016834 | 0.0004219
61 | 0.98465 | -0.10749 | 0.0031489 | 0.00078919
62 | 0.98788 | -0.084652 | 0.0017067 | 0.00042775
63 | 0.99345 | -0.045531 | 0 | 0
64 | 0.99514 | -0.033957 | 0.0023899 | 0.00059897
65 | 0.99488 | -0.035799 | 0.0027833 | 0.00069757
66 | 0.99546 | -0.031728 | 0.0043173 | 0.001082
67 | 0.99604 | -0.02764 | 0.00070237 | 0.00017603
68 | 0.99676 | -0.022577 | 0.0011362 | 0.00028476
69 | 0.99734 | -0.018557 | 0 | 0
70 | 0.99614 | -0.026937 | 0.0013827 | 0.00034653
71 | 0.99632 | -0.02569 | 0.0010191 | 0.00025541
72 | 0.99602 | -0.027782 | 0 | 0
73 | 0.99669 | -0.023091 | 0 | 0
74 | 0.99577 | -0.029566 | 0.0018582 | 0.00046572
75 | 0.99596 | -0.028231 | 0.0012662 | 0.00031734
76 | 0.99663 | -0.023492 | 0.0012053 | 0.00030208
77 | 0.99678 | -0.022489 | 0.0011953 | 0.00029956
78 | 0.99577 | -0.029587 | 0.002164 | 0.00054234
79 | 0.99575 | -0.029686 | 0.0026074 | 0.00065348
80 | 0.99659 | -0.023813 | 0.0022167 | 0.00055555
81 | 0.99575 | -0.02969 | 0.0013402 | 0.00033589
82 | 0.98393 | -0.11259 | 0.0012025 | 0.00030137
83 | 0.98404 | -0.11183 | 0.003963 | 0.00099322
84 | 0.98382 | -0.11343 | 0.0019111 | 0.00047896
85 | 0.98412 | -0.1113 | 0.0029277 | 0.00073375
86 | 0.98378 | -0.11368 | 0.0013936 | 0.00034927
87 | 0.98436 | -0.10958 | 0.0019506 | 0.00048886
88 | 0.99256 | -0.051928 | 0.0016074 | 0.00040286
89 | 0.99395 | -0.04222 | 0.00098751 | 0.00024749
90 | 0.99539 | -0.032096 | 0.0011515 | 0.0002886
91 | 0.99165 | -0.058335 | 0.00089695 | 0.0002248
92 | 0.99155 | -0.059024 | 0 | 0
93 | 1 | 0 | -0.18655 | -0.046826
94 | 0.99149 | -0.059501 | 0.0017999 | 0.00045111
95 | 0.99151 | -0.059358 | 0.0010222 | 0.00025619
96 | 0.98124 | -0.13173 | 0.00093373 | 0.00023401
97 | 0.98136 | -0.13088 | 0 | 0
98 | 0.98115 | -0.13236 | 0 | 0
99 | 0.98108 | -0.1329 | 0.0016548 | 0.00041472
100 | 0.9817 | -0.12844 | 0.0010615 | 0.00026604
101 | 0.981 | -0.13348 | 0.0020979 | 0.00052577
102 | 0.98047 | -0.13723 | 0.0029281 | 0.00073384
103 | 0.98188 | -0.12718 | 0.0029311 | 0.00073461
104 | 0.98098 | -0.13362 | 0.0024392 | 0.00061132
105 | 0.98036 | -0.13802 | 0.0016885 | 0.00042319
106 | 0.98264 | -0.12176 | 0.0015377 | 0.00038538
107 | 0.99548 | -0.031306 | 0.0017857 | 0.00044753
108 | 0.98285 | -0.12029 | 0.0012439 | 0.00031175
109 | 0.99302 | -0.048502 | 0.002429 | 0.00060876
110 | 0.99321 | -0.047193 | 0.0028104 | 0.00070435
111 | 0.99296 | -0.048935 | 0.0043094 | 0.00108
112 | 0.97985 | -0.14168 | 0.0012566 | 0.00031492
113 | 0.97992 | -0.14119 | 0.0015775 | 0.00039536
114 | 0.9796 | -0.14344 | 0.0014327 | 0.00035906
115 | 0.98021 | -0.13908 | 0.0012948 | 0.00032451
116 | 0.9915 | -0.059364 | 0.00093969 | 0.00023551
117 | 0.9915 | -0.059396 | 0.0016189 | 0.00040574
118 | 0.98374 | -0.11393 | 0 | 0
119 | 0.98367 | -0.11442 | 0.0022076 | 0.00055327
120 | 0.98355 | -0.11534 | 0.001126 | 0.0002822
121 | 0.98333 | -0.1169 | 0.0011616 | 0.00029112
122 | 0.98332 | -0.11697 | 0.0013828 | 0.00034656
123 | 0.98319 | -0.11784 | 0.0019916 | 0.00049914
124 | 0.98317 | -0.11801 | 0.0010628 | 0.00026635
125 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0016055 | -0.00040239 | 0.0016055 | 0.00040235 | 1.1851e-08 | -3.6931e-08 | 0.0024197 | 0.0024196 | 0.0024197 | 0.98736 | -0.088374 | 0.98736 | -0.088321 | 0.89617
1 | -0.0026337 | -0.00066002 | 0.002634 | 0.00065973 | 3.1988e-07 | -2.9322e-07 | 0.0039691 | 0.0039689 | 0.0039691 | 0.98736 | -0.088321 | 0.98749 | -0.087443 | 1.47
2 | -0.0035827 | -0.0008975 | 0.0035828 | 0.00089747 | 8.3544e-08 | -2.6639e-08 | 0.0053985 | 0.0053985 | 0.0053985 | 0.98749 | -0.087443 | 0.98751 | -0.087274 | 1.9995
3 | -0.0044176 | -0.0011067 | 0.0044183 | 0.0011066 | 7.2519e-07 | -5.6715e-08 | 0.0066564 | 0.0066563 | 0.0066564 | 0.98751 | -0.087274 | 0.98768 | -0.086087 | 2.4653
4 | -0.0070125 | -0.0017568 | 0.0070139 | 0.0017571 | 1.3929e-06 | 2.7971e-07 | 0.010565 | 0.010565 | 0.010565 | 0.98768 | -0.086087 | 0.98788 | -0.084652 | 3.9128
5 | -0.0063711 | -0.0015954 | 0.0063748 | 0.001596 | 3.636e-06 | 5.6717e-07 | 0.009536 | 0.0095357 | 0.009536 | 0.99412 | -0.041216 | 0.9947 | -0.037087 | 3.5319
6 | 0.0055908 | 0.0013999 | -0.0055877 | -0.0013996 | 3.1753e-06 | 2.7967e-07 | 0.008368 | 0.0083684 | 0.0083684 | 0.99412 | -0.041216 | 0.99353 | -0.045325 | 3.0994
7 | -0.0063748 | -0.001596 | 0.0063759 | 0.0015962 | 1.1041e-06 | 1.7201e-07 | 0.0095357 | 0.0095356 | 0.0095357 | 0.9947 | -0.037087 | 0.99488 | -0.035833 | 3.5317
8 | 0.0055877 | 0.0013996 | -0.0055862 | -0.0013995 | 1.4436e-06 | 1.2754e-07 | 0.0083684 | 0.0083685 | 0.0083685 | 0.99353 | -0.045325 | 0.99327 | -0.047194 | 3.0995
9 | -0.0069356 | -0.0017365 | 0.0069356 | 0.0017365 | 3.2617e-08 | 6.2364e-09 | 0.010373 | 0.010373 | 0.010373 | 0.99488 | -0.035833 | 0.99488 | -0.035799 | 3.8418
10 | 0.0035392 | 0.00088644 | -0.0035383 | -0.00088677 | 9.3569e-07 | -3.3035e-07 | 0.0053019 | 0.0053021 | 0.0053021 | 0.99327 | -0.047194 | 0.993 | -0.049105 | 1.9638
11 | -0.00094094 | -0.00023582 | 0.00094094 | 0.00023582 | 6.8223e-10 | -6.4698e-09 | 0.0014296 | 0.0014296 | 0.0014296 | 0.97936 | -0.14522 | 0.97936 | -0.14521 | 0.5295
12 | -0.0027961 | -0.00070015 | 0.0027964 | 0.00069997 | 2.4655e-07 | -1.807e-07 | 0.0042481 | 0.004248 | 0.0042481 | 0.97936 | -0.14521 | 0.97944 | -0.14457 | 1.5734
13 | 0.00099314 | 0.00024829 | -0.00099307 | -0.00024889 | 7.0706e-08 | -5.9905e-07 | 0.0015087 | 0.001509 | 0.001509 | 0.97936 | -0.14521 | 0.97928 | -0.14573 | 0.55887
14 | -0.0036328 | -0.00090961 | 0.0036328 | 0.0009096 | 1.2406e-08 | -3.4439e-09 | 0.0055188 | 0.0055188 | 0.0055188 | 0.97944 | -0.14457 | 0.97945 | -0.14455 | 2.044
15 | -0.0045249 | -0.0011332 | 0.0045255 | 0.0011331 | 6.4918e-07 | -2.7457e-08 | 0.006874 | 0.0068739 | 0.006874 | 0.97945 | -0.14455 | 0.97959 | -0.14351 | 2.5459
16 | -0.005541 | -0.0013876 | 0.005541 | 0.0013876 | 5.8305e-08 | 5.8188e-09 | 0.0084165 | 0.0084165 | 0.0084165 | 0.97959 | -0.14351 | 0.9796 | -0.14344 | 3.1172
17 | -0.036112 | -0.0090608 | 0.036114 | 0.0090617 | 2.4598e-06 | 9.2896e-07 | 0.054341 | 0.054341 | 0.054341 | 0.98892 | -0.077599 | 0.98899 | -0.077108 | 20.1264
18 | 0.03471 | 0.0087093 | -0.034703 | -0.0087068 | 6.4917e-06 | 2.4479e-06 | 0.052231 | 0.052231 | 0.052231 | 0.98892 | -0.077599 | 0.98873 | -0.078947 | 19.3448
19 | -0.037558 | -0.0094235 | 0.037592 | 0.0094364 | 3.4174e-05 | 1.2924e-05 | 0.056513 | 0.056513 | 0.056513 | 0.98899 | -0.077108 | 0.98991 | -0.070556 | 20.9308
20 | 0.033561 | 0.0084207 | -0.033489 | -0.0083936 | 7.2105e-05 | 2.7153e-05 | 0.050513 | 0.050513 | 0.050513 | 0.98873 | -0.078947 | 0.98653 | -0.094465 | 18.7085
21 | -0.039252 | -0.0098525 | 0.039301 | 0.009871 | 4.8957e-05 | 1.854e-05 | 0.059009 | 0.059008 | 0.059009 | 0.98991 | -0.070556 | 0.99119 | -0.061585 | 21.855
22 | 0.0019838 | 0.00049655 | -0.0019837 | -0.00049675 | 1.0648e-07 | -2.0241e-07 | 0.002992 | 0.0029921 | 0.0029921 | 0.98653 | -0.094465 | 0.98648 | -0.094854 | 1.1082
23 | 0.0088387 | 0.0022129 | -0.0088369 | -0.0022124 | 1.7747e-06 | 4.7829e-07 | 0.013331 | 0.013331 | 0.013331 | 0.98653 | -0.094465 | 0.98633 | -0.095919 | 4.9374
24 | 0.022667 | 0.0056841 | -0.022649 | -0.0056776 | 1.7768e-05 | 6.523e-06 | 0.03419 | 0.03419 | 0.03419 | 0.98653 | -0.094465 | 0.98574 | -0.10013 | 12.6631
25 | -0.040639 | -0.010206 | 0.040662 | 0.010215 | 2.2509e-05 | 8.5325e-06 | 0.061017 | 0.061017 | 0.061017 | 0.99119 | -0.061585 | 0.99175 | -0.057603 | 22.5989
26 | -0.0020541 | -0.0005148 | 0.0020543 | 0.0005145 | 1.7703e-07 | -3.0453e-07 | 0.0031082 | 0.003108 | 0.0031082 | 0.98337 | -0.11693 | 0.98346 | -0.11631 | 1.1512
27 | -0.0041551 | -0.001041 | 0.0041556 | 0.0010409 | 5.2906e-07 | -6.8762e-08 | 0.0062867 | 0.0062866 | 0.0062867 | 0.98346 | -0.11631 | 0.98359 | -0.11539 | 2.3284
28 | -0.0041556 | -0.0010409 | 0.0041559 | 0.0010409 | 2.8341e-07 | -3.6867e-08 | 0.0062866 | 0.0062865 | 0.0062866 | 0.98359 | -0.11539 | 0.98366 | -0.1149 | 2.3284
29 | -0.0056818 | -0.0014232 | 0.0056828 | 0.0014233 | 9.8519e-07 | 1.0756e-07 | 0.0085948 | 0.0085947 | 0.0085948 | 0.98366 | -0.1149 | 0.98384 | -0.11364 | 3.1833
30 | 0.0015259 | 0.00038232 | -0.0015259 | -0.00038243 | 3.2857e-08 | -1.128e-07 | 0.0023083 | 0.0023083 | 0.0023083 | 0.98366 | -0.1149 | 0.98364 | -0.11505 | 0.85494
31 | -0.0029198 | -0.00073143 | 0.00292 | 0.00073133 | 1.5851e-07 | -1.057e-07 | 0.0044077 | 0.0044077 | 0.0044077 | 0.98568 | -0.10052 | 0.98574 | -0.10013 | 1.6325
32 | 0.0019407 | 0.00048604 | -0.0019405 | -0.00048635 | 1.5361e-07 | -3.0646e-07 | 0.0029296 | 0.0029297 | 0.0029297 | 0.98568 | -0.10052 | 0.9856 | -0.10109 | 1.0851
33 | 0.019729 | 0.0049463 | -0.019724 | -0.0049445 | 4.9951e-06 | 1.8062e-06 | 0.029783 | 0.029783 | 0.029783 | 0.98574 | -0.10013 | 0.98548 | -0.10195 | 11.0306
34 | 0.018225 | 0.0045689 | -0.018216 | -0.0045655 | 9.295e-06 | 3.3245e-06 | 0.02752 | 0.02752 | 0.02752 | 0.98548 | -0.10195 | 0.98496 | -0.10564 | 10.1926
35 | 0.017014 | 0.0042643 | -0.017014 | -0.0042643 | 2.1377e-09 | 7.5057e-10 | 0.025704 | 0.025704 | 0.025704 | 0.98496 | -0.10564 | 0.98496 | -0.10564 | 9.5201
36 | 0.00069813 | 0.00017455 | -0.0006981 | -0.00017496 | 2.258e-08 | -4.0795e-07 | 0.0010529 | 0.0010531 | 0.0010531 | 0.98648 | -0.094854 | 0.98645 | -0.095088 | 0.39002
37 | 0.0076244 | 0.0019085 | -0.0076219 | -0.001908 | 2.4666e-06 | 5.6746e-07 | 0.011502 | 0.011502 | 0.011502 | 0.98633 | -0.095919 | 0.986 | -0.098262 | 4.2599
38 | -0.0071084 | -0.0017806 | 0.0071087 | 0.0017807 | 2.2854e-07 | 4.7661e-08 | 0.010751 | 0.010751 | 0.010751 | 0.98384 | -0.11364 | 0.98387 | -0.11341 | 3.9818
39 | -0.0084437 | -0.0021153 | 0.0084454 | 0.0021157 | 1.6682e-06 | 4.3339e-07 | 0.01277 | 0.01277 | 0.01277 | 0.98387 | -0.11341 | 0.98407 | -0.11198 | 4.7297
40 | 0.0097766 | 0.0024494 | -0.0097759 | -0.0024492 | 6.5692e-07 | 1.9145e-07 | 0.014782 | 0.014782 | 0.014782 | 0.98414 | -0.1115 | 0.98407 | -0.11198 | 5.4748
41 | -0.011696 | -0.0029303 | 0.011699 | 0.0029313 | 2.9753e-06 | 9.5056e-07 | 0.017684 | 0.017684 | 0.017684 | 0.98414 | -0.1115 | 0.98439 | -0.10966 | 6.5495
42 | -0.01338 | -0.0033526 | 0.01338 | 0.0033528 | 4.9634e-07 | 1.6618e-07 | 0.020225 | 0.020225 | 0.020225 | 0.98439 | -0.10966 | 0.98443 | -0.10939 | 7.4906
43 | -0.015485 | -0.0038802 | 0.015493 | 0.003883 | 8.0472e-06 | 2.7956e-06 | 0.023406 | 0.023406 | 0.023406 | 0.98443 | -0.10939 | 0.98496 | -0.10564 | 8.6688
44 | 0.0048012 | 0.001201 | -0.0048009 | -0.001201 | 3.1875e-07 | -1.5199e-09 | 0.0072449 | 0.007245 | 0.007245 | 0.986 | -0.098262 | 0.98593 | -0.098743 | 2.6833
45 | 0.0038006 | 0.00095033 | -0.0037961 | -0.00095139 | 4.5138e-06 | -1.0645e-06 | 0.0057353 | 0.0057363 | 0.0057363 | 0.98593 | -0.098743 | 0.98472 | -0.10735 | 2.1245
46 | 0.0062792 | 0.0015731 | -0.0062785 | -0.001573 | 6.3557e-07 | 9.6384e-08 | 0.009421 | 0.009421 | 0.009421 | 0.99175 | -0.057603 | 0.99165 | -0.058335 | 3.4893
47 | -0.046941 | -0.011788 | 0.046978 | 0.011802 | 3.7054e-05 | 1.4097e-05 | 0.070438 | 0.070438 | 0.070438 | 0.99175 | -0.057603 | 0.99256 | -0.051928 | 26.0881
48 | 0.067268 | 0.016893 | -0.067158 | -0.016851 | 0.00011022 | 4.2174e-05 | 0.10139 | 0.10139 | 0.10139 | 0.98733 | -0.088519 | 0.98566 | -0.10033 | 37.5528
49 | -0.069032 | -0.017335 | 0.069131 | 0.017373 | 9.8693e-05 | 3.7772e-05 | 0.10405 | 0.10405 | 0.10405 | 0.98733 | -0.088519 | 0.98878 | -0.078247 | 38.5375
50 | 0.046426 | 0.011653 | -0.046364 | -0.01163 | 6.194e-05 | 2.3566e-05 | 0.070094 | 0.070095 | 0.070095 | 0.98566 | -0.10033 | 0.9843 | -0.10995 | 25.961
51 | 0.020731 | 0.0051977 | -0.020723 | -0.0051948 | 8.1023e-06 | 2.9474e-06 | 0.031298 | 0.031298 | 0.031298 | 0.98566 | -0.10033 | 0.98526 | -0.10315 | 11.5919
52 | 0.014514 | 0.0036375 | -0.014511 | -0.0036365 | 3.054e-06 | 1.0431e-06 | 0.021842 | 0.021842 | 0.021842 | 0.98878 | -0.078247 | 0.98857 | -0.079768 | 8.0896
53 | -0.083645 | -0.021011 | 0.083718 | 0.021039 | 7.3629e-05 | 2.8223e-05 | 0.12589 | 0.12589 | 0.12589 | 0.98878 | -0.078247 | 0.98968 | -0.071923 | 46.627
54 | 0.034587 | 0.0086789 | -0.03457 | -0.0086725 | 1.7099e-05 | 6.4492e-06 | 0.052291 | 0.052291 | 0.052291 | 0.9843 | -0.10995 | 0.9838 | -0.11351 | 19.3671
55 | 0.011777 | 0.0029509 | -0.011774 | -0.0029499 | 2.9626e-06 | 9.4913e-07 | 0.017803 | 0.017804 | 0.017804 | 0.9843 | -0.10995 | 0.98405 | -0.11177 | 6.5939
56 | 0.018555 | 0.0046514 | -0.018547 | -0.0046484 | 8.6282e-06 | 3.0944e-06 | 0.028024 | 0.028024 | 0.028024 | 0.98526 | -0.10315 | 0.98479 | -0.10651 | 10.3793
57 | 0.01181 | 0.0029597 | -0.011804 | -0.0029575 | 6.6849e-06 | 2.1368e-06 | 0.017777 | 0.017777 | 0.017777 | 0.98857 | -0.079768 | 0.98799 | -0.083859 | 6.5842
58 | -0.085737 | -0.021545 | 0.086023 | 0.021655 | 0.0002863 | 0.00010976 | 0.12893 | 0.12893 | 0.12893 | 0.98968 | -0.071923 | 0.99309 | -0.048012 | 47.7513
59 | 0.033119 | 0.0083087 | -0.033107 | -0.0083042 | 1.1988e-05 | 4.5136e-06 | 0.050096 | 0.050096 | 0.050096 | 0.9838 | -0.11351 | 0.98343 | -0.11612 | 18.554
60 | 0.010622 | 0.0026611 | -0.010621 | -0.0026608 | 1.0136e-06 | 3.0987e-07 | 0.016061 | 0.016061 | 0.016061 | 0.98405 | -0.11177 | 0.98395 | -0.11246 | 5.9485
61 | 0.016508 | 0.0041373 | -0.016505 | -0.0041366 | 2.2404e-06 | 7.8827e-07 | 0.024943 | 0.024943 | 0.024943 | 0.98479 | -0.10651 | 0.98465 | -0.10749 | 9.2382
62 | 0.0087216 | 0.0021851 | -0.0087206 | -0.0021848 | 9.5637e-07 | 2.5409e-07 | 0.013135 | 0.013135 | 0.013135 | 0.98799 | -0.083859 | 0.98788 | -0.084652 | 4.8649
63 | -0.087993 | -0.022148 | 0.088023 | 0.02216 | 3.049e-05 | 1.1691e-05 | 0.13188 | 0.13188 | 0.13188 | 0.99309 | -0.048012 | 0.99345 | -0.045531 | 48.8442
64 | 0.029698 | 0.0074499 | -0.029681 | -0.0074435 | 1.7176e-05 | 6.4334e-06 | 0.044938 | 0.044938 | 0.044938 | 0.98343 | -0.11612 | 0.98285 | -0.12029 | 16.6438
65 | 0.0089372 | 0.0022389 | -0.0089354 | -0.0022384 | 1.8208e-06 | 4.9744e-07 | 0.013515 | 0.013515 | 0.013515 | 0.98395 | -0.11246 | 0.98374 | -0.11393 | 5.0057
66 | 0.013357 | 0.0033474 | -0.013353 | -0.0033461 | 3.8708e-06 | 1.2952e-06 | 0.020185 | 0.020185 | 0.020185 | 0.98465 | -0.10749 | 0.98436 | -0.10958 | 7.4758
67 | -0.097576 | -0.024554 | 0.09777 | 0.024628 | 0.00019411 | 7.4469e-05 | 0.14619 | 0.14619 | 0.14619 | 0.99345 | -0.045531 | 0.99548 | -0.031306 | 54.1434
68 | 0.0095524 | 0.002394 | -0.0095502 | -0.0023933 | 2.1972e-06 | 6.2243e-07 | 0.014308 | 0.014308 | 0.014308 | 0.99345 | -0.045531 | 0.99321 | -0.047193 | 5.2992
69 | 0.0097214 | 0.0024347 | -0.009719 | -0.002434 | 2.4757e-06 | 7.0828e-07 | 0.014536 | 0.014536 | 0.014536 | 0.99514 | -0.033957 | 0.99488 | -0.035799 | 5.3836
70 | -0.012111 | -0.0030337 | 0.012115 | 0.0030349 | 3.734e-06 | 1.199e-06 | 0.018109 | 0.018109 | 0.018109 | 0.99514 | -0.033957 | 0.99546 | -0.031728 | 6.7071
71 | -0.016432 | -0.0041169 | 0.016442 | 0.0041202 | 9.2974e-06 | 3.2547e-06 | 0.024563 | 0.024562 | 0.024563 | 0.99546 | -0.031728 | 0.99604 | -0.02764 | 9.0972
72 | -0.017144 | -0.0042962 | 0.017156 | 0.0043004 | 1.2021e-05 | 4.2408e-06 | 0.025612 | 0.025612 | 0.025612 | 0.99604 | -0.02764 | 0.99676 | -0.022577 | 9.4858
73 | -0.018292 | -0.0045852 | 0.018302 | 0.0045888 | 1.019e-05 | 3.6336e-06 | 0.027308 | 0.027308 | 0.027308 | 0.99676 | -0.022577 | 0.99734 | -0.018557 | 10.114
74 | -0.085533 | -0.021497 | 0.085755 | 0.021582 | 0.00022156 | 8.4929e-05 | 0.12764 | 0.12764 | 0.12764 | 0.99734 | -0.018557 | 1 | 0 | 47.2728
75 | 0.016275 | 0.0040788 | -0.016266 | -0.0040757 | 8.8553e-06 | 3.092e-06 | 0.024282 | 0.024282 | 0.024282 | 0.99734 | -0.018557 | 0.99678 | -0.022489 | 8.9933
76 | 0.050956 | 0.012829 | -0.05086 | -0.012793 | 9.6203e-05 | 3.6654e-05 | 0.076047 | 0.076047 | 0.076047 | 0.99734 | -0.018557 | 0.99539 | -0.032096 | 28.1656
77 | -0.010622 | -0.002661 | 0.010624 | 0.0026616 | 1.8323e-06 | 5.5284e-07 | 0.015866 | 0.015866 | 0.015866 | 0.99614 | -0.026937 | 0.99632 | -0.02569 | 5.8765
78 | 0.0092392 | 0.0023145 | -0.0092382 | -0.0023142 | 1.0795e-06 | 2.9695e-07 | 0.013801 | 0.013801 | 0.013801 | 0.99614 | -0.026937 | 0.99602 | -0.027782 | 5.1115
79 | -0.011643 | -0.002917 | 0.011647 | 0.0029183 | 4.1881e-06 | 1.3216e-06 | 0.017388 | 0.017388 | 0.017388 | 0.99632 | -0.02569 | 0.99669 | -0.023091 | 6.4402
80 | 0.0053638 | 0.0013439 | -0.0053625 | -0.0013439 | 1.3243e-06 | 7.9287e-08 | 0.0080131 | 0.0080133 | 0.0080133 | 0.99602 | -0.027782 | 0.99577 | -0.029566 | 2.9679
81 | 0.0038744 | 0.00097025 | -0.0038742 | -0.0009703 | 2.4014e-07 | -5.7142e-08 | 0.0057879 | 0.005788 | 0.005788 | 0.99602 | -0.027782 | 0.99596 | -0.028231 | 2.1437
82 | 0.0034223 | 0.00085741 | -0.0034221 | -0.00085749 | 1.8973e-07 | -7.8817e-08 | 0.0051092 | 0.0051093 | 0.0051093 | 0.99669 | -0.023091 | 0.99663 | -0.023492 | 1.8923
83 | -0.015069 | -0.0037757 | 0.015071 | 0.0037761 | 1.2549e-06 | 4.3087e-07 | 0.022498 | 0.022498 | 0.022498 | 0.99669 | -0.023091 | 0.99678 | -0.022489 | 8.3324
84 | 0.0035042 | 0.00087814 | -0.0035042 | -0.00087814 | 9.9218e-09 | -3.7272e-09 | 0.0052364 | 0.0052364 | 0.0052364 | 0.99577 | -0.029566 | 0.99577 | -0.029587 | 1.9394
85 | 0.0026079 | 0.00065296 | -0.0026074 | -0.00065348 | 5.2487e-07 | -5.1901e-07 | 0.0038962 | 0.0038964 | 0.0038964 | 0.99596 | -0.028231 | 0.99575 | -0.029686 | 1.4431
86 | 0.0022168 | 0.0005554 | -0.0022167 | -0.00055555 | 9.8585e-08 | -1.5002e-07 | 0.0033097 | 0.0033098 | 0.0033098 | 0.99663 | -0.023492 | 0.99659 | -0.023813 | 1.2258
87 | 0.0013403 | 0.0003358 | -0.0013402 | -0.00033589 | 1.912e-08 | -9.2014e-08 | 0.0020028 | 0.0020028 | 0.0020028 | 0.99577 | -0.029587 | 0.99575 | -0.02969 | 0.74178
88 | -0.0045076 | -0.0011292 | 0.0045081 | 0.0011292 | 4.7868e-07 | -2.5594e-08 | 0.0068167 | 0.0068167 | 0.0068167 | 0.98393 | -0.11259 | 0.98404 | -0.11183 | 2.5247
89 | 0.0033051 | 0.00082787 | -0.0033047 | -0.00082803 | 3.8293e-07 | -1.6467e-07 | 0.0049982 | 0.0049983 | 0.0049983 | 0.98393 | -0.11259 | 0.98382 | -0.11343 | 1.8512
90 | -0.0084711 | -0.0021224 | 0.0084717 | 0.0021226 | 6.1815e-07 | 1.6104e-07 | 0.012809 | 0.012809 | 0.012809 | 0.98404 | -0.11183 | 0.98412 | -0.1113 | 4.7442
91 | 0.0013937 | 0.00034908 | -0.0013936 | -0.00034927 | 4.7449e-08 | -1.9906e-07 | 0.0021078 | 0.0021079 | 0.0021079 | 0.98382 | -0.11343 | 0.98378 | -0.11368 | 0.78071
92 | -0.011399 | -0.0028564 | 0.011402 | 0.0028572 | 2.7079e-06 | 8.5587e-07 | 0.017236 | 0.017236 | 0.017236 | 0.98412 | -0.1113 | 0.98436 | -0.10958 | 6.3837
93 | -0.048585 | -0.012205 | 0.048651 | 0.01223 | 6.5693e-05 | 2.501e-05 | 0.072848 | 0.072847 | 0.072848 | 0.99256 | -0.051928 | 0.99395 | -0.04222 | 26.9806
94 | -0.049639 | -0.012477 | 0.049709 | 0.012504 | 7.0081e-05 | 2.669e-05 | 0.074326 | 0.074326 | 0.074326 | 0.99395 | -0.04222 | 0.99539 | -0.032096 | 27.5281
95 | 0.0053816 | 0.0013482 | -0.0053811 | -0.0013482 | 5.1281e-07 | 3.4659e-08 | 0.0080751 | 0.0080752 | 0.0080752 | 0.99165 | -0.058335 | 0.99155 | -0.059024 | 2.9908
96 | 0.0018001 | 0.00045082 | -0.0017999 | -0.00045111 | 1.1887e-07 | -2.9099e-07 | 0.0027012 | 0.0027014 | 0.0027014 | 0.99155 | -0.059024 | 0.99149 | -0.059501 | 1.0005
97 | 0.003581 | 0.00089736 | -0.0035808 | -0.00089741 | 1.6556e-07 | -5.4821e-08 | 0.0053739 | 0.005374 | 0.005374 | 0.99155 | -0.059024 | 0.99151 | -0.059358 | 1.9904
98 | 0.099993 | 0.025244 | -0.099556 | -0.025076 | 0.00043777 | 0.00016796 | 0.14886 | 0.14886 | 0.14886 | 1 | 0 | 0.99548 | -0.031306 | 55.132
99 | 0.0025586 | 0.00064122 | -0.0025586 | -0.00064123 | 2.2327e-09 | -2.271e-09 | 0.0038399 | 0.0038399 | 0.0038399 | 0.99151 | -0.059358 | 0.9915 | -0.059364 | 1.4222
100 | -0.0054719 | -0.001371 | 0.0054726 | 0.0013711 | 6.4776e-07 | 5.8671e-08 | 0.0082978 | 0.0082977 | 0.0082978 | 0.98124 | -0.13173 | 0.98136 | -0.13088 | 3.0733
101 | 0.0045382 | 0.001137 | -0.0045378 | -0.001137 | 3.911e-07 | -1.6729e-08 | 0.0068818 | 0.0068819 | 0.0068819 | 0.98124 | -0.13173 | 0.98115 | -0.13236 | 2.5489
102 | 0.017396 | 0.0043606 | -0.017392 | -0.0043589 | 4.8806e-06 | 1.7352e-06 | 0.026378 | 0.026378 | 0.026378 | 0.98136 | -0.13088 | 0.98108 | -0.1329 | 9.7697
103 | -0.022869 | -0.0057316 | 0.022877 | 0.0057345 | 7.7341e-06 | 2.8444e-06 | 0.034676 | 0.034676 | 0.034676 | 0.98136 | -0.13088 | 0.9817 | -0.12844 | 12.8429
104 | 0.0045378 | 0.001137 | -0.0045371 | -0.001137 | 7.0732e-07 | -3.0173e-08 | 0.0068819 | 0.006882 | 0.006882 | 0.98115 | -0.13236 | 0.981 | -0.13348 | 2.5489
105 | 0.015737 | 0.0039441 | -0.015727 | -0.0039408 | 9.4204e-06 | 3.2888e-06 | 0.023868 | 0.023868 | 0.023868 | 0.98108 | -0.1329 | 0.98047 | -0.13723 | 8.8401
106 | -0.023938 | -0.0060005 | 0.023942 | 0.0060021 | 4.1498e-06 | 1.5322e-06 | 0.036285 | 0.036285 | 0.036285 | 0.9817 | -0.12844 | 0.98188 | -0.12718 | 13.4388
107 | 0.0024392 | 0.00061126 | -0.0024392 | -0.00061132 | 4.7518e-08 | -5.1955e-08 | 0.0036999 | 0.0036999 | 0.0036999 | 0.981 | -0.13348 | 0.98098 | -0.13362 | 1.3703
108 | 0.012799 | 0.003207 | -0.012798 | -0.0032065 | 1.3994e-06 | 4.6328e-07 | 0.019425 | 0.019425 | 0.019425 | 0.98047 | -0.13723 | 0.98036 | -0.13802 | 7.1943
109 | -0.026874 | -0.0067367 | 0.026894 | 0.0067442 | 2.0204e-05 | 7.5237e-06 | 0.040727 | 0.040727 | 0.040727 | 0.98188 | -0.12718 | 0.98264 | -0.12176 | 15.084
110 | 0.011109 | 0.0027833 | -0.011108 | -0.0027828 | 1.6279e-06 | 5.1043e-07 | 0.016862 | 0.016862 | 0.016862 | 0.98036 | -0.13802 | 0.98021 | -0.13908 | 6.2451
111 | -0.028431 | -0.0071296 | 0.028437 | 0.0071317 | 5.7768e-06 | 2.1586e-06 | 0.043055 | 0.043055 | 0.043055 | 0.98264 | -0.12176 | 0.98285 | -0.12029 | 15.9464
112 | -0.0067386 | -0.0016888 | 0.0067398 | 0.001689 | 1.2213e-06 | 2.2136e-07 | 0.010098 | 0.010097 | 0.010098 | 0.99302 | -0.048502 | 0.99321 | -0.047193 | 3.7398
113 | 0.0043096 | 0.00108 | -0.0043094 | -0.00108 | 2.5817e-07 | -2.904e-08 | 0.0064578 | 0.0064579 | 0.0064579 | 0.99302 | -0.048502 | 0.99296 | -0.048935 | 2.3918
114 | -0.008232 | -0.002062 | 0.0082325 | 0.0020621 | 5.538e-07 | 1.4146e-07 | 0.012501 | 0.012501 | 0.012501 | 0.97985 | -0.14168 | 0.97992 | -0.14119 | 4.6299
115 | 0.0069754 | 0.0017471 | -0.0069737 | -0.0017467 | 1.6945e-06 | 3.4695e-07 | 0.010593 | 0.010593 | 0.010593 | 0.97985 | -0.14168 | 0.9796 | -0.14344 | 3.9232
116 | -0.00981 | -0.0024575 | 0.0098129 | 0.0024583 | 2.8664e-06 | 8.4161e-07 | 0.014896 | 0.014896 | 0.014896 | 0.97992 | -0.14119 | 0.98021 | -0.13908 | 5.5171
117 | 0.0016189 | 0.00040572 | -0.0016189 | -0.00040574 | 7.1726e-09 | -2.2355e-08 | 0.0024296 | 0.0024296 | 0.0024296 | 0.9915 | -0.059364 | 0.9915 | -0.059396 | 0.89986
118 | 0.0022077 | 0.00055305 | -0.0022076 | -0.00055327 | 1.5117e-07 | -2.1766e-07 | 0.0033393 | 0.0033394 | 0.0033394 | 0.98374 | -0.11393 | 0.98367 | -0.11442 | 1.2368
119 | 0.0067276 | 0.0016853 | -0.0067263 | -0.0016851 | 1.31e-06 | 2.4651e-07 | 0.010176 | 0.010176 | 0.010176 | 0.98374 | -0.11393 | 0.98355 | -0.11534 | 3.7689
120 | 0.0056004 | 0.0014029 | -0.0055991 | -0.0014028 | 1.2129e-06 | 1.2294e-07 | 0.0084726 | 0.0084727 | 0.0084727 | 0.98355 | -0.11534 | 0.98333 | -0.1169 | 3.138
121 | 0.0044376 | 0.0011117 | -0.0044375 | -0.0011117 | 4.0998e-08 | -2.7153e-09 | 0.006715 | 0.006715 | 0.006715 | 0.98333 | -0.1169 | 0.98332 | -0.11697 | 2.487
122 | 0.0030547 | 0.0007651 | -0.0030544 | -0.0007653 | 3.6875e-07 | -2.0895e-07 | 0.0046224 | 0.0046226 | 0.0046226 | 0.98332 | -0.11697 | 0.98319 | -0.11784 | 1.7121
123 | 0.0010628 | 0.00026617 | -0.0010628 | -0.00026635 | 2.4938e-08 | -1.8632e-07 | 0.0016084 | 0.0016085 | 0.0016085 | 0.98319 | -0.11784 | 0.98317 | -0.11801 | 0.59573

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18947 | 0.047558

## res_load
| p_mw | q_mvar
0 | 0.0016055 | 0.00040239
1 | 0.0010281 | 0.00025767
2 | 0.0009487 | 0.00023777
3 | 0.00083479 | 0.00020922
4 | 0.0025942 | 0.00065017
5 | 0.00078031 | 0.00019556
6 | 0.00055972 | 0.00014028
7 | 0.002047 | 0.00051303
8 | 0.0035383 | 0.00088677
9 | 0.00094094 | 0.00023582
10 | 0.00086204 | 0.00021605
11 | 0.00083646 | 0.00020964
12 | 0.00099307 | 0.00024889
13 | 0.00089202 | 0.00022356
14 | 0.0010155 | 0.0002545
15 | 0.0014024 | 0.00035148
16 | 0.0014436 | 0.00036179
17 | 0.0011417 | 0.00028613
18 | 0.0016601 | 0.00041606
19 | 0.0013379 | 0.00033531
20 | 0.0020541 | 0.0005148
21 | 0.0021008 | 0.00052652
22 | 0.00097913 | 0.00024539
23 | 0.0019405 | 0.00048635
24 | 0.0014987 | 0.0003756
25 | 0.0012019 | 0.00030123
26 | 0.0012856 | 0.0003222
27 | 0.0012125 | 0.00030388
28 | 0.0015259 | 0.00038243
29 | 0.0014256 | 0.00035729
30 | 0.0013351 | 0.0003346
31 | 0.0006981 | 0.00017496
32 | 0.0019191 | 0.00048098
33 | 0.0013306 | 0.00033347
34 | 0.0016811 | 0.00042132
35 | 0.0021045 | 0.00052743
36 | 0.0015215 | 0.00038132
37 | 0.0028207 | 0.00070694
38 | 0.0010003 | 0.0002507
39 | 0.0037961 | 0.00095139
40 | 0.0017642 | 0.00044215
41 | 0.0021679 | 0.00054332
42 | 0.0027005 | 0.00067681
43 | 0.002019 | 0.000506
44 | 0.0014515 | 0.00036378
45 | 0.0011523 | 0.0002888
46 | 0.002039 | 0.00051101
47 | 0.0030821 | 0.00077244
48 | 0.0019694 | 0.00049358
49 | 0.0034086 | 0.00085428
50 | 0.0016834 | 0.0004219
51 | 0.0031489 | 0.00078919
52 | 0.0017067 | 0.00042775
53 | 0.0023899 | 0.00059897
54 | 0.0027833 | 0.00069757
55 | 0.0043173 | 0.001082
56 | 0.00070237 | 0.00017603
57 | 0.0011362 | 0.00028476
58 | 0.0013827 | 0.00034653
59 | 0.0010191 | 0.00025541
60 | 0.0018582 | 0.00046572
61 | 0.0012662 | 0.00031734
62 | 0.0012053 | 0.00030208
63 | 0.0011953 | 0.00029956
64 | 0.002164 | 0.00054234
65 | 0.0026074 | 0.00065348
66 | 0.0022167 | 0.00055555
67 | 0.0013402 | 0.00033589
68 | 0.0012025 | 0.00030137
69 | 0.003963 | 0.00099322
70 | 0.0019111 | 0.00047896
71 | 0.0029277 | 0.00073375
72 | 0.0013936 | 0.00034927
73 | 0.0019506 | 0.00048886
74 | 0.0016074 | 0.00040286
75 | 0.00098751 | 0.00024749
76 | 0.0011515 | 0.0002886
77 | 0.00089695 | 0.0002248
78 | 0.0029218 | 0.00073228
79 | 0.0017999 | 0.00045111
80 | 0.0010222 | 0.00025619
81 | 0.00093373 | 0.00023401
82 | 0.0016548 | 0.00041472
83 | 0.0010615 | 0.00026604
84 | 0.0020979 | 0.00052577
85 | 0.0029281 | 0.00073384
86 | 0.0029311 | 0.00073461
87 | 0.0024392 | 0.00061132
88 | 0.0016885 | 0.00042319
89 | 0.0015377 | 0.00038538
90 | 0.0017857 | 0.00044753
91 | 0.0012439 | 0.00031175
92 | 0.002429 | 0.00060876
93 | 0.0028104 | 0.00070435
94 | 0.0043094 | 0.00108
95 | 0.0012566 | 0.00031492
96 | 0.0015775 | 0.00039536
97 | 0.0014327 | 0.00035906
98 | 0.0012948 | 0.00032451
99 | 0.00093969 | 0.00023551
100 | 0.0016189 | 0.00040574
101 | 0.0022076 | 0.00055327
102 | 0.001126 | 0.0002822
103 | 0.0011616 | 0.00029112
104 | 0.0013828 | 0.00034656
105 | 0.0019916 | 0.00049914
106 | 0.0010628 | 0.00026635

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1