## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2422-17_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2422-17_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2422-17_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2422-17_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2422-17_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2422-17_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2422-17_0_3_node_64 | 0.4 | n |  | TRUE
7 | bus_LV_2422-17_0_3_node_69 | 0.4 | n |  | TRUE
8 | bus_LV_2422-17_0_3_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_2422-17_0_3_node_43 | 0.4 | n |  | TRUE
10 | bus_LV_2422-17_0_3_node_65 | 0.4 | n |  | TRUE
11 | bus_LV_2422-17_0_3_node_60 | 0.4 | n |  | TRUE
12 | bus_LV_2422-17_0_3_node_67 | 0.4 | n |  | TRUE
13 | bus_LV_2422-17_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2422-17_0_3_node_42 | 0.4 | n |  | TRUE
15 | bus_LV_2422-17_0_3_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_2422-17_0_3_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_2422-17_0_3_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_2422-17_0_3_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_2422-17_0_3_node_47 | 0.4 | n |  | TRUE
20 | bus_LV_2422-17_0_3_node_46 | 0.4 | n |  | TRUE
21 | bus_LV_2422-17_0_3_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_2422-17_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2422-17_0_3_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_2422-17_0_3_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_2422-17_0_3_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_2422-17_0_3_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_2422-17_0_3_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_2422-17_0_3_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_2422-17_0_3_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_2422-17_0_3_node_48 | 0.4 | n |  | TRUE
31 | bus_LV_2422-17_0_3_node_38 | 0.4 | n |  | TRUE
32 | bus_LV_2422-17_0_3_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_2422-17_0_3_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_2422-17_0_3_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_2422-17_0_3_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_2422-17_0_3_node_40 | 0.4 | n |  | TRUE
37 | bus_LV_2422-17_0_3_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_2422-17_0_3_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_2422-17_0_3_node_62 | 0.4 | n |  | TRUE
40 | bus_LV_2422-17_0_3_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_2422-17_0_3_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_2422-17_0_3_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_2422-17_0_3_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_2422-17_0_3_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_2422-17_0_3_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_2422-17_0_3_node_49 | 0.4 | n |  | TRUE
47 | bus_LV_2422-17_0_3_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_2422-17_0_3_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_2422-17_0_3_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_2422-17_0_3_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_2422-17_0_3_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_2422-17_0_3_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_2422-17_0_3_node_37 | 0.4 | n |  | TRUE
54 | bus_LV_2422-17_0_3_node_52 | 0.4 | n |  | TRUE
55 | bus_LV_2422-17_0_3_node_51 | 0.4 | n |  | TRUE
56 | bus_LV_2422-17_0_3_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_2422-17_0_3_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_2422-17_0_3_node_50 | 0.4 | n |  | TRUE
59 | bus_LV_2422-17_0_3_node_53 | 0.4 | n |  | TRUE
60 | bus_LV_2422-17_0_3_node_54 | 0.4 | n |  | TRUE
61 | bus_LV_2422-17_0_3_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_2422-17_0_3_node_57 | 0.4 | n |  | TRUE
63 | bus_LV_2422-17_0_3_node_59 | 0.4 | n |  | TRUE
64 | bus_LV_2422-17_0_3_node_61 | 0.4 | n |  | TRUE
65 | bus_LV_2422-17_0_3_node_66 | 0.4 | n |  | TRUE
66 | bus_LV_2422-17_0_3_node_72 | 0.4 | n |  | TRUE
67 | bus_LV_2422-17_0_3_node_71 | 0.4 | n |  | TRUE
68 | bus_LV_2422-17_0_3_node_70 | 0.4 | n |  | TRUE
69 | bus_LV_2422-17_0_3_node_68 | 0.4 | n |  | TRUE
70 | bus_MV_333_0_node_24 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2422-17_0_3_load_0 | 0 | 0.033674 | 0.0084396 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2422-17_0_3_load_1 | 1 | 0.0021142 | 0.00052988 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2422-17_0_3_load_3 | 3 | 0.00305 | 0.0007644 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2422-17_0_3_load_69 | 7 | 0.0015354 | 0.0003848 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2422-17_0_3_load_12 | 8 | 0.024471 | 0.0061329 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2422-17_0_3_load_43 | 9 | 0.0093986 | 0.0023555 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2422-17_0_3_load_65 | 10 | 0.0011667 | 0.00029241 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2422-17_0_3_load_60 | 11 | 0.001068 | 0.00026765 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2422-17_0_3_load_67 | 12 | 0.0013164 | 0.00032992 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2422-17_0_3_load_10 | 13 | 0.0017179 | 0.00043054 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2422-17_0_3_load_42 | 14 | 0.018056 | 0.0045251 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2422-17_0_3_load_6 | 15 | 0.001691 | 0.00042381 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2422-17_0_3_load_7 | 16 | 0.0013063 | 0.00032738 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2422-17_0_3_load_8 | 17 | 0.0017426 | 0.00043673 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2422-17_0_3_load_47 | 19 | 0.0015499 | 0.00038845 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2422-17_0_3_load_46 | 20 | 0.002414 | 0.000605 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2422-17_0_3_load_11 | 21 | 0.0017954 | 0.00044996 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2422-17_0_3_load_18 | 23 | 0.0031342 | 0.0007855 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2422-17_0_3_load_23 | 24 | 0.0015365 | 0.00038508 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2422-17_0_3_load_16 | 25 | 0.0013381 | 0.00033536 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2422-17_0_3_load_24 | 26 | 0.0017643 | 0.00044218 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2422-17_0_3_load_14 | 27 | 0.0010441 | 0.00026169 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2422-17_0_3_load_15 | 28 | 0.0017185 | 0.0004307 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2422-17_0_3_load_17 | 29 | 0.0019544 | 0.00048983 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2422-17_0_3_load_19 | 32 | 0.00099094 | 0.00024835 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2422-17_0_3_load_20 | 33 | 0.0013967 | 0.00035003 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2422-17_0_3_load_21 | 34 | 0.0010405 | 0.00026078 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2422-17_0_3_load_22 | 35 | 0.0015183 | 0.00038051 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2422-17_0_3_load_40 | 36 | 0.0009905 | 0.00024824 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2422-17_0_3_load_41 | 37 | 0.0009917 | 0.00024854 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2422-17_0_3_load_25 | 38 | 0.0014392 | 0.00036071 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2422-17_0_3_load_62 | 39 | 0.0020262 | 0.00050781 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2422-17_0_3_load_26 | 40 | 0.0036977 | 0.00092674 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2422-17_0_3_load_27 | 41 | 0.0029463 | 0.00073842 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2422-17_0_3_load_29 | 43 | 0.0028441 | 0.00071281 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2422-17_0_3_load_30 | 44 | 0.0023338 | 0.0005849 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2422-17_0_3_load_39 | 45 | 0.0013552 | 0.00033964 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2422-17_0_3_load_49 | 46 | 0.0024545 | 0.00061517 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2422-17_0_3_load_35 | 47 | 0.0016757 | 0.00041997 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2422-17_0_3_load_31 | 48 | 0.0016328 | 0.00040923 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2422-17_0_3_load_32 | 49 | 0.0014061 | 0.0003524 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2422-17_0_3_load_34 | 51 | 0.0046148 | 0.0011566 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2422-17_0_3_load_36 | 52 | 0.0026764 | 0.00067077 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2422-17_0_3_load_37 | 53 | 0.0027906 | 0.0006994 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2422-17_0_3_load_52 | 54 | 0.002668 | 0.00066867 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2422-17_0_3_load_51 | 55 | 0.0010042 | 0.00025168 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2422-17_0_3_load_44 | 56 | 0.021213 | 0.0053165 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2422-17_0_3_load_45 | 57 | 0.018371 | 0.0046041 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2422-17_0_3_load_50 | 58 | 0.012929 | 0.0032402 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2422-17_0_3_load_53 | 59 | 0.001185 | 0.00029698 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2422-17_0_3_load_54 | 60 | 0.0030204 | 0.00075699 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2422-17_0_3_load_56 | 61 | 0.0036755 | 0.00092117 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2422-17_0_3_load_57 | 62 | 0.003123 | 0.00078271 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2422-17_0_3_load_61 | 64 | 0.00097776 | 0.00024505 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2422-17_0_3_load_66 | 65 | 0.0010793 | 0.00027051 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2422-17_0_3_load_72 | 66 | 0.0010654 | 0.000267 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2422-17_0_3_load_71 | 67 | 0.0017901 | 0.00044864 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2422-17_0_3_load_70 | 68 | 0.0016033 | 0.00040183 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2422-17_0_3_load_68 | 69 | 0.0013164 | 0.00032992 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2422-17_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0061574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2422-17_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.030438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2422-17_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.027066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2422-17_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.023056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2422-17_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.036073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2422-17_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.054966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2422-17_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.041343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2422-17_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.032959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_2422-17_0_3_line_8 | NAYY 4x150 SE | 5 | 9 | 0.018818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2422-17_0_3_line_9 | NAYY 4x150 SE | 6 | 10 | 0.063185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2422-17_0_3_line_10 | NAYY 4x150 SE | 6 | 11 | 0.016101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2422-17_0_3_line_11 | NAYY 4x150 SE | 7 | 12 | 0.022005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2422-17_0_3_line_12 | NAYY 4x150 SE | 8 | 13 | 0.042056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2422-17_0_3_line_13 | NAYY 4x150 SE | 9 | 14 | 0.0080007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2422-17_0_3_line_14 | NAYY 4x150 SE | 10 | 68 | 0.0011366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2422-17_0_3_line_15 | NAYY 4x150 SE | 11 | 63 | 0.017198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2422-17_0_3_line_16 | NAYY 4x150 SE | 12 | 69 | 0.020148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2422-17_0_3_line_17 | NAYY 4x150 SE | 13 | 21 | 0.02257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2422-17_0_3_line_18 | NAYY 4x150 SE | 14 | 56 | 0.00012586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2422-17_0_3_line_19 | NAYY 4x150 SE | 15 | 16 | 0.0025354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2422-17_0_3_line_20 | NAYY 4x150 SE | 15 | 17 | 0.038368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2422-17_0_3_line_21 | NAYY 4x150 SE | 16 | 18 | 0.040453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2422-17_0_3_line_22 | NAYY 4x150 SE | 18 | 19 | 0.020085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2422-17_0_3_line_23 | NAYY 4x150 SE | 19 | 20 | 0.0094748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2422-17_0_3_line_24 | NAYY 4x150 SE | 20 | 30 | 0.029336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2422-17_0_3_line_25 | NAYY 4x150 SE | 21 | 22 | 0.027702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2422-17_0_3_line_26 | NAYY 4x150 SE | 22 | 23 | 0.0011665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2422-17_0_3_line_27 | NAYY 4x150 SE | 22 | 24 | 0.015041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2422-17_0_3_line_28 | NAYY 4x150 SE | 23 | 25 | 0.0071884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2422-17_0_3_line_29 | NAYY 4x150 SE | 24 | 26 | 0.018714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2422-17_0_3_line_30 | NAYY 4x150 SE | 25 | 27 | 0.015059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2422-17_0_3_line_31 | NAYY 4x150 SE | 26 | 38 | 0.037553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2422-17_0_3_line_32 | NAYY 4x150 SE | 27 | 28 | 0.0093066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2422-17_0_3_line_33 | NAYY 4x150 SE | 28 | 29 | 0.022942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2422-17_0_3_line_34 | NAYY 4x150 SE | 29 | 30 | 0.017488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2422-17_0_3_line_35 | NAYY 4x150 SE | 30 | 31 | 0.026224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2422-17_0_3_line_36 | NAYY 4x150 SE | 31 | 54 | 0.01055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2422-17_0_3_line_37 | NAYY 4x150 SE | 31 | 53 | 0.0065236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2422-17_0_3_line_38 | NAYY 4x150 SE | 32 | 33 | 0.0018192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2422-17_0_3_line_39 | NAYY 4x150 SE | 32 | 34 | 0.0030452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2422-17_0_3_line_40 | NAYY 4x150 SE | 33 | 35 | 0.00925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2422-17_0_3_line_41 | NAYY 4x150 SE | 35 | 36 | 0.0055639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2422-17_0_3_line_42 | NAYY 4x150 SE | 36 | 37 | 0.004329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2422-17_0_3_line_43 | NAYY 4x150 SE | 37 | 46 | 0.0067789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2422-17_0_3_line_44 | NAYY 4x150 SE | 38 | 39 | 0.020546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2422-17_0_3_line_45 | NAYY 4x150 SE | 40 | 41 | 0.0044502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2422-17_0_3_line_46 | NAYY 4x150 SE | 40 | 42 | 0.025081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2422-17_0_3_line_47 | NAYY 4x150 SE | 42 | 43 | 0.00796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2422-17_0_3_line_48 | NAYY 4x150 SE | 42 | 44 | 0.044623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2422-17_0_3_line_49 | NAYY 4x150 SE | 43 | 45 | 0.025113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2422-17_0_3_line_50 | NAYY 4x150 SE | 44 | 46 | 0.021267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2422-17_0_3_line_51 | NAYY 4x150 SE | 45 | 47 | 0.0071341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2422-17_0_3_line_52 | NAYY 4x150 SE | 47 | 50 | 0.017161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2422-17_0_3_line_53 | NAYY 4x150 SE | 48 | 49 | 0.016884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2422-17_0_3_line_54 | NAYY 4x150 SE | 48 | 50 | 0.017406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2422-17_0_3_line_55 | NAYY 4x150 SE | 49 | 51 | 0.005648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2422-17_0_3_line_56 | NAYY 4x150 SE | 51 | 52 | 0.019417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2422-17_0_3_line_57 | NAYY 4x150 SE | 52 | 53 | 0.011982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2422-17_0_3_line_58 | NAYY 4x150 SE | 54 | 55 | 0.0078171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2422-17_0_3_line_59 | NAYY 4x150 SE | 55 | 59 | 0.0028006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2422-17_0_3_line_60 | NAYY 4x150 SE | 56 | 57 | 0.012246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2422-17_0_3_line_61 | NAYY 4x150 SE | 57 | 58 | 0.049945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2422-17_0_3_line_62 | NAYY 4x150 SE | 59 | 60 | 0.0082677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2422-17_0_3_line_63 | NAYY 4x150 SE | 61 | 62 | 0.0072214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2422-17_0_3_line_64 | NAYY 4x150 SE | 62 | 63 | 0.0068519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2422-17_0_3_line_65 | NAYY 4x150 SE | 63 | 64 | 0.038796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2422-17_0_3_line_66 | NAYY 4x150 SE | 64 | 65 | 0.0075104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2422-17_0_3_line_67 | NAYY 4x150 SE | 66 | 67 | 0.0026018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2422-17_0_3_line_68 | NAYY 4x150 SE | 67 | 68 | 0.01761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2422-17_0_3_trafo_12 | 0.25 MVA 20/0.4 kV | 70 | 8 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2619600.865 | 1240208.187 | 2619604.7816 | 1240212.938
1 | 2619581.5034 | 1240184.7008 | 2619600.865 | 1240208.187
2 | 2619621.9985 | 1240233.8226 | 2619604.7816 | 1240212.938
3 | 2619581.5034 | 1240184.7008 | 2619566.0368 | 1240201.8384
4 | 2619605.5996 | 1240157.7966 | 2619581.5034 | 1240184.7008
5 | 2619566.0368 | 1240201.8384 | 2619529.1694 | 1240242.6985
6 | 2619566.0368 | 1240201.8384 | 2619535.6948 | 1240173.7569
7 | 2619605.5996 | 1240157.7966 | 2619602.697 | 1240143.7004 | 2619593.8899 | 1240127.3551
8 | 2619605.5996 | 1240157.7966 | 2619621.8208 | 1240148.2572
9 | 2619529.1694 | 1240242.6985 | 2619482.703 | 1240199.8818
10 | 2619529.1694 | 1240242.6985 | 2619521.8844 | 1240250.6684 | 2619518.3055 | 1240254.5821
11 | 2619519.5452 | 1240158.8105 | 2619535.6948 | 1240173.7569
12 | 2619573.9411 | 1240090.3318 | 2619593.8899 | 1240127.3551
13 | 2619628.7174 | 1240144.2015 | 2619621.8208 | 1240148.2572
14 | 2619482.703 | 1240199.8818 | 2619481.8671 | 1240199.1116
15 | 2619506.6997 | 1240267.2735 | 2619518.3055 | 1240254.5821
16 | 2619519.5452 | 1240158.8105 | 2619504.758 | 1240145.125
17 | 2619573.9411 | 1240090.3318 | 2619567.4037 | 1240078.199 | 2619562.5619 | 1240070.8652
18 | 2619628.7174 | 1240144.2015 | 2619628.8258 | 1240144.1377
19 | 2619488.6364 | 1240056.8972 | 2619487.0204 | 1240054.9436
20 | 2619488.6364 | 1240056.8972 | 2619492.1841 | 1240061.1861 | 2619495.8337 | 1240062.0097 | 2619501.3128 | 1240060.6156 | 2619518.9546 | 1240045.2319
21 | 2619461.2359 | 1240023.7726 | 2619487.0204 | 1240054.9436
22 | 2619461.2359 | 1240023.7726 | 2619476.8426 | 1240011.1295
23 | 2619484.2048 | 1240005.1654 | 2619476.8426 | 1240011.1295
24 | 2619506.9995 | 1239986.6992 | 2619484.2048 | 1240005.1654
25 | 2619547.2993 | 1240047.7473 | 2619562.5619 | 1240070.8652
26 | 2619547.2993 | 1240047.7473 | 2619546.6566 | 1240046.7738
27 | 2619547.2993 | 1240047.7473 | 2619536.0044 | 1240057.68
28 | 2619542.6964 | 1240040.7746 | 2619546.6566 | 1240046.7738
29 | 2619521.9513 | 1240070.0383 | 2619536.0044 | 1240057.68
30 | 2619542.6964 | 1240040.7746 | 2619534.4001 | 1240028.207
31 | 2619521.9513 | 1240070.0383 | 2619514.2353 | 1240076.8236 | 2619511.4044 | 1240075.4024 | 2619493.3398 | 1240091.371
32 | 2619534.4001 | 1240028.207 | 2619529.273 | 1240020.4402
33 | 2619516.6339 | 1240001.2939 | 2619529.273 | 1240020.4402
34 | 2619506.9995 | 1239986.6992 | 2619516.6339 | 1240001.2939
35 | 2619506.9995 | 1239986.6992 | 2619529.1938 | 1239972.6298
36 | 2619529.1938 | 1239972.6298 | 2619536.1548 | 1239980.5576
37 | 2619529.1938 | 1239972.6298 | 2619527.9428 | 1239966.2273
38 | 2619596.7659 | 1239994.0887 | 2619596.9595 | 1239995.8976
39 | 2619597.2834 | 1239998.9255 | 2619596.9595 | 1239995.8976
40 | 2619595.7818 | 1239984.8912 | 2619596.7659 | 1239994.0887
41 | 2619595.7818 | 1239984.8912 | 2619595.1899 | 1239979.3589
42 | 2619595.1899 | 1239979.3589 | 2619594.7294 | 1239975.0545
43 | 2619594.0082 | 1239968.314 | 2619594.7294 | 1239975.0545
44 | 2619493.3398 | 1240091.371 | 2619477.946 | 1240104.9786
45 | 2619616.3441 | 1239906.1015 | 2619611.9218 | 1239905.6037
46 | 2619586.9984 | 1239902.7983 | 2619611.9218 | 1239905.6037
47 | 2619586.9984 | 1239902.7983 | 2619579.0992 | 1239901.8159
48 | 2619586.9984 | 1239902.7983 | 2619591.7457 | 1239947.168
49 | 2619579.0992 | 1239901.8159 | 2619554.1781 | 1239898.7165
50 | 2619594.0082 | 1239968.314 | 2619591.7457 | 1239947.168
51 | 2619547.0986 | 1239897.836 | 2619554.1781 | 1239898.7165
52 | 2619530.0413 | 1239896.4184 | 2619534.2009 | 1239896.2319 | 2619547.0986 | 1239897.836
53 | 2619525.7596 | 1239930.052 | 2619526.489 | 1239928.1599 | 2619528.8496 | 1239920.8297 | 2619530.0877 | 1239914.5187 | 2619530.1501 | 1239913.7974
54 | 2619530.0413 | 1239896.4184 | 2619529.9411 | 1239903.9005 | 2619530.4021 | 1239910.8842 | 2619530.1501 | 1239913.7974
55 | 2619523.7281 | 1239935.322 | 2619525.7596 | 1239930.052
56 | 2619523.7281 | 1239935.322 | 2619523.7281 | 1239935.322 | 2619523.4691 | 1239938.2007 | 2619523.147 | 1239941.8908 | 2619524.1962 | 1239947.053 | 2619525.6451 | 1239954.4679
57 | 2619527.9428 | 1239966.2273 | 2619525.6451 | 1239954.4679
58 | 2619542.103 | 1239985.6297 | 2619536.1548 | 1239980.5576
59 | 2619542.103 | 1239985.6297 | 2619543.537 | 1239986.8525 | 2619543.9083 | 1239987.6898
60 | 2619639.3819 | 1240137.9299 | 2619628.8258 | 1240144.1377
61 | 2619639.3819 | 1240137.9299 | 2619649.7989 | 1240131.8038 | 2619656.6406 | 1240129.9697 | 2619662.0121 | 1240131.3994 | 2619676.955 | 1240151.5725 | 2619677.0231 | 1240151.6633
62 | 2619547.26 | 1239995.2477 | 2619543.9083 | 1239987.6898
63 | 2619497.5349 | 1240277.9535 | 2619502.2376 | 1240272.4733
64 | 2619506.6997 | 1240267.2735 | 2619502.2376 | 1240272.4733
65 | 2619506.6997 | 1240267.2735 | 2619477.9633 | 1240241.2086
66 | 2619477.9633 | 1240241.2086 | 2619472.4003 | 1240236.1628
67 | 2619468.9164 | 1240187.1782 | 2619467.0031 | 1240185.4151
68 | 2619481.8671 | 1240199.1116 | 2619468.9164 | 1240187.1782

## bus_geodata
| x | y | coords
0 | 2619600.865 | 1240208.187
1 | 2619604.7816 | 1240212.938
2 | 2619581.5034 | 1240184.7008
3 | 2619621.9985 | 1240233.8226
4 | 2619566.0368 | 1240201.8384
5 | 2619605.5996 | 1240157.7966
6 | 2619529.1694 | 1240242.6985
7 | 2619535.6948 | 1240173.7569
8 | 2619593.8899 | 1240127.3551
9 | 2619621.8208 | 1240148.2572
10 | 2619482.703 | 1240199.8818
11 | 2619518.3055 | 1240254.5821
12 | 2619519.5452 | 1240158.8105
13 | 2619573.9411 | 1240090.3318
14 | 2619628.7174 | 1240144.2015
15 | 2619488.6364 | 1240056.8972
16 | 2619487.0204 | 1240054.9436
17 | 2619518.9546 | 1240045.2319
18 | 2619461.2359 | 1240023.7726
19 | 2619476.8426 | 1240011.1295
20 | 2619484.2048 | 1240005.1654
21 | 2619562.5619 | 1240070.8652
22 | 2619547.2993 | 1240047.7473
23 | 2619546.6566 | 1240046.7738
24 | 2619536.0044 | 1240057.68
25 | 2619542.6964 | 1240040.7746
26 | 2619521.9513 | 1240070.0383
27 | 2619534.4001 | 1240028.207
28 | 2619529.273 | 1240020.4402
29 | 2619516.6339 | 1240001.2939
30 | 2619506.9995 | 1239986.6992
31 | 2619529.1938 | 1239972.6298
32 | 2619596.9595 | 1239995.8976
33 | 2619596.7659 | 1239994.0887
34 | 2619597.2834 | 1239998.9255
35 | 2619595.7818 | 1239984.8912
36 | 2619595.1899 | 1239979.3589
37 | 2619594.7294 | 1239975.0545
38 | 2619493.3398 | 1240091.371
39 | 2619477.946 | 1240104.9786
40 | 2619611.9218 | 1239905.6037
41 | 2619616.3441 | 1239906.1015
42 | 2619586.9984 | 1239902.7983
43 | 2619579.0992 | 1239901.8159
44 | 2619591.7457 | 1239947.168
45 | 2619554.1781 | 1239898.7165
46 | 2619594.0082 | 1239968.314
47 | 2619547.0986 | 1239897.836
48 | 2619530.1501 | 1239913.7974
49 | 2619525.7596 | 1239930.052
50 | 2619530.0413 | 1239896.4184
51 | 2619523.7281 | 1239935.322
52 | 2619525.6451 | 1239954.4679
53 | 2619527.9428 | 1239966.2273
54 | 2619536.1548 | 1239980.5576
55 | 2619542.103 | 1239985.6297
56 | 2619628.8258 | 1240144.1377
57 | 2619639.3819 | 1240137.9299
58 | 2619677.0231 | 1240151.6633
59 | 2619543.9083 | 1239987.6898
60 | 2619547.26 | 1239995.2477
61 | 2619497.5349 | 1240277.9535
62 | 2619502.2376 | 1240272.4733
63 | 2619506.6997 | 1240267.2735
64 | 2619477.9633 | 1240241.2086
65 | 2619472.4003 | 1240236.1628
66 | 2619467.0031 | 1240185.4151
67 | 2619468.9164 | 1240187.1782
68 | 2619481.8671 | 1240199.1116
69 | 2619504.758 | 1240145.125
70 | 2619605.5996 | 1240157.7966

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99199 | -0.056137 | 0.033674 | 0.0084396
1 | 0.99194 | -0.05646 | 0.0021142 | 0.00052988
2 | 0.99369 | -0.044166 | 0 | 0
3 | 0.99182 | -0.057298 | 0.00305 | 0.0007644
4 | 0.99303 | -0.048772 | 0 | 0
5 | 0.99672 | -0.022867 | 0 | 0
6 | 0.9918 | -0.057443 | 0 | 0
7 | 0.99279 | -0.050519 | 0.0015354 | 0.0003848
8 | 1 | 0 | -0.21497 | -0.053959
9 | 0.99456 | -0.038019 | 0.0093986 | 0.0023555
10 | 0.99129 | -0.061055 | 0.0011667 | 0.00029241
11 | 0.99158 | -0.059066 | 0.001068 | 0.00026765
12 | 0.9927 | -0.051106 | 0.0013164 | 0.00032992
13 | 0.99552 | -0.030977 | 0.0017179 | 0.00043054
14 | 0.99375 | -0.04372 | 0.018056 | 0.0045251
15 | 0.98344 | -0.11581 | 0.001691 | 0.00042381
16 | 0.98345 | -0.11572 | 0.0013063 | 0.00032738
17 | 0.98335 | -0.1165 | 0.0017426 | 0.00043673
18 | 0.98373 | -0.11374 | 0 | 0
19 | 0.98387 | -0.11276 | 0.0015499 | 0.00038845
20 | 0.98396 | -0.11214 | 0.002414 | 0.000605
21 | 0.99317 | -0.047324 | 0.0017954 | 0.00044996
22 | 0.99036 | -0.066987 | 0 | 0
23 | 0.99025 | -0.067737 | 0.0031342 | 0.0007855
24 | 0.99022 | -0.068024 | 0.0015365 | 0.00038508
25 | 0.98963 | -0.072132 | 0.0013381 | 0.00033536
26 | 0.99007 | -0.069021 | 0.0017643 | 0.00044218
27 | 0.98834 | -0.081153 | 0.0010441 | 0.00026169
28 | 0.98756 | -0.08664 | 0.0017185 | 0.0004307
29 | 0.9857 | -0.099797 | 0.0019544 | 0.00048983
30 | 0.98433 | -0.10951 | 0 | 0
31 | 0.9826 | -0.12176 | 0 | 0
32 | 0.97618 | -0.1676 | 0.00099094 | 0.00024835
33 | 0.97618 | -0.16756 | 0.0013967 | 0.00035003
34 | 0.97617 | -0.16763 | 0.0010405 | 0.00026078
35 | 0.97623 | -0.16723 | 0.0015183 | 0.00038051
36 | 0.97627 | -0.16694 | 0.0009905 | 0.00024824
37 | 0.97631 | -0.16667 | 0.0009917 | 0.00024854
38 | 0.98989 | -0.070348 | 0.0014392 | 0.00036071
39 | 0.98983 | -0.070772 | 0.0020262 | 0.00050781
40 | 0.97719 | -0.16036 | 0.0036977 | 0.00092674
41 | 0.97717 | -0.1605 | 0.0029463 | 0.00073842
42 | 0.97743 | -0.15862 | 0 | 0
43 | 0.97764 | -0.15709 | 0.0028441 | 0.00071281
44 | 0.97667 | -0.16409 | 0.0023338 | 0.0005849
45 | 0.97842 | -0.15153 | 0.0013552 | 0.00033964
46 | 0.97638 | -0.16618 | 0.0024545 | 0.00061517
47 | 0.97866 | -0.14986 | 0.0016757 | 0.00041997
48 | 0.97988 | -0.14113 | 0.0016328 | 0.00040923
49 | 0.98051 | -0.13659 | 0.0014061 | 0.0003524
50 | 0.97926 | -0.14552 | 0 | 0
51 | 0.98074 | -0.13499 | 0.0046148 | 0.0011566
52 | 0.98164 | -0.12857 | 0.0026764 | 0.00067077
53 | 0.98225 | -0.12428 | 0.0027906 | 0.0006994
54 | 0.98248 | -0.12262 | 0.002668 | 0.00066867
55 | 0.98242 | -0.12304 | 0.0010042 | 0.00025168
56 | 0.99374 | -0.043787 | 0.021213 | 0.0053165
57 | 0.99319 | -0.047664 | 0.018371 | 0.0046041
58 | 0.99227 | -0.054204 | 0.012929 | 0.0032402
59 | 0.9824 | -0.12316 | 0.001185 | 0.00029698
60 | 0.98237 | -0.12342 | 0.0030204 | 0.00075699
61 | 0.99125 | -0.061356 | 0.0036755 | 0.00092117
62 | 0.99129 | -0.061087 | 0.003123 | 0.00078271
63 | 0.99136 | -0.060614 | 0 | 0
64 | 0.99124 | -0.061425 | 0.00097776 | 0.00024505
65 | 0.99123 | -0.061508 | 0.0010793 | 0.00027051
66 | 0.99121 | -0.061646 | 0.0010654 | 0.000267
67 | 0.99121 | -0.061617 | 0.0017901 | 0.00044864
68 | 0.99129 | -0.061106 | 0.0016033 | 0.00040183
69 | 0.99266 | -0.051375 | 0.0013164 | 0.00032992
70 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0051648 | 0.0012941 | -0.0051646 | -0.0012941 | 2.3061e-07 | 9.2085e-09 | 0.0077473 | 0.0077473 | 0.0077473 | 0.99199 | -0.056137 | 0.99194 | -0.05646 | 2.8694
1 | -0.038839 | -0.0097337 | 0.038904 | 0.0097581 | 6.4467e-05 | 2.4402e-05 | 0.05826 | 0.05826 | 0.05826 | 0.99199 | -0.056137 | 0.99369 | -0.044166 | 21.5778
2 | 0.0030503 | 0.00076418 | -0.00305 | -0.0007644 | 3.5362e-07 | -2.1334e-07 | 0.0045757 | 0.0045758 | 0.0045758 | 0.99194 | -0.05646 | 0.99182 | -0.057298 | 1.6948
3 | 0.019758 | 0.0049528 | -0.019745 | -0.0049483 | 1.2594e-05 | 4.5455e-06 | 0.029587 | 0.029587 | 0.029587 | 0.99369 | -0.044166 | 0.99303 | -0.048772 | 10.9582
4 | -0.058661 | -0.014711 | 0.058835 | 0.014777 | 0.00017371 | 6.6342e-05 | 0.087847 | 0.087847 | 0.087847 | 0.99369 | -0.044166 | 0.99672 | -0.022867 | 32.5359
5 | 0.015576 | 0.0039042 | -0.015557 | -0.0038977 | 1.8684e-05 | 6.476e-06 | 0.02334 | 0.02334 | 0.02334 | 0.99303 | -0.048772 | 0.9918 | -0.057443 | 8.6445
6 | 0.0041695 | 0.0010441 | -0.0041685 | -0.0010442 | 1.0069e-06 | -1.4744e-07 | 0.0062475 | 0.0062477 | 0.0062477 | 0.99303 | -0.048772 | 0.99279 | -0.050519 | 2.3139
7 | -0.13905 | -0.034915 | 0.1395 | 0.035085 | 0.00044326 | 0.00016962 | 0.20762 | 0.20762 | 0.20762 | 0.99672 | -0.022867 | 1 | 0 | 38.448
8 | 0.08022 | 0.020138 | -0.080051 | -0.020073 | 0.00016845 | 6.4545e-05 | 0.11977 | 0.11977 | 0.11977 | 0.99672 | -0.022867 | 0.99456 | -0.038019 | 44.3602
9 | 0.0056285 | 0.00141 | -0.0056257 | -0.0014097 | 2.8116e-06 | 2.6637e-07 | 0.0084443 | 0.0084446 | 0.0084446 | 0.9918 | -0.057443 | 0.99129 | -0.061055 | 3.1276
10 | 0.0099285 | 0.0024878 | -0.0099263 | -0.0024871 | 2.2293e-06 | 6.4968e-07 | 0.014896 | 0.014896 | 0.014896 | 0.9918 | -0.057443 | 0.99158 | -0.059066 | 5.5169
11 | 0.0026331 | 0.00065941 | -0.0026329 | -0.00065961 | 2.1385e-07 | -2.0226e-07 | 0.0039464 | 0.0039465 | 0.0039465 | 0.99279 | -0.050519 | 0.9927 | -0.051106 | 1.4617
12 | 0.074671 | 0.018875 | -0.074347 | -0.018751 | 0.00032432 | 0.00012419 | 0.11117 | 0.11117 | 0.11117 | 1 | 0 | 0.99552 | -0.030977 | 41.1736
13 | 0.070653 | 0.017718 | -0.070597 | -0.017696 | 5.5789e-05 | 2.1354e-05 | 0.10571 | 0.10571 | 0.10571 | 0.99456 | -0.038019 | 0.99375 | -0.04372 | 39.1521
14 | 0.004459 | 0.0011173 | -0.004459 | -0.0011173 | 3.1774e-08 | -2.432e-09 | 0.0066933 | 0.0066933 | 0.0066933 | 0.99129 | -0.061055 | 0.99129 | -0.061106 | 2.479
15 | 0.0088583 | 0.0022195 | -0.0088564 | -0.002219 | 1.8963e-06 | 5.0757e-07 | 0.013293 | 0.013293 | 0.013293 | 0.99158 | -0.059066 | 0.99136 | -0.060614 | 4.9234
16 | 0.0013165 | 0.00032968 | -0.0013164 | -0.00032992 | 4.8955e-08 | -2.4165e-07 | 0.0019732 | 0.0019733 | 0.0019733 | 0.9927 | -0.051106 | 0.99266 | -0.051375 | 0.73086
17 | 0.072629 | 0.01832 | -0.072463 | -0.018256 | 0.00016611 | 6.3594e-05 | 0.1086 | 0.1086 | 0.1086 | 0.99552 | -0.030977 | 0.99317 | -0.047324 | 40.2227
18 | 0.052541 | 0.013171 | -0.052541 | -0.013171 | 4.861e-07 | 1.8533e-07 | 0.078675 | 0.078675 | 0.078675 | 0.99375 | -0.04372 | 0.99374 | -0.043787 | 29.1389
19 | -0.0034338 | -0.00086012 | 0.0034338 | 0.00086011 | 4.2704e-08 | -1.5746e-08 | 0.0051954 | 0.0051954 | 0.0051954 | 0.98344 | -0.11581 | 0.98345 | -0.11572 | 1.9242
20 | 0.0017427 | 0.00043631 | -0.0017426 | -0.00043673 | 1.6646e-07 | -4.2276e-07 | 0.0026367 | 0.0026369 | 0.0026369 | 0.98344 | -0.11581 | 0.98335 | -0.1165 | 0.97663
21 | -0.0047401 | -0.0011875 | 0.0047414 | 0.0011875 | 1.2983e-06 | -1.4087e-08 | 0.0071718 | 0.0071716 | 0.0071718 | 0.98345 | -0.11572 | 0.98373 | -0.11374 | 2.6562
22 | -0.0047414 | -0.0011875 | 0.004742 | 0.0011875 | 6.4461e-07 | -7.1116e-09 | 0.0071716 | 0.0071716 | 0.0071716 | 0.98373 | -0.11374 | 0.98387 | -0.11276 | 2.6562
23 | -0.006292 | -0.0015759 | 0.0062925 | 0.001576 | 5.3535e-07 | 8.5566e-08 | 0.0095157 | 0.0095157 | 0.0095157 | 0.98387 | -0.11276 | 0.98396 | -0.11214 | 3.5243
24 | -0.0087065 | -0.002181 | 0.0087097 | 0.0021819 | 3.1733e-06 | 8.4773e-07 | 0.013166 | 0.013166 | 0.013166 | 0.98396 | -0.11214 | 0.98433 | -0.10951 | 4.8764
25 | 0.070668 | 0.017806 | -0.070474 | -0.017732 | 0.0001939 | 7.4219e-05 | 0.10591 | 0.10591 | 0.10591 | 0.99317 | -0.047324 | 0.99036 | -0.066987 | 39.2264
26 | 0.063705 | 0.016037 | -0.063698 | -0.016034 | 6.6722e-06 | 2.5512e-06 | 0.095742 | 0.095742 | 0.095742 | 0.99036 | -0.066987 | 0.99025 | -0.067737 | 35.4599
27 | 0.0067687 | 0.0016955 | -0.0067677 | -0.0016954 | 9.7067e-07 | 1.7982e-07 | 0.01017 | 0.01017 | 0.01017 | 0.99036 | -0.066987 | 0.99022 | -0.068024 | 3.7665
28 | 0.060564 | 0.015249 | -0.060527 | -0.015234 | 3.7171e-05 | 1.4204e-05 | 0.091032 | 0.091032 | 0.091032 | 0.99025 | -0.067737 | 0.98963 | -0.072132 | 33.7156
29 | 0.0052312 | 0.0013103 | -0.0052305 | -0.0013102 | 7.2159e-07 | 3.6833e-08 | 0.0078608 | 0.0078609 | 0.0078609 | 0.99022 | -0.068024 | 0.99007 | -0.069021 | 2.9114
30 | 0.059189 | 0.014899 | -0.059114 | -0.014871 | 7.4466e-05 | 2.8448e-05 | 0.08902 | 0.08902 | 0.08902 | 0.98963 | -0.072132 | 0.98834 | -0.081153 | 32.9705
31 | 0.0034662 | 0.00086806 | -0.0034656 | -0.0008683 | 6.3591e-07 | -2.3827e-07 | 0.0052092 | 0.0052094 | 0.0052094 | 0.99007 | -0.069021 | 0.98989 | -0.070348 | 1.9294
32 | 0.05807 | 0.014609 | -0.058026 | -0.014592 | 4.441e-05 | 1.6961e-05 | 0.087448 | 0.087448 | 0.087448 | 0.98834 | -0.081153 | 0.98756 | -0.08664 | 32.3883
33 | 0.056307 | 0.014161 | -0.056204 | -0.014122 | 0.00010309 | 3.9356e-05 | 0.084859 | 0.084859 | 0.084859 | 0.98756 | -0.08664 | 0.9857 | -0.099797 | 31.4293
34 | 0.05425 | 0.013632 | -0.054177 | -0.013604 | 7.3212e-05 | 2.7936e-05 | 0.081909 | 0.081909 | 0.081909 | 0.9857 | -0.099797 | 0.98433 | -0.10951 | 30.3366
35 | 0.045467 | 0.011422 | -0.04539 | -0.011393 | 7.7328e-05 | 2.9409e-05 | 0.068743 | 0.068743 | 0.068743 | 0.98433 | -0.10951 | 0.9826 | -0.12176 | 25.4603
36 | 0.007879 | 0.0019745 | -0.0078781 | -0.0019743 | 9.3723e-07 | 2.2685e-07 | 0.011932 | 0.011932 | 0.011932 | 0.9826 | -0.12176 | 0.98248 | -0.12262 | 4.4192
37 | 0.037511 | 0.0094184 | -0.037497 | -0.0094134 | 1.3138e-05 | 4.9706e-06 | 0.056811 | 0.056811 | 0.056811 | 0.9826 | -0.12176 | 0.98225 | -0.12428 | 21.0411
38 | -0.0020315 | -0.00050909 | 0.0020315 | 0.00050908 | 1.0885e-08 | -1.8557e-08 | 0.0030966 | 0.0030966 | 0.0030966 | 0.97618 | -0.1676 | 0.97618 | -0.16756 | 1.1469
39 | 0.0010405 | 0.00026074 | -0.0010405 | -0.00026078 | 4.7803e-09 | -3.6231e-08 | 0.0015861 | 0.0015861 | 0.0015861 | 0.97618 | -0.1676 | 0.97617 | -0.16763 | 0.58744
40 | -0.0034281 | -0.00085911 | 0.0034283 | 0.00085906 | 1.5761e-07 | -5.5028e-08 | 0.0052255 | 0.0052255 | 0.0052255 | 0.97618 | -0.16756 | 0.97623 | -0.16723 | 1.9354
41 | -0.0049465 | -0.0012396 | 0.0049467 | 0.0012396 | 1.9736e-07 | 6.3415e-09 | 0.0075397 | 0.0075397 | 0.0075397 | 0.97623 | -0.16723 | 0.97627 | -0.16694 | 2.7925
42 | -0.0059372 | -0.0014878 | 0.0059375 | 0.0014878 | 2.2121e-07 | 3.095e-08 | 0.0090494 | 0.0090494 | 0.0090494 | 0.97627 | -0.16694 | 0.97631 | -0.16667 | 3.3516
43 | -0.0069292 | -0.0017364 | 0.0069296 | 0.0017365 | 4.7178e-07 | 9.6679e-08 | 0.010561 | 0.010561 | 0.010561 | 0.97631 | -0.16667 | 0.97638 | -0.16618 | 3.9114
44 | 0.0020263 | 0.00050759 | -0.0020262 | -0.00050781 | 1.1895e-07 | -2.1836e-07 | 0.0030459 | 0.003046 | 0.003046 | 0.98989 | -0.070348 | 0.98983 | -0.070772 | 1.1281
45 | 0.0029464 | 0.00073839 | -0.0029463 | -0.00073842 | 5.5899e-08 | -3.425e-08 | 0.0044866 | 0.0044866 | 0.0044866 | 0.97719 | -0.16036 | 0.97717 | -0.1605 | 1.6617
46 | -0.0066441 | -0.0016651 | 0.0066457 | 0.0016654 | 1.602e-06 | 3.0186e-07 | 0.010117 | 0.010117 | 0.010117 | 0.97719 | -0.16036 | 0.97743 | -0.15862 | 3.7472
47 | -0.018375 | -0.0046056 | 0.018379 | 0.004607 | 3.887e-06 | 1.3952e-06 | 0.027974 | 0.027974 | 0.027974 | 0.97743 | -0.15862 | 0.97764 | -0.15709 | 10.3608
48 | 0.01173 | 0.0029402 | -0.011721 | -0.0029373 | 8.879e-06 | 2.8561e-06 | 0.017857 | 0.017857 | 0.017857 | 0.97743 | -0.15862 | 0.97667 | -0.16409 | 6.6138
49 | -0.021223 | -0.0053198 | 0.02124 | 0.0053258 | 1.6352e-05 | 5.9741e-06 | 0.032303 | 0.032303 | 0.032303 | 0.97764 | -0.15709 | 0.97842 | -0.15153 | 11.9641
50 | 0.0093869 | 0.0023524 | -0.0093842 | -0.0023517 | 2.7143e-06 | 7.7789e-07 | 0.014301 | 0.014302 | 0.014302 | 0.97667 | -0.16409 | 0.97638 | -0.16618 | 5.2969
51 | -0.022595 | -0.0056654 | 0.0226 | 0.0056674 | 5.2569e-06 | 1.9323e-06 | 0.034364 | 0.034364 | 0.034364 | 0.97842 | -0.15153 | 0.97866 | -0.14986 | 12.7274
52 | -0.024276 | -0.0060873 | 0.02429 | 0.0060927 | 1.459e-05 | 5.3957e-06 | 0.036912 | 0.036912 | 0.036912 | 0.97866 | -0.14986 | 0.97926 | -0.14552 | 13.671
53 | -0.025938 | -0.0065074 | 0.025954 | 0.0065135 | 1.6348e-05 | 6.0748e-06 | 0.039391 | 0.039391 | 0.039391 | 0.97988 | -0.14113 | 0.98051 | -0.13659 | 14.5893
54 | 0.024305 | 0.0060982 | -0.02429 | -0.0060927 | 1.4798e-05 | 5.4724e-06 | 0.036912 | 0.036912 | 0.036912 | 0.97988 | -0.14113 | 0.97926 | -0.14552 | 13.671
55 | -0.02736 | -0.0068659 | 0.027366 | 0.0068682 | 6.0771e-06 | 2.2661e-06 | 0.041525 | 0.041525 | 0.041525 | 0.98051 | -0.13659 | 0.98074 | -0.13499 | 15.3796
56 | -0.031981 | -0.0080247 | 0.03201 | 0.0080355 | 2.8532e-05 | 1.0729e-05 | 0.048527 | 0.048527 | 0.048527 | 0.98074 | -0.13499 | 0.98164 | -0.12857 | 17.9728
57 | -0.034686 | -0.0087062 | 0.034707 | 0.008714 | 2.0673e-05 | 7.7996e-06 | 0.052584 | 0.052583 | 0.052584 | 0.98164 | -0.12857 | 0.98225 | -0.12428 | 19.4754
58 | 0.0052101 | 0.0013056 | -0.0052098 | -0.0013056 | 3.0372e-07 | 1.783e-08 | 0.0078908 | 0.0078909 | 0.0078909 | 0.98248 | -0.12262 | 0.98242 | -0.12304 | 2.9225
59 | 0.0042056 | 0.0010539 | -0.0042055 | -0.0010539 | 7.0908e-08 | -8.1881e-09 | 0.0063699 | 0.0063699 | 0.0063699 | 0.98242 | -0.12304 | 0.9824 | -0.12316 | 2.3592
60 | 0.031328 | 0.0078545 | -0.031311 | -0.0078482 | 1.6816e-05 | 6.3093e-06 | 0.046911 | 0.046911 | 0.046911 | 0.99374 | -0.043787 | 0.99319 | -0.047664 | 17.3745
61 | 0.01294 | 0.0032441 | -0.012929 | -0.0032402 | 1.1715e-05 | 3.86e-06 | 0.019388 | 0.019388 | 0.019388 | 0.99319 | -0.047664 | 0.99227 | -0.054204 | 7.1808
62 | 0.0030205 | 0.00075693 | -0.0030204 | -0.00075699 | 1.0799e-07 | -6.3145e-08 | 0.0045751 | 0.0045751 | 0.0045751 | 0.9824 | -0.12316 | 0.98237 | -0.12342 | 1.6945
63 | -0.0036755 | -0.00092117 | 0.0036756 | 0.00092113 | 1.3718e-07 | -4.0332e-08 | 0.0055175 | 0.0055174 | 0.0055175 | 0.99125 | -0.061356 | 0.99129 | -0.061087 | 2.0435
64 | -0.0067987 | -0.0017038 | 0.0067991 | 0.0017039 | 4.453e-07 | 8.2931e-08 | 0.010205 | 0.010205 | 0.010205 | 0.99129 | -0.061087 | 0.99136 | -0.060614 | 3.7798
65 | 0.0020573 | 0.00051505 | -0.0020571 | -0.00051546 | 2.3084e-07 | -4.1138e-07 | 0.0030878 | 0.003088 | 0.003088 | 0.99136 | -0.060614 | 0.99124 | -0.061425 | 1.1437
66 | 0.0010793 | 0.00027041 | -0.0010793 | -0.00027051 | 1.2303e-08 | -9.2079e-08 | 0.0016202 | 0.0016203 | 0.0016203 | 0.99124 | -0.061425 | 0.99123 | -0.061508 | 0.6001
67 | -0.0010654 | -0.000267 | 0.0010654 | 0.00026697 | 4.1527e-09 | -3.1939e-08 | 0.0015993 | 0.0015993 | 0.0015993 | 0.99121 | -0.061646 | 0.99121 | -0.061617 | 0.59234
68 | -0.0028555 | -0.00071562 | 0.0028557 | 0.00071547 | 2.0192e-07 | -1.4935e-07 | 0.0042866 | 0.0042866 | 0.0042866 | 0.99121 | -0.061617 | 0.99129 | -0.061106 | 1.5876

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23944 | 0.060092

## res_load
| p_mw | q_mvar
0 | 0.033674 | 0.0084396
1 | 0.0021142 | 0.00052988
2 | 0.00305 | 0.0007644
3 | 0.0015354 | 0.0003848
4 | 0.024471 | 0.0061329
5 | 0.0093986 | 0.0023555
6 | 0.0011667 | 0.00029241
7 | 0.001068 | 0.00026765
8 | 0.0013164 | 0.00032992
9 | 0.0017179 | 0.00043054
10 | 0.018056 | 0.0045251
11 | 0.001691 | 0.00042381
12 | 0.0013063 | 0.00032738
13 | 0.0017426 | 0.00043673
14 | 0.0015499 | 0.00038845
15 | 0.002414 | 0.000605
16 | 0.0017954 | 0.00044996
17 | 0.0031342 | 0.0007855
18 | 0.0015365 | 0.00038508
19 | 0.0013381 | 0.00033536
20 | 0.0017643 | 0.00044218
21 | 0.0010441 | 0.00026169
22 | 0.0017185 | 0.0004307
23 | 0.0019544 | 0.00048983
24 | 0.00099094 | 0.00024835
25 | 0.0013967 | 0.00035003
26 | 0.0010405 | 0.00026078
27 | 0.0015183 | 0.00038051
28 | 0.0009905 | 0.00024824
29 | 0.0009917 | 0.00024854
30 | 0.0014392 | 0.00036071
31 | 0.0020262 | 0.00050781
32 | 0.0036977 | 0.00092674
33 | 0.0029463 | 0.00073842
34 | 0.0028441 | 0.00071281
35 | 0.0023338 | 0.0005849
36 | 0.0013552 | 0.00033964
37 | 0.0024545 | 0.00061517
38 | 0.0016757 | 0.00041997
39 | 0.0016328 | 0.00040923
40 | 0.0014061 | 0.0003524
41 | 0.0046148 | 0.0011566
42 | 0.0026764 | 0.00067077
43 | 0.0027906 | 0.0006994
44 | 0.002668 | 0.00066867
45 | 0.0010042 | 0.00025168
46 | 0.021213 | 0.0053165
47 | 0.018371 | 0.0046041
48 | 0.012929 | 0.0032402
49 | 0.001185 | 0.00029698
50 | 0.0030204 | 0.00075699
51 | 0.0036755 | 0.00092117
52 | 0.003123 | 0.00078271
53 | 0.00097776 | 0.00024505
54 | 0.0010793 | 0.00027051
55 | 0.0010654 | 0.000267
56 | 0.0017901 | 0.00044864
57 | 0.0016033 | 0.00040183
58 | 0.0013164 | 0.00032992

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1