## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2422-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2422-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2422-1_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2422-1_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2422-1_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2422-1_0_3_node_26 | 0.4 | n |  | TRUE
6 | bus_LV_2422-1_0_3_node_46 | 0.4 | n |  | TRUE
7 | bus_LV_2422-1_0_3_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_2422-1_0_3_node_45 | 0.4 | n |  | TRUE
9 | bus_LV_2422-1_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2422-1_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2422-1_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2422-1_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2422-1_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2422-1_0_3_node_67 | 0.4 | n |  | TRUE
15 | bus_LV_2422-1_0_3_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_2422-1_0_3_node_66 | 0.4 | n |  | TRUE
17 | bus_LV_2422-1_0_3_node_31 | 0.4 | n |  | TRUE
18 | bus_LV_2422-1_0_3_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2422-1_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2422-1_0_3_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_2422-1_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_2422-1_0_3_node_73 | 0.4 | n |  | TRUE
23 | bus_LV_2422-1_0_3_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_2422-1_0_3_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_2422-1_0_3_node_60 | 0.4 | n |  | TRUE
26 | bus_LV_2422-1_0_3_node_72 | 0.4 | n |  | TRUE
27 | bus_LV_2422-1_0_3_node_80 | 0.4 | n |  | TRUE
28 | bus_LV_2422-1_0_3_node_96 | 0.4 | n |  | TRUE
29 | bus_LV_2422-1_0_3_node_79 | 0.4 | n |  | TRUE
30 | bus_LV_2422-1_0_3_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_2422-1_0_3_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_2422-1_0_3_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_2422-1_0_3_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_2422-1_0_3_node_92 | 0.4 | n |  | TRUE
35 | bus_LV_2422-1_0_3_node_115 | 0.4 | n |  | TRUE
36 | bus_LV_2422-1_0_3_node_108 | 0.4 | n |  | TRUE
37 | bus_LV_2422-1_0_3_node_109 | 0.4 | n |  | TRUE
38 | bus_LV_2422-1_0_3_node_107 | 0.4 | n |  | TRUE
39 | bus_LV_2422-1_0_3_node_111 | 0.4 | n |  | TRUE
40 | bus_LV_2422-1_0_3_node_117 | 0.4 | n |  | TRUE
41 | bus_LV_2422-1_0_3_node_112 | 0.4 | n |  | TRUE
42 | bus_LV_2422-1_0_3_node_113 | 0.4 | n |  | TRUE
43 | bus_LV_2422-1_0_3_node_116 | 0.4 | n |  | TRUE
44 | bus_LV_2422-1_0_3_node_56 | 0.4 | n |  | TRUE
45 | bus_LV_2422-1_0_3_node_53 | 0.4 | n |  | TRUE
46 | bus_LV_2422-1_0_3_node_104 | 0.4 | n |  | TRUE
47 | bus_LV_2422-1_0_3_node_54 | 0.4 | n |  | TRUE
48 | bus_LV_2422-1_0_3_node_20 | 0.4 | n |  | TRUE
49 | bus_LV_2422-1_0_3_node_21 | 0.4 | n |  | TRUE
50 | bus_LV_2422-1_0_3_node_22 | 0.4 | n |  | TRUE
51 | bus_LV_2422-1_0_3_node_23 | 0.4 | n |  | TRUE
52 | bus_LV_2422-1_0_3_node_24 | 0.4 | n |  | TRUE
53 | bus_LV_2422-1_0_3_node_29 | 0.4 | n |  | TRUE
54 | bus_LV_2422-1_0_3_node_78 | 0.4 | n |  | TRUE
55 | bus_LV_2422-1_0_3_node_64 | 0.4 | n |  | TRUE
56 | bus_LV_2422-1_0_3_node_25 | 0.4 | n |  | TRUE
57 | bus_LV_2422-1_0_3_node_89 | 0.4 | n |  | TRUE
58 | bus_LV_2422-1_0_3_node_30 | 0.4 | n |  | TRUE
59 | bus_LV_2422-1_0_3_node_62 | 0.4 | n |  | TRUE
60 | bus_LV_2422-1_0_3_node_91 | 0.4 | n |  | TRUE
61 | bus_LV_2422-1_0_3_node_87 | 0.4 | n |  | TRUE
62 | bus_LV_2422-1_0_3_node_28 | 0.4 | n |  | TRUE
63 | bus_LV_2422-1_0_3_node_85 | 0.4 | n |  | TRUE
64 | bus_LV_2422-1_0_3_node_99 | 0.4 | n |  | TRUE
65 | bus_LV_2422-1_0_3_node_86 | 0.4 | n |  | TRUE
66 | bus_LV_2422-1_0_3_node_106 | 0.4 | n |  | TRUE
67 | bus_LV_2422-1_0_3_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_2422-1_0_3_node_50 | 0.4 | n |  | TRUE
69 | bus_LV_2422-1_0_3_node_49 | 0.4 | n |  | TRUE
70 | bus_LV_2422-1_0_3_node_32 | 0.4 | n |  | TRUE
71 | bus_LV_2422-1_0_3_node_34 | 0.4 | n |  | TRUE
72 | bus_LV_2422-1_0_3_node_35 | 0.4 | n |  | TRUE
73 | bus_LV_2422-1_0_3_node_37 | 0.4 | n |  | TRUE
74 | bus_LV_2422-1_0_3_node_36 | 0.4 | n |  | TRUE
75 | bus_LV_2422-1_0_3_node_38 | 0.4 | n |  | TRUE
76 | bus_LV_2422-1_0_3_node_39 | 0.4 | n |  | TRUE
77 | bus_LV_2422-1_0_3_node_82 | 0.4 | n |  | TRUE
78 | bus_LV_2422-1_0_3_node_81 | 0.4 | n |  | TRUE
79 | bus_LV_2422-1_0_3_node_40 | 0.4 | n |  | TRUE
80 | bus_LV_2422-1_0_3_node_41 | 0.4 | n |  | TRUE
81 | bus_LV_2422-1_0_3_node_42 | 0.4 | n |  | TRUE
82 | bus_LV_2422-1_0_3_node_43 | 0.4 | n |  | TRUE
83 | bus_LV_2422-1_0_3_node_44 | 0.4 | n |  | TRUE
84 | bus_LV_2422-1_0_3_node_94 | 0.4 | n |  | TRUE
85 | bus_LV_2422-1_0_3_node_103 | 0.4 | n |  | TRUE
86 | bus_LV_2422-1_0_3_node_83 | 0.4 | n |  | TRUE
87 | bus_LV_2422-1_0_3_node_69 | 0.4 | n |  | TRUE
88 | bus_LV_2422-1_0_3_node_84 | 0.4 | n |  | TRUE
89 | bus_LV_2422-1_0_3_node_47 | 0.4 | n |  | TRUE
90 | bus_LV_2422-1_0_3_node_48 | 0.4 | n |  | TRUE
91 | bus_LV_2422-1_0_3_node_51 | 0.4 | n |  | TRUE
92 | bus_LV_2422-1_0_3_node_59 | 0.4 | n |  | TRUE
93 | bus_LV_2422-1_0_3_node_58 | 0.4 | n |  | TRUE
94 | bus_LV_2422-1_0_3_node_55 | 0.4 | n |  | TRUE
95 | bus_LV_2422-1_0_3_node_76 | 0.4 | n |  | TRUE
96 | bus_LV_2422-1_0_3_node_77 | 0.4 | n |  | TRUE
97 | bus_LV_2422-1_0_3_node_57 | 0.4 | n |  | TRUE
98 | bus_LV_2422-1_0_3_node_95 | 0.4 | n |  | TRUE
99 | bus_LV_2422-1_0_3_node_61 | 0.4 | n |  | TRUE
100 | bus_LV_2422-1_0_3_node_63 | 0.4 | n |  | TRUE
101 | bus_LV_2422-1_0_3_node_65 | 0.4 | n |  | TRUE
102 | bus_LV_2422-1_0_3_node_68 | 0.4 | n |  | TRUE
103 | bus_LV_2422-1_0_3_node_70 | 0.4 | n |  | TRUE
104 | bus_LV_2422-1_0_3_node_93 | 0.4 | n |  | TRUE
105 | bus_LV_2422-1_0_3_node_101 | 0.4 | n |  | TRUE
106 | bus_LV_2422-1_0_3_node_102 | 0.4 | n |  | TRUE
107 | bus_LV_2422-1_0_3_node_75 | 0.4 | n |  | TRUE
108 | bus_LV_2422-1_0_3_node_71 | 0.4 | n |  | TRUE
109 | bus_LV_2422-1_0_3_node_74 | 0.4 | n |  | TRUE
110 | bus_LV_2422-1_0_3_node_97 | 0.4 | n |  | TRUE
111 | bus_LV_2422-1_0_3_node_98 | 0.4 | n |  | TRUE
112 | bus_LV_2422-1_0_3_node_100 | 0.4 | n |  | TRUE
113 | bus_LV_2422-1_0_3_node_105 | 0.4 | n |  | TRUE
114 | bus_LV_2422-1_0_3_node_88 | 0.4 | n |  | TRUE
115 | bus_LV_2422-1_0_3_node_90 | 0.4 | n |  | TRUE
116 | bus_LV_2422-1_0_3_node_110 | 0.4 | n |  | TRUE
117 | bus_MV_333_0_node_30 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2422-1_0_3_load_0 | 0 | 0.0016087 | 0.00040317 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2422-1_0_3_load_1 | 1 | 0.0011886 | 0.00029789 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2422-1_0_3_load_2 | 2 | 0.0013708 | 0.00034355 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2422-1_0_3_load_3 | 3 | 0.0017456 | 0.0004375 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2422-1_0_3_load_4 | 4 | 0.0021532 | 0.00053964 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2422-1_0_3_load_26 | 5 | 0.0018837 | 0.00047211 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2422-1_0_3_load_46 | 6 | 0.001488 | 0.00037293 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2422-1_0_3_load_27 | 7 | 0.0017574 | 0.00044044 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2422-1_0_3_load_45 | 8 | 0.0018531 | 0.00046443 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2422-1_0_3_load_5 | 9 | 0.0012377 | 0.00031018 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2422-1_0_3_load_6 | 10 | 0.00073543 | 0.00018432 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2422-1_0_3_load_7 | 11 | 0.00078747 | 0.00019736 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2422-1_0_3_load_8 | 12 | 0.00066179 | 0.00016586 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2422-1_0_3_load_9 | 13 | 0.0015326 | 0.0003841 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2422-1_0_3_load_67 | 14 | 0.00069209 | 0.00017345 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2422-1_0_3_load_33 | 15 | 0.00080755 | 0.00020239 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2422-1_0_3_load_66 | 16 | 0.00038605 | 9.6754e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2422-1_0_3_load_31 | 17 | 0.0012129 | 0.00030398 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2422-1_0_3_load_10 | 18 | 0.0036072 | 0.00090405 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2422-1_0_3_load_11 | 19 | 0.00075661 | 0.00018962 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2422-1_0_3_load_13 | 21 | 0.00058118 | 0.00014566 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2422-1_0_3_load_73 | 22 | 0.0024986 | 0.00062622 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2422-1_0_3_load_14 | 23 | 0.0026564 | 0.00066577 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2422-1_0_3_load_15 | 24 | 0.0028542 | 0.00071534 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2422-1_0_3_load_60 | 25 | 0.0018248 | 0.00045733 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2422-1_0_3_load_72 | 26 | 0.0011582 | 0.00029026 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2422-1_0_3_load_80 | 27 | 0.0025782 | 0.00064617 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2422-1_0_3_load_96 | 28 | 0.0022839 | 0.0005724 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2422-1_0_3_load_79 | 29 | 0.0037189 | 0.00093203 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2422-1_0_3_load_16 | 30 | 0.0031035 | 0.0007778 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2422-1_0_3_load_17 | 31 | 0.012622 | 0.0031635 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2422-1_0_3_load_18 | 32 | 0.0030922 | 0.00077498 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2422-1_0_3_load_19 | 33 | 0.001283 | 0.00032155 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2422-1_0_3_load_92 | 34 | 0.00077181 | 0.00019343 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2422-1_0_3_load_115 | 35 | 0.0013367 | 0.00033502 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2422-1_0_3_load_108 | 36 | 0.0013556 | 0.00033974 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2422-1_0_3_load_107 | 38 | 0.0048377 | 0.0012124 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2422-1_0_3_load_111 | 39 | 0.0010841 | 0.00027169 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2422-1_0_3_load_117 | 40 | 0.01094 | 0.0027419 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2422-1_0_3_load_112 | 41 | 0.0013448 | 0.00033705 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2422-1_0_3_load_113 | 42 | 0.0011615 | 0.00029109 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2422-1_0_3_load_116 | 43 | 0.001345 | 0.0003371 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2422-1_0_3_load_56 | 44 | 0.0068973 | 0.0017286 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2422-1_0_3_load_53 | 45 | 0.0012433 | 0.0003116 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2422-1_0_3_load_104 | 46 | 0.0010276 | 0.00025755 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2422-1_0_3_load_54 | 47 | 0.0030322 | 0.00075994 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2422-1_0_3_load_20 | 48 | 0.0035016 | 0.00087759 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2422-1_0_3_load_21 | 49 | 0.0012043 | 0.00030183 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2422-1_0_3_load_23 | 51 | 0.0012959 | 0.00032479 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2422-1_0_3_load_29 | 53 | 0.001436 | 0.0003599 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2422-1_0_3_load_78 | 54 | 0.0023257 | 0.00058287 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2422-1_0_3_load_64 | 55 | 0.0035696 | 0.00089463 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2422-1_0_3_load_25 | 56 | 0.00083595 | 0.00020951 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2422-1_0_3_load_30 | 58 | 0.0013565 | 0.00033998 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2422-1_0_3_load_62 | 59 | 0.0026431 | 0.00066244 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2422-1_0_3_load_91 | 60 | 0.00060068 | 0.00015054 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2422-1_0_3_load_87 | 61 | 0.00097676 | 0.0002448 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2422-1_0_3_load_85 | 63 | 0.0022323 | 0.00055947 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2422-1_0_3_load_99 | 64 | 0.001192 | 0.00029875 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2422-1_0_3_load_106 | 66 | 0.0009871 | 0.00024739 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2422-1_0_3_load_50 | 68 | 0.0018162 | 0.00045519 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2422-1_0_3_load_49 | 69 | 0.001602 | 0.00040151 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2422-1_0_3_load_32 | 70 | 0.0013454 | 0.0003372 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2422-1_0_3_load_34 | 71 | 0.0028672 | 0.0007186 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2422-1_0_3_load_35 | 72 | 0.0028246 | 0.00070792 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2422-1_0_3_load_36 | 74 | 0.0028685 | 0.00071892 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2422-1_0_3_load_38 | 75 | 0.0013091 | 0.0003281 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2422-1_0_3_load_39 | 76 | 0.0018926 | 0.00047433 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2422-1_0_3_load_82 | 77 | 0.0030783 | 0.00077149 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2422-1_0_3_load_81 | 78 | 0.0018099 | 0.0004536 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2422-1_0_3_load_40 | 79 | 0.0030258 | 0.00075834 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2422-1_0_3_load_41 | 80 | 0.0014202 | 0.00035594 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2422-1_0_3_load_44 | 83 | 0.0013509 | 0.00033858 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2422-1_0_3_load_103 | 85 | 0.0021562 | 0.00054039 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2422-1_0_3_load_83 | 86 | 0.0012543 | 0.00031436 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2422-1_0_3_load_69 | 87 | 0.0036445 | 0.00091339 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2422-1_0_3_load_84 | 88 | 0.0016848 | 0.00042224 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2422-1_0_3_load_47 | 89 | 0.00097511 | 0.00024439 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2422-1_0_3_load_48 | 90 | 0.0017177 | 0.00043049 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2422-1_0_3_load_51 | 91 | 0.0018206 | 0.00045628 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2422-1_0_3_load_55 | 94 | 0.0014627 | 0.00036659 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2422-1_0_3_load_76 | 95 | 0.0014897 | 0.00037336 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2422-1_0_3_load_57 | 97 | 0.0016828 | 0.00042174 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2422-1_0_3_load_95 | 98 | 0.0017816 | 0.00044651 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2422-1_0_3_load_61 | 99 | 0.0021484 | 0.00053844 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2422-1_0_3_load_63 | 100 | 0.0022987 | 0.0005761 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2422-1_0_3_load_65 | 101 | 0.0012455 | 0.00031215 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2422-1_0_3_load_70 | 103 | 0.00071814 | 0.00017998 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2422-1_0_3_load_93 | 104 | 0.0015198 | 0.00038089 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2422-1_0_3_load_102 | 106 | 0.0020819 | 0.00052178 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2422-1_0_3_load_75 | 107 | 0.0013698 | 0.0003433 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2422-1_0_3_load_71 | 108 | 0.00079388 | 0.00019896 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2422-1_0_3_load_98 | 111 | 0.0026369 | 0.00066088 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2422-1_0_3_load_100 | 112 | 0.00097322 | 0.00024391 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2422-1_0_3_load_105 | 113 | 0.0018901 | 0.0004737 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2422-1_0_3_load_88 | 114 | 0.00065283 | 0.00016362 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2422-1_0_3_load_90 | 115 | 0.0023876 | 0.00059839 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2422-1_0_3_load_110 | 116 | 0.0013439 | 0.0003368 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 59 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2422-1_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.022776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2422-1_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0025665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2422-1_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0012794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2422-1_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.023299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2422-1_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.023807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2422-1_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0064029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2422-1_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.0017763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2422-1_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.023383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2422-1_0_3_line_8 | NAYY 4x150 SE | 7 | 62 | 0.023025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2422-1_0_3_line_9 | NAYY 4x150 SE | 8 | 89 | 0.0018884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2422-1_0_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.0064193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2422-1_0_3_line_11 | NAYY 4x150 SE | 9 | 11 | 0.016338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2422-1_0_3_line_12 | NAYY 4x150 SE | 10 | 12 | 0.026102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2422-1_0_3_line_13 | NAYY 4x150 SE | 11 | 13 | 0.01104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2422-1_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.026898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2422-1_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.014304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2422-1_0_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.0307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2422-1_0_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.0098771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2422-1_0_3_line_18 | NAYY 4x150 SE | 16 | 102 | 0.023566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2422-1_0_3_line_19 | NAYY 4x150 SE | 17 | 70 | 0.015371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2422-1_0_3_line_20 | NAYY 4x150 SE | 18 | 19 | 0.014104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2422-1_0_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.0050002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2422-1_0_3_line_22 | NAYY 4x150 SE | 19 | 21 | 0.01357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2422-1_0_3_line_23 | NAYY 4x150 SE | 19 | 22 | 0.10646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2422-1_0_3_line_24 | NAYY 4x150 SE | 20 | 23 | 0.020101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2422-1_0_3_line_25 | NAYY 4x150 SE | 20 | 24 | 0.014047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2422-1_0_3_line_26 | NAYY 4x150 SE | 21 | 25 | 0.021251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2422-1_0_3_line_27 | NAYY 4x150 SE | 22 | 26 | 0.026811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2422-1_0_3_line_28 | NAYY 4x150 SE | 24 | 27 | 0.017826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2422-1_0_3_line_29 | NAYY 4x150 SE | 25 | 28 | 0.0062363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2422-1_0_3_line_30 | NAYY 4x150 SE | 26 | 108 | 0.020864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2422-1_0_3_line_31 | NAYY 4x150 SE | 27 | 29 | 0.008406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2422-1_0_3_line_32 | NAYY 4x150 SE | 28 | 98 | 0.0060937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2422-1_0_3_line_33 | NAYY 4x150 SE | 29 | 54 | 0.0094092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2422-1_0_3_line_34 | NAYY 4x150 SE | 30 | 31 | 0.0023215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2422-1_0_3_line_35 | NAYY 4x150 SE | 30 | 32 | 0.040075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2422-1_0_3_line_36 | NAYY 4x150 SE | 32 | 33 | 0.024272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2422-1_0_3_line_37 | NAYY 4x150 SE | 33 | 44 | 0.027053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2422-1_0_3_line_38 | NAYY 4x150 SE | 33 | 45 | 0.014854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2422-1_0_3_line_39 | NAYY 4x150 SE | 34 | 35 | 0.094926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2422-1_0_3_line_40 | NAYY 4x150 SE | 35 | 43 | 0.00026762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2422-1_0_3_line_41 | NAYY 4x150 SE | 35 | 42 | 0.031259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2422-1_0_3_line_42 | NAYY 4x150 SE | 36 | 37 | 0.0091557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2422-1_0_3_line_43 | NAYY 4x150 SE | 36 | 38 | 0.02162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2422-1_0_3_line_44 | NAYY 4x150 SE | 37 | 39 | 0.011203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2422-1_0_3_line_45 | NAYY 4x150 SE | 38 | 75 | 0.0016705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2422-1_0_3_line_46 | NAYY 4x150 SE | 39 | 40 | 0.017382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2422-1_0_3_line_47 | NAYY 4x150 SE | 40 | 43 | 0.0053858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2422-1_0_3_line_48 | NAYY 4x150 SE | 41 | 42 | 0.0010867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2422-1_0_3_line_49 | NAYY 4x150 SE | 44 | 46 | 0.0098226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2422-1_0_3_line_50 | NAYY 4x150 SE | 45 | 47 | 0.018369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2422-1_0_3_line_51 | NAYY 4x150 SE | 46 | 92 | 0.016376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2422-1_0_3_line_52 | NAYY 4x150 SE | 47 | 94 | 0.00017354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2422-1_0_3_line_53 | NAYY 4x150 SE | 48 | 49 | 0.024028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2422-1_0_3_line_54 | NAYY 4x150 SE | 48 | 50 | 0.017064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2422-1_0_3_line_55 | NAYY 4x150 SE | 49 | 51 | 0.020877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2422-1_0_3_line_56 | NAYY 4x150 SE | 50 | 52 | 0.029891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2422-1_0_3_line_57 | NAYY 4x150 SE | 51 | 53 | 0.020283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2422-1_0_3_line_58 | NAYY 4x150 SE | 52 | 54 | 0.0084817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2422-1_0_3_line_59 | NAYY 4x150 SE | 52 | 55 | 0.0090958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
60 | LV_2422-1_0_3_line_60 | NAYY 4x150 SE | 53 | 58 | 0.024337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2422-1_0_3_line_61 | NAYY 4x150 SE | 55 | 59 | 0.0082352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
62 | LV_2422-1_0_3_line_62 | NAYY 4x150 SE | 56 | 57 | 0.018931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2422-1_0_3_line_63 | NAYY 4x150 SE | 57 | 60 | 0.014607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2422-1_0_3_line_64 | NAYY 4x150 SE | 57 | 61 | 0.011689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2422-1_0_3_line_65 | NAYY 4x150 SE | 58 | 68 | 0.025644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2422-1_0_3_line_66 | NAYY 4x150 SE | 59 | 99 | 0.012316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2422-1_0_3_line_67 | NAYY 4x150 SE | 60 | 90 | 0.021909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2422-1_0_3_line_68 | NAYY 4x150 SE | 61 | 114 | 0.015772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2422-1_0_3_line_69 | NAYY 4x150 SE | 62 | 63 | 0.0050151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2422-1_0_3_line_70 | NAYY 4x150 SE | 63 | 64 | 0.011149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2422-1_0_3_line_71 | NAYY 4x150 SE | 64 | 112 | 0.0061382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2422-1_0_3_line_72 | NAYY 4x150 SE | 65 | 66 | 0.018425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2422-1_0_3_line_73 | NAYY 4x150 SE | 65 | 67 | 0.009075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2422-1_0_3_line_74 | NAYY 4x150 SE | 66 | 113 | 0.0030039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2422-1_0_3_line_75 | NAYY 4x150 SE | 67 | 91 | 0.018975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2422-1_0_3_line_76 | NAYY 4x150 SE | 68 | 69 | 0.012271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2422-1_0_3_line_77 | NAYY 4x150 SE | 69 | 91 | 0.016003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2422-1_0_3_line_78 | NAYY 4x150 SE | 71 | 72 | 0.015234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2422-1_0_3_line_79 | NAYY 4x150 SE | 71 | 73 | 0.050146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2422-1_0_3_line_80 | NAYY 4x150 SE | 72 | 74 | 0.015233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2422-1_0_3_line_81 | NAYY 4x150 SE | 73 | 75 | 0.032465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2422-1_0_3_line_82 | NAYY 4x150 SE | 73 | 76 | 0.023837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2422-1_0_3_line_83 | NAYY 4x150 SE | 74 | 77 | 0.02553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2422-1_0_3_line_84 | NAYY 4x150 SE | 77 | 78 | 5.6074e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2422-1_0_3_line_85 | NAYY 4x150 SE | 78 | 96 | 0.018878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2422-1_0_3_line_86 | NAYY 4x150 SE | 79 | 80 | 0.0029159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2422-1_0_3_line_87 | NAYY 4x150 SE | 79 | 81 | 0.032986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2422-1_0_3_line_88 | NAYY 4x150 SE | 81 | 82 | 0.023966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2422-1_0_3_line_89 | NAYY 4x150 SE | 81 | 83 | 0.0019899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2422-1_0_3_line_90 | NAYY 4x150 SE | 82 | 84 | 0.022892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2422-1_0_3_line_91 | NAYY 4x150 SE | 82 | 85 | 0.019599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2422-1_0_3_line_92 | NAYY 4x150 SE | 83 | 86 | 0.021846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2422-1_0_3_line_93 | NAYY 4x150 SE | 84 | 87 | 0.017793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2422-1_0_3_line_94 | NAYY 4x150 SE | 86 | 88 | 0.017954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2422-1_0_3_line_95 | NAYY 4x150 SE | 87 | 104 | 0.010573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2422-1_0_3_line_96 | NAYY 4x150 SE | 87 | 102 | 0.021377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2422-1_0_3_line_97 | NAYY 4x150 SE | 88 | 110 | 0.067101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2422-1_0_3_line_98 | NAYY 4x150 SE | 89 | 90 | 0.010034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2422-1_0_3_line_99 | NAYY 4x150 SE | 92 | 93 | 0.00308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2422-1_0_3_line_100 | NAYY 4x150 SE | 93 | 97 | 0.015366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2422-1_0_3_line_101 | NAYY 4x150 SE | 94 | 95 | 0.015998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2422-1_0_3_line_102 | NAYY 4x150 SE | 95 | 96 | 0.012406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2422-1_0_3_line_103 | NAYY 4x150 SE | 96 | 101 | 0.0076985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2422-1_0_3_line_104 | NAYY 4x150 SE | 98 | 115 | 0.0062814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2422-1_0_3_line_105 | NAYY 4x150 SE | 99 | 100 | 0.011283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2422-1_0_3_line_106 | NAYY 4x150 SE | 100 | 101 | 0.017935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2422-1_0_3_line_107 | NAYY 4x150 SE | 102 | 103 | 0.04105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2422-1_0_3_line_108 | NAYY 4x150 SE | 103 | 105 | 0.0069304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2422-1_0_3_line_109 | NAYY 4x150 SE | 105 | 106 | 0.018819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2422-1_0_3_line_110 | NAYY 4x150 SE | 105 | 107 | 0.027032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2422-1_0_3_line_111 | NAYY 4x150 SE | 106 | 116 | 0.0013933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2422-1_0_3_line_112 | NAYY 4x150 SE | 107 | 109 | 0.016918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2422-1_0_3_line_113 | NAYY 4x150 SE | 108 | 109 | 0.060609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2422-1_0_3_line_114 | NAYY 4x150 SE | 110 | 111 | 0.006663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2422-1_0_3_line_115 | NAYY 4x150 SE | 114 | 115 | 0.011174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2422-1_0_3_trafo_62 | 0.25 MVA 20/0.4 kV | 117 | 59 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2620269.9057 | 1240928.6571 | 2620249.4042 | 1240918.7364
1 | 2620269.9057 | 1240928.6571 | 2620272.216 | 1240929.775
2 | 2620248.2526 | 1240918.1792 | 2620249.4042 | 1240918.7364
3 | 2620272.216 | 1240929.775 | 2620293.1883 | 1240939.9235
4 | 2620248.2526 | 1240918.1792 | 2620226.8226 | 1240907.8093
5 | 2620298.9519 | 1240942.7125 | 2620293.1883 | 1240939.9235
6 | 2620225.2237 | 1240907.0355 | 2620226.8226 | 1240907.8093
7 | 2620320.0002 | 1240952.8977 | 2620298.9519 | 1240942.7125
8 | 2620204.4974 | 1240897.0061 | 2620225.2237 | 1240907.0355
9 | 2620320.0002 | 1240952.8977 | 2620321.7 | 1240953.7202
10 | 2620623.3062 | 1241248.6746 | 2620616.8895 | 1241248.4928
11 | 2620623.3062 | 1241248.6746 | 2620639.6374 | 1241249.1374
12 | 2620616.8895 | 1241248.4928 | 2620596.4749 | 1241247.9143 | 2620590.7966 | 1241248.0008
13 | 2620650.673 | 1241249.4501 | 2620639.6374 | 1241249.1374
14 | 2620590.7966 | 1241248.0008 | 2620563.9018 | 1241248.4106
15 | 2620650.673 | 1241249.4501 | 2620664.9711 | 1241249.8553
16 | 2620533.2058 | 1241248.8784 | 2620563.9018 | 1241248.4106
17 | 2620664.9711 | 1241249.8553 | 2620674.8443 | 1241250.1351
18 | 2620509.6429 | 1241249.2375 | 2620533.2058 | 1241248.8784
19 | 2620690.104 | 1241251.5381 | 2620684.1027 | 1241250.3975 | 2620674.8443 | 1241250.1351
20 | 2620395.5347 | 1241059.741 | 2620396.8023 | 1241063.6999 | 2620396.4228 | 1241068.5572 | 2620392.9626 | 1241072.2699
21 | 2620388.2019 | 1241073.799 | 2620392.9626 | 1241072.2699
22 | 2620395.5347 | 1241059.741 | 2620391.3966 | 1241046.8173
23 | 2620395.5347 | 1241059.741 | 2620500.78 | 1241075.7928
24 | 2620388.2019 | 1241073.799 | 2620378.5587 | 1241085.9402 | 2620377.0174 | 1241090.2705
25 | 2620388.2019 | 1241073.799 | 2620375.2581 | 1241068.342
26 | 2620384.9161 | 1241026.578 | 2620391.3966 | 1241046.8173
27 | 2620500.78 | 1241075.7928 | 2620494.4039 | 1241099.402 | 2620494.188 | 1241101.7477
28 | 2620375.2581 | 1241068.342 | 2620358.8325 | 1241061.4172
29 | 2620383.0144 | 1241020.6388 | 2620384.9161 | 1241026.578
30 | 2620492.276 | 1241122.5239 | 2620494.188 | 1241101.7477
31 | 2620351.0868 | 1241058.1517 | 2620358.8325 | 1241061.4172
32 | 2620383.0144 | 1241020.6388 | 2620381.1561 | 1241014.8353
33 | 2620351.0868 | 1241058.1517 | 2620342.4166 | 1241054.4964
34 | 2620195.8479 | 1241061.0403 | 2620195.0918 | 1241063.2352
35 | 2620208.8986 | 1241023.1503 | 2620195.8479 | 1241061.0403
36 | 2620216.803 | 1241000.2015 | 2620208.8986 | 1241023.1503
37 | 2620216.803 | 1241000.2015 | 2620192.0085 | 1240989.38
38 | 2620216.803 | 1241000.2015 | 2620230.4301 | 1241006.1137
39 | 2620142.0368 | 1241112.1331 | 2620107.7023 | 1241200.6326
40 | 2620142.2898 | 1241112.2204 | 2620142.0368 | 1241112.1331
41 | 2620112.4879 | 1241101.9366 | 2620142.0368 | 1241112.1331
42 | 2620174.4027 | 1241123.3016 | 2620183.0761 | 1241126.2338
43 | 2620203.5571 | 1241133.1577 | 2620183.0761 | 1241126.2338
44 | 2620174.4027 | 1241123.3016 | 2620163.8122 | 1241119.6471
45 | 2620203.5571 | 1241133.1577 | 2620205.1396 | 1241133.6927
46 | 2620163.8122 | 1241119.6471 | 2620147.381 | 1241113.9772
47 | 2620142.2898 | 1241112.2204 | 2620147.381 | 1241113.9772
48 | 2620111.4606 | 1241101.5821 | 2620112.4879 | 1241101.9366
49 | 2620183.006 | 1240985.4509 | 2620192.0085 | 1240989.38
50 | 2620230.4301 | 1241006.1137 | 2620247.281 | 1241013.4245
51 | 2620167.9973 | 1240978.9004 | 2620183.006 | 1240985.4509
52 | 2620247.281 | 1241013.4245 | 2620247.4402 | 1241013.4936
53 | 2620329.4251 | 1241015.6903 | 2620307.7782 | 1241005.2615
54 | 2620344.7977 | 1241023.0964 | 2620329.4251 | 1241015.6903
55 | 2620307.7782 | 1241005.2615 | 2620288.9701 | 1240996.2003
56 | 2620334.601 | 1241051.2014 | 2620344.7977 | 1241023.0964
57 | 2620270.6973 | 1240987.397 | 2620288.9701 | 1240996.2003
58 | 2620334.601 | 1241051.2014 | 2620342.4166 | 1241054.4964
59 | 2620334.601 | 1241051.2014 | 2620326.2513 | 1241047.5935
60 | 2620248.7721 | 1240976.8341 | 2620270.6973 | 1240987.397
61 | 2620326.2513 | 1241047.5935 | 2620318.6917 | 1241044.327
62 | 2620363.6021 | 1240973.9966 | 2620356.8313 | 1240991.6758
63 | 2620363.6021 | 1240973.9966 | 2620350.4537 | 1240967.6341
64 | 2620363.6021 | 1240973.9966 | 2620370.4094 | 1240983.4987
65 | 2620225.6698 | 1240965.7041 | 2620248.7721 | 1240976.8341
66 | 2620307.3861 | 1241039.4419 | 2620318.6917 | 1241044.327
67 | 2620350.4537 | 1240967.6341 | 2620330.7325 | 1240958.0911
68 | 2620370.4094 | 1240983.4987 | 2620371.6984 | 1240985.2981 | 2620375.8331 | 1240998.211
69 | 2620204.4974 | 1240897.0061 | 2620200.0397 | 1240894.7084
70 | 2620200.0397 | 1240894.7084 | 2620190.1293 | 1240889.6001
71 | 2620190.1293 | 1240889.6001 | 2620184.6733 | 1240886.7878
72 | 2620186.7989 | 1240936.9044 | 2620170.0077 | 1240929.3202
73 | 2620186.7989 | 1240936.9044 | 2620183.104 | 1240945.1971
74 | 2620167.2701 | 1240928.0837 | 2620170.0077 | 1240929.3202
75 | 2620183.104 | 1240945.1971 | 2620200.1984 | 1240953.4327
76 | 2620214.6151 | 1240960.3782 | 2620225.6698 | 1240965.7041
77 | 2620214.6151 | 1240960.3782 | 2620200.1984 | 1240953.4327
78 | 2620255.5505 | 1241081.7348 | 2620250.9705 | 1241096.2643
79 | 2620250.9705 | 1241096.2643 | 2620235.895 | 1241144.09
80 | 2620255.5505 | 1241081.7348 | 2620260.1302 | 1241067.2061
81 | 2620235.895 | 1241144.09 | 2620205.1396 | 1241133.6927
82 | 2620235.895 | 1241144.09 | 2620228.5942 | 1241166.7813
83 | 2620267.8054 | 1241042.8569 | 2620260.1302 | 1241067.2061
84 | 2620267.8223 | 1241042.8035 | 2620267.8054 | 1241042.8569
85 | 2620273.4977 | 1241024.7987 | 2620267.8223 | 1241042.8035
86 | 2620435.2026 | 1241213.4184 | 2620435.7626 | 1241210.5568
87 | 2620428.8678 | 1241245.7908 | 2620435.2026 | 1241213.4184
88 | 2620428.8678 | 1241245.7908 | 2620433.086 | 1241245.8832 | 2620436.3573 | 1241246.5059 | 2620439.4973 | 1241247.962 | 2620441.8809 | 1241249.5379 | 2620443.3959 | 1241250.8772 | 2620444.5717 | 1241251.9042 | 2620448.2977 | 1241256.6199 | 2620448.6364 | 1241257.0547
89 | 2620428.8678 | 1241245.7908 | 2620426.8812 | 1241245.6754
90 | 2620448.6364 | 1241257.0547 | 2620459.2251 | 1241253.5444 | 2620470.3668 | 1241249.6692
91 | 2620448.6364 | 1241257.0547 | 2620450.3068 | 1241261.5855 | 2620450.7379 | 1241265.9342 | 2620450.429 | 1241270.0134 | 2620449.0923 | 1241276.1794
92 | 2620405.0724 | 1241244.4087 | 2620426.8812 | 1241245.6754
93 | 2620470.3668 | 1241249.6692 | 2620488.203 | 1241249.0969
94 | 2620405.0724 | 1241244.4087 | 2620389.2004 | 1241243.4867 | 2620387.1507 | 1241243.3289
95 | 2620488.203 | 1241249.0969 | 2620488.3941 | 1241259.6679
96 | 2620488.203 | 1241249.0969 | 2620490.9624 | 1241249.1175 | 2620509.6429 | 1241249.2375
97 | 2620387.1507 | 1241243.3289 | 2620320.3188 | 1241237.3251
98 | 2620321.7 | 1240953.7202 | 2620330.7325 | 1240958.0911
99 | 2620165.1968 | 1240977.6012 | 2620167.9973 | 1240978.9004
100 | 2620165.1968 | 1240977.6012 | 2620151.1113 | 1240971.4602
101 | 2620247.4402 | 1241013.4936 | 2620262.1164 | 1241019.8608
102 | 2620273.4977 | 1241024.7987 | 2620262.1164 | 1241019.8608
103 | 2620273.4977 | 1241024.7987 | 2620280.5648 | 1241027.8523
104 | 2620379.2407 | 1241008.8531 | 2620381.1561 | 1241014.8353
105 | 2620307.3861 | 1241039.4419 | 2620297.0284 | 1241034.9663
106 | 2620280.5648 | 1241027.8523 | 2620297.0284 | 1241034.9663
107 | 2620509.6429 | 1241249.2375 | 2620517.4156 | 1241227.0392 | 2620520.98 | 1241212.8648 | 2620520.8893 | 1241209.9513
108 | 2620520.6737 | 1241203.0242 | 2620520.8893 | 1241209.9513
109 | 2620520.6737 | 1241203.0242 | 2620527.0449 | 1241199.2105 | 2620538.3832 | 1241200.3327
110 | 2620520.6737 | 1241203.0242 | 2620516.1966 | 1241192.5022 | 2620509.0207 | 1241186.3069 | 2620503.0534 | 1241184.9633
111 | 2620538.3832 | 1241200.3327 | 2620539.7697 | 1241200.47
112 | 2620486.2993 | 1241182.8376 | 2620498.49 | 1241183.9358 | 2620503.0534 | 1241184.9633
113 | 2620486.2993 | 1241182.8376 | 2620492.276 | 1241122.5239
114 | 2620319.4042 | 1241243.915 | 2620320.2452 | 1241238.9481 | 2620320.3188 | 1241237.3251
115 | 2620379.2407 | 1241008.8531 | 2620375.8331 | 1240998.211

## bus_geodata
| x | y | coords
0 | 2620269.9057 | 1240928.6571
1 | 2620249.4042 | 1240918.7364
2 | 2620272.216 | 1240929.775
3 | 2620248.2526 | 1240918.1792
4 | 2620293.1883 | 1240939.9235
5 | 2620226.8226 | 1240907.8093
6 | 2620298.9519 | 1240942.7125
7 | 2620225.2237 | 1240907.0355
8 | 2620320.0002 | 1240952.8977
9 | 2620623.3062 | 1241248.6746
10 | 2620616.8895 | 1241248.4928
11 | 2620639.6374 | 1241249.1374
12 | 2620590.7966 | 1241248.0008
13 | 2620650.673 | 1241249.4501
14 | 2620563.9018 | 1241248.4106
15 | 2620664.9711 | 1241249.8553
16 | 2620533.2058 | 1241248.8784
17 | 2620674.8443 | 1241250.1351
18 | 2620392.9626 | 1241072.2699
19 | 2620395.5347 | 1241059.741
20 | 2620388.2019 | 1241073.799
21 | 2620391.3966 | 1241046.8173
22 | 2620500.78 | 1241075.7928
23 | 2620377.0174 | 1241090.2705
24 | 2620375.2581 | 1241068.342
25 | 2620384.9161 | 1241026.578
26 | 2620494.188 | 1241101.7477
27 | 2620358.8325 | 1241061.4172
28 | 2620383.0144 | 1241020.6388
29 | 2620351.0868 | 1241058.1517
30 | 2620195.8479 | 1241061.0403
31 | 2620195.0918 | 1241063.2352
32 | 2620208.8986 | 1241023.1503
33 | 2620216.803 | 1241000.2015
34 | 2620107.7023 | 1241200.6326
35 | 2620142.0368 | 1241112.1331
36 | 2620183.0761 | 1241126.2338
37 | 2620174.4027 | 1241123.3016
38 | 2620203.5571 | 1241133.1577
39 | 2620163.8122 | 1241119.6471
40 | 2620147.381 | 1241113.9772
41 | 2620111.4606 | 1241101.5821
42 | 2620112.4879 | 1241101.9366
43 | 2620142.2898 | 1241112.2204
44 | 2620192.0085 | 1240989.38
45 | 2620230.4301 | 1241006.1137
46 | 2620183.006 | 1240985.4509
47 | 2620247.281 | 1241013.4245
48 | 2620329.4251 | 1241015.6903
49 | 2620307.7782 | 1241005.2615
50 | 2620344.7977 | 1241023.0964
51 | 2620288.9701 | 1240996.2003
52 | 2620334.601 | 1241051.2014
53 | 2620270.6973 | 1240987.397
54 | 2620342.4166 | 1241054.4964
55 | 2620326.2513 | 1241047.5935
56 | 2620356.8313 | 1240991.6758
57 | 2620363.6021 | 1240973.9966
58 | 2620248.7721 | 1240976.8341
59 | 2620318.6917 | 1241044.327
60 | 2620350.4537 | 1240967.6341
61 | 2620370.4094 | 1240983.4987
62 | 2620204.4974 | 1240897.0061
63 | 2620200.0397 | 1240894.7084
64 | 2620190.1293 | 1240889.6001
65 | 2620186.7989 | 1240936.9044
66 | 2620170.0077 | 1240929.3202
67 | 2620183.104 | 1240945.1971
68 | 2620225.6698 | 1240965.7041
69 | 2620214.6151 | 1240960.3782
70 | 2620690.104 | 1241251.5381
71 | 2620250.9705 | 1241096.2642
72 | 2620255.5505 | 1241081.7348
73 | 2620235.895 | 1241144.09
74 | 2620260.1302 | 1241067.2061
75 | 2620205.1396 | 1241133.6927
76 | 2620228.5942 | 1241166.7813
77 | 2620267.8054 | 1241042.8569
78 | 2620267.8223 | 1241042.8035
79 | 2620435.2026 | 1241213.4184
80 | 2620435.7626 | 1241210.5568
81 | 2620428.8678 | 1241245.7908
82 | 2620448.6364 | 1241257.0547
83 | 2620426.8812 | 1241245.6754
84 | 2620470.3668 | 1241249.6692
85 | 2620449.0923 | 1241276.1794
86 | 2620405.0724 | 1241244.4087
87 | 2620488.203 | 1241249.0969
88 | 2620387.1507 | 1241243.3289
89 | 2620321.7 | 1240953.7202
90 | 2620330.7325 | 1240958.0911
91 | 2620200.1984 | 1240953.4327
92 | 2620167.9973 | 1240978.9004
93 | 2620165.1968 | 1240977.6012
94 | 2620247.4402 | 1241013.4936
95 | 2620262.1164 | 1241019.8608
96 | 2620273.4977 | 1241024.7987
97 | 2620151.1113 | 1240971.4602
98 | 2620381.1561 | 1241014.8353
99 | 2620307.3861 | 1241039.4419
100 | 2620297.0284 | 1241034.9663
101 | 2620280.5648 | 1241027.8523
102 | 2620509.6429 | 1241249.2375
103 | 2620520.8893 | 1241209.9513
104 | 2620488.3941 | 1241259.6679
105 | 2620520.6737 | 1241203.0242
106 | 2620538.3832 | 1241200.3327
107 | 2620503.0534 | 1241184.9633
108 | 2620492.276 | 1241122.5239
109 | 2620486.2993 | 1241182.8376
110 | 2620320.3188 | 1241237.3251
111 | 2620319.4042 | 1241243.915
112 | 2620184.6733 | 1240886.7878
113 | 2620167.2701 | 1240928.0837
114 | 2620375.8331 | 1240998.211
115 | 2620379.2407 | 1241008.8531
116 | 2620539.7697 | 1241200.47
117 | 2620334.601 | 1241051.2014

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98281 | -0.12036 | 0.0016087 | 0.00040317
1 | 0.98245 | -0.12295 | 0.0011886 | 0.00029789
2 | 0.98286 | -0.12003 | 0.0013708 | 0.00034355
3 | 0.98243 | -0.12307 | 0.0017456 | 0.0004375
4 | 0.98333 | -0.11667 | 0.0021532 | 0.00053964
5 | 0.98215 | -0.12506 | 0.0018837 | 0.00047211
6 | 0.98348 | -0.1156 | 0.001488 | 0.00037293
7 | 0.98214 | -0.12517 | 0.0017574 | 0.00044044
8 | 0.98408 | -0.11136 | 0.0018531 | 0.00046443
9 | 0.97261 | -0.19277 | 0.0012377 | 0.00031018
10 | 0.97268 | -0.1923 | 0.00073543 | 0.00018432
11 | 0.97248 | -0.19376 | 0.00078747 | 0.00019736
12 | 0.97297 | -0.19019 | 0.00066179 | 0.00016586
13 | 0.9724 | -0.19433 | 0.0015326 | 0.0003841
14 | 0.9733 | -0.18783 | 0.00069209 | 0.00017345
15 | 0.97233 | -0.19484 | 0.00080755 | 0.00020239
16 | 0.9737 | -0.18491 | 0.00038605 | 9.6754e-05
17 | 0.97229 | -0.1951 | 0.0012129 | 0.00030398
18 | 0.99098 | -0.062648 | 0.0036072 | 0.00090405
19 | 0.98948 | -0.073125 | 0.00075661 | 0.00018962
20 | 0.99153 | -0.058758 | 0 | 0
21 | 0.98881 | -0.077844 | 0.00058118 | 0.00014566
22 | 0.98355 | -0.11475 | 0.0024986 | 0.00062622
23 | 0.99145 | -0.059301 | 0.0026564 | 0.00066577
24 | 0.99315 | -0.047476 | 0.0028542 | 0.00071534
25 | 0.98778 | -0.085121 | 0.0018248 | 0.00045733
26 | 0.98215 | -0.12461 | 0.0011582 | 0.00029026
27 | 0.99527 | -0.032699 | 0.0025782 | 0.00064617
28 | 0.98749 | -0.087143 | 0.0022839 | 0.0005724
29 | 0.99631 | -0.025534 | 0.0037189 | 0.00093203
30 | 0.98979 | -0.071521 | 0.0031035 | 0.0007778
31 | 0.98975 | -0.07182 | 0.012622 | 0.0031635
32 | 0.9907 | -0.065106 | 0.0030922 | 0.00077498
33 | 0.99136 | -0.060463 | 0.001283 | 0.00032155
34 | 0.98551 | -0.10178 | 0.00077181 | 0.00019343
35 | 0.98562 | -0.10102 | 0.0013367 | 0.00033502
36 | 0.98662 | -0.093899 | 0.0013556 | 0.00033974
37 | 0.98638 | -0.095589 | 0 | 0
38 | 0.98722 | -0.08961 | 0.0048377 | 0.0012124
39 | 0.98609 | -0.097658 | 0.0010841 | 0.00027169
40 | 0.98566 | -0.10068 | 0.01094 | 0.0027419
41 | 0.9855 | -0.10184 | 0.0013448 | 0.00033705
42 | 0.9855 | -0.10183 | 0.0011615 | 0.00029109
43 | 0.98562 | -0.10101 | 0.001345 | 0.0003371
44 | 0.99098 | -0.063105 | 0.0068973 | 0.0017286
45 | 0.99199 | -0.055983 | 0.0012433 | 0.0003116
46 | 0.99095 | -0.063376 | 0.0010276 | 0.00025755
47 | 0.99281 | -0.050218 | 0.0030322 | 0.00075994
48 | 0.99749 | -0.017436 | 0.0035016 | 0.00087759
49 | 0.99703 | -0.020674 | 0.0012043 | 0.00030183
50 | 0.99791 | -0.01454 | 0 | 0
51 | 0.99667 | -0.023236 | 0.0012959 | 0.00032479
52 | 0.99863 | -0.009471 | 0 | 0
53 | 0.99635 | -0.025463 | 0.001436 | 0.0003599
54 | 0.99751 | -0.017181 | 0.0023257 | 0.00058287
55 | 0.99934 | -0.0045742 | 0.0035696 | 0.00089463
56 | 0.98559 | -0.10062 | 0.00083595 | 0.00020951
57 | 0.98561 | -0.10045 | 0 | 0
58 | 0.99602 | -0.027784 | 0.0013565 | 0.00033998
59 | 1 | 0 | -0.19786 | -0.049696
60 | 0.98513 | -0.10387 | 0.00060068 | 0.00015054
61 | 0.98601 | -0.09762 | 0.00097676 | 0.0002448
62 | 0.98199 | -0.12622 | 0 | 0
63 | 0.98196 | -0.12645 | 0.0022323 | 0.00055947
64 | 0.98192 | -0.1267 | 0.001192 | 0.00029875
65 | 0.99539 | -0.032231 | 0 | 0
66 | 0.99531 | -0.032765 | 0.0009871 | 0.00024739
67 | 0.99543 | -0.031968 | 0 | 0
68 | 0.99572 | -0.02988 | 0.0018162 | 0.00045519
69 | 0.99561 | -0.03066 | 0.001602 | 0.00040151
70 | 0.97226 | -0.19532 | 0.0013454 | 0.0003372
71 | 0.99046 | -0.066719 | 0.0028672 | 0.0007186
72 | 0.99113 | -0.06203 | 0.0028246 | 0.00070792
73 | 0.98848 | -0.080728 | 0 | 0
74 | 0.99186 | -0.05691 | 0.0028685 | 0.00071892
75 | 0.98728 | -0.089197 | 0.0013091 | 0.0003281
76 | 0.98841 | -0.081189 | 0.0018926 | 0.00047433
77 | 0.99318 | -0.047606 | 0.0030783 | 0.00077149
78 | 0.99318 | -0.047584 | 0.0018099 | 0.0004536
79 | 0.97202 | -0.19703 | 0.0030258 | 0.00075834
80 | 0.97201 | -0.19708 | 0.0014202 | 0.00035594
81 | 0.97224 | -0.19548 | 0 | 0
82 | 0.97264 | -0.1926 | 0 | 0
83 | 0.97222 | -0.19563 | 0.0013509 | 0.00033858
84 | 0.97309 | -0.18933 | 0 | 0
85 | 0.97257 | -0.19305 | 0.0021562 | 0.00054039
86 | 0.97204 | -0.19692 | 0.0012543 | 0.00031436
87 | 0.97344 | -0.18679 | 0.0036445 | 0.00091339
88 | 0.97192 | -0.19774 | 0.0016848 | 0.00042224
89 | 0.98413 | -0.11098 | 0.00097511 | 0.00024439
90 | 0.98443 | -0.10887 | 0.0017177 | 0.00043049
91 | 0.9955 | -0.031417 | 0.0018206 | 0.00045628
92 | 0.99091 | -0.063657 | 0 | 0
93 | 0.9909 | -0.06371 | 0 | 0
94 | 0.99282 | -0.050159 | 0.0014627 | 0.00036659
95 | 0.99364 | -0.044419 | 0.0014897 | 0.00037336
96 | 0.99429 | -0.039787 | 0 | 0
97 | 0.99086 | -0.063972 | 0.0016828 | 0.00042174
98 | 0.98723 | -0.088977 | 0.0017816 | 0.00044651
99 | 0.99852 | -0.010281 | 0.0021484 | 0.00053844
100 | 0.9972 | -0.019483 | 0.0022987 | 0.0005761
101 | 0.99516 | -0.033744 | 0.0012455 | 0.00031215
102 | 0.97403 | -0.18258 | 0 | 0
103 | 0.97572 | -0.17045 | 0.00071814 | 0.00017998
104 | 0.97342 | -0.18696 | 0.0015198 | 0.00038089
105 | 0.97601 | -0.16836 | 0 | 0
106 | 0.97592 | -0.16903 | 0.0020819 | 0.00052178
107 | 0.97729 | -0.15922 | 0.0013698 | 0.0003433
108 | 0.9811 | -0.13206 | 0.00079388 | 0.00019896
109 | 0.97812 | -0.15328 | 0 | 0
110 | 0.97166 | -0.19961 | 0 | 0
111 | 0.97164 | -0.1998 | 0.0026369 | 0.00066088
112 | 0.98192 | -0.12676 | 0.00097322 | 0.00024391
113 | 0.9953 | -0.032823 | 0.0018901 | 0.0004737
114 | 0.98657 | -0.093643 | 0.00065283 | 0.00016362
115 | 0.98698 | -0.090754 | 0.0023876 | 0.00059839
116 | 0.97591 | -0.16905 | 0.0013439 | 0.0003368
117 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.01098 | 0.0027517 | -0.010976 | -0.0027504 | 3.9278e-06 | 1.2222e-06 | 0.016624 | 0.016624 | 0.016624 | 0.98281 | -0.12036 | 0.98245 | -0.12295 | 6.1572
1 | -0.012589 | -0.0031548 | 0.012589 | 0.003155 | 5.818e-07 | 1.9124e-07 | 0.01906 | 0.01906 | 0.01906 | 0.98281 | -0.12036 | 0.98286 | -0.12003 | 7.0592
2 | 0.0097876 | 0.0024525 | -0.0097875 | -0.0024525 | 1.7543e-07 | 5.1275e-08 | 0.014824 | 0.014824 | 0.014824 | 0.98245 | -0.12295 | 0.98243 | -0.12307 | 5.4904
3 | -0.01396 | -0.0034986 | 0.013967 | 0.0035008 | 6.4943e-06 | 2.2024e-06 | 0.021135 | 0.021135 | 0.021135 | 0.98286 | -0.12003 | 0.98333 | -0.11667 | 7.8279
4 | 0.0080418 | 0.002015 | -0.0080396 | -0.0020145 | 2.204e-06 | 5.4631e-07 | 0.01218 | 0.01218 | 0.01218 | 0.98243 | -0.12307 | 0.98215 | -0.12506 | 4.5112
5 | -0.01612 | -0.0040404 | 0.016122 | 0.0040413 | 2.3774e-06 | 8.3315e-07 | 0.024393 | 0.024393 | 0.024393 | 0.98333 | -0.11667 | 0.98348 | -0.1156 | 9.0346
6 | 0.0061559 | 0.0015423 | -0.0061558 | -0.0015423 | 9.6413e-08 | 1.4602e-08 | 0.0093264 | 0.0093264 | 0.0093264 | 0.98215 | -0.12506 | 0.98214 | -0.12517 | 3.4542
7 | -0.01761 | -0.0044142 | 0.017621 | 0.0044179 | 1.0359e-05 | 3.6873e-06 | 0.026645 | 0.026645 | 0.026645 | 0.98348 | -0.1156 | 0.98408 | -0.11136 | 9.8684
8 | 0.0043984 | 0.0011019 | -0.0043978 | -0.0011019 | 6.3803e-07 | -4.594e-08 | 0.0066638 | 0.0066639 | 0.0066639 | 0.98214 | -0.12517 | 0.98199 | -0.12622 | 2.4681
9 | -0.019474 | -0.0048823 | 0.019475 | 0.0048827 | 1.0218e-06 | 3.69e-07 | 0.029447 | 0.029447 | 0.029447 | 0.98408 | -0.11136 | 0.98413 | -0.11098 | 10.9062
10 | -0.0069251 | -0.001735 | 0.0069255 | 0.0017351 | 4.4961e-07 | 9.3257e-08 | 0.010595 | 0.010595 | 0.010595 | 0.97261 | -0.19277 | 0.97268 | -0.1923 | 3.9239
11 | 0.0056874 | 0.0014248 | -0.0056867 | -0.0014247 | 7.7184e-07 | 9.4131e-08 | 0.0087011 | 0.0087012 | 0.0087012 | 0.97261 | -0.19277 | 0.97248 | -0.19376 | 3.2227
12 | -0.007661 | -0.0019194 | 0.0076632 | 0.0019199 | 2.2371e-06 | 5.3634e-07 | 0.01172 | 0.01172 | 0.01172 | 0.97268 | -0.1923 | 0.97297 | -0.19019 | 4.3406
13 | 0.0048992 | 0.0012273 | -0.0048988 | -0.0012273 | 3.8712e-07 | 1.1929e-08 | 0.0074962 | 0.0074963 | 0.0074963 | 0.97248 | -0.19376 | 0.9724 | -0.19433 | 2.7764
14 | -0.008325 | -0.0020858 | 0.0083277 | 0.0020865 | 2.7206e-06 | 7.1221e-07 | 0.012732 | 0.012732 | 0.012732 | 0.97297 | -0.19019 | 0.9733 | -0.18783 | 4.7154
15 | 0.0033662 | 0.00084322 | -0.003366 | -0.0008433 | 2.3683e-07 | -8.6338e-08 | 0.0051511 | 0.0051511 | 0.0051511 | 0.9724 | -0.19433 | 0.97233 | -0.19484 | 1.9078
16 | -0.0090198 | -0.0022599 | 0.0090235 | 0.002261 | 3.6426e-06 | 1.0193e-06 | 0.01379 | 0.013789 | 0.01379 | 0.9733 | -0.18783 | 0.9737 | -0.18491 | 5.1073
17 | 0.0025585 | 0.00064091 | -0.0025584 | -0.000641 | 9.4481e-08 | -8.6165e-08 | 0.0039153 | 0.0039153 | 0.0039153 | 0.97233 | -0.19484 | 0.97229 | -0.1951 | 1.4501
18 | -0.0094095 | -0.0023577 | 0.0094126 | 0.0023586 | 3.0405e-06 | 8.7621e-07 | 0.014379 | 0.014379 | 0.014379 | 0.9737 | -0.18491 | 0.97403 | -0.18258 | 5.3257
19 | 0.0013455 | 0.00033702 | -0.0013454 | -0.0003372 | 4.0667e-08 | -1.7499e-07 | 0.0020591 | 0.0020591 | 0.0020591 | 0.97229 | -0.1951 | 0.97226 | -0.19532 | 0.76264
20 | 0.073737 | 0.018582 | -0.073629 | -0.01854 | 0.00010796 | 4.1343e-05 | 0.11076 | 0.11076 | 0.11076 | 0.99098 | -0.062648 | 0.98948 | -0.073125 | 41.0212
21 | -0.077344 | -0.019486 | 0.077386 | 0.019502 | 4.211e-05 | 1.6132e-05 | 0.11617 | 0.11617 | 0.11617 | 0.99098 | -0.062648 | 0.99153 | -0.058758 | 43.0273
22 | 0.034238 | 0.0086 | -0.034215 | -0.0085916 | 2.2454e-05 | 8.462e-06 | 0.051495 | 0.051495 | 0.051495 | 0.98948 | -0.073125 | 0.98881 | -0.077844 | 19.0722
23 | 0.038635 | 0.0097506 | -0.03841 | -0.0096656 | 0.00022444 | 8.4965e-05 | 0.058125 | 0.058125 | 0.058125 | 0.98948 | -0.073125 | 0.98355 | -0.11475 | 21.5278
24 | 0.0026566 | 0.00066558 | -0.0026564 | -0.00066577 | 1.9937e-07 | -1.8256e-07 | 0.0039868 | 0.0039869 | 0.0039869 | 0.99153 | -0.058758 | 0.99145 | -0.059301 | 1.4766
25 | -0.080043 | -0.020167 | 0.08017 | 0.020216 | 0.00012656 | 4.8495e-05 | 0.12016 | 0.12016 | 0.12016 | 0.99153 | -0.058758 | 0.99315 | -0.047476 | 44.5039
26 | 0.033634 | 0.0084459 | -0.0336 | -0.0084331 | 3.398e-05 | 1.2797e-05 | 0.05062 | 0.05062 | 0.05062 | 0.98881 | -0.077844 | 0.98778 | -0.085121 | 18.7483
27 | 0.035912 | 0.0090394 | -0.035862 | -0.0090207 | 4.941e-05 | 1.8664e-05 | 0.054345 | 0.054345 | 0.054345 | 0.98355 | -0.11475 | 0.98215 | -0.12461 | 20.1278
28 | -0.083024 | -0.020931 | 0.083196 | 0.020997 | 0.00017224 | 6.6014e-05 | 0.12444 | 0.12444 | 0.12444 | 0.99315 | -0.047476 | 0.99527 | -0.032699 | 46.0877
29 | 0.031775 | 0.0079758 | -0.031766 | -0.0079724 | 8.918e-06 | 3.3502e-06 | 0.047872 | 0.047872 | 0.047872 | 0.98778 | -0.085121 | 0.98749 | -0.087143 | 17.7302
30 | 0.034704 | 0.0087305 | -0.034668 | -0.0087169 | 3.6008e-05 | 1.3585e-05 | 0.05259 | 0.05259 | 0.05259 | 0.98215 | -0.12461 | 0.9811 | -0.13206 | 19.4779
31 | -0.085774 | -0.021643 | 0.085861 | 0.021676 | 8.6331e-05 | 3.3095e-05 | 0.12829 | 0.12829 | 0.12829 | 0.99527 | -0.032699 | 0.99631 | -0.025534 | 47.5153
32 | 0.029483 | 0.0074 | -0.029475 | -0.0073972 | 7.5061e-06 | 2.809e-06 | 0.04443 | 0.04443 | 0.04443 | 0.98749 | -0.087143 | 0.98723 | -0.088977 | 16.4556
33 | -0.08958 | -0.022608 | 0.089685 | 0.022649 | 0.00010518 | 4.0332e-05 | 0.13385 | 0.13385 | 0.13385 | 0.99631 | -0.025534 | 0.99751 | -0.017181 | 49.5724
34 | 0.012623 | 0.0031636 | -0.012622 | -0.0031635 | 5.2167e-07 | 1.7081e-07 | 0.018977 | 0.018977 | 0.018977 | 0.98979 | -0.071521 | 0.98975 | -0.07182 | 7.0285
35 | -0.015726 | -0.0039414 | 0.01574 | 0.0039463 | 1.3978e-05 | 4.8605e-06 | 0.023642 | 0.023642 | 0.023642 | 0.98979 | -0.071521 | 0.9907 | -0.065106 | 8.7565
36 | -0.018833 | -0.0047213 | 0.018845 | 0.0047256 | 1.2119e-05 | 4.3483e-06 | 0.028287 | 0.028287 | 0.028287 | 0.9907 | -0.065106 | 0.99136 | -0.060463 | 10.4766
37 | 0.0096114 | 0.0024084 | -0.0096079 | -0.0024074 | 3.5134e-06 | 1.0026e-06 | 0.014426 | 0.014427 | 0.014427 | 0.99136 | -0.060463 | 0.99098 | -0.063105 | 5.3432
38 | -0.029739 | -0.0074556 | 0.029758 | 0.0074625 | 1.847e-05 | 6.9121e-06 | 0.044639 | 0.044639 | 0.044639 | 0.99136 | -0.060463 | 0.99199 | -0.055983 | 16.5329
39 | -0.00077181 | -0.00019343 | 0.00077189 | 0.00019226 | 8.0413e-08 | -1.1787e-06 | 0.0011654 | 0.0011649 | 0.0011654 | 0.98551 | -0.10178 | 0.98562 | -0.10102 | 0.43161
40 | -0.0046152 | -0.0011551 | 0.0046152 | 0.0011551 | 8.1059e-09 | -2.9293e-10 | 0.0069672 | 0.0069672 | 0.0069672 | 0.98562 | -0.10102 | 0.98562 | -0.10101 | 2.5804
41 | 0.0025066 | 0.00062783 | -0.0025063 | -0.00062812 | 2.7932e-07 | -2.909e-07 | 0.0037841 | 0.0037843 | 0.0037843 | 0.98562 | -0.10102 | 0.9855 | -0.10183 | 1.4016
42 | 0.018002 | 0.0045117 | -0.017997 | -0.0045102 | 4.2112e-06 | 1.5028e-06 | 0.02715 | 0.02715 | 0.02715 | 0.98662 | -0.093899 | 0.98638 | -0.095589 | 10.0555
43 | -0.019357 | -0.0048515 | 0.019369 | 0.0048556 | 1.1498e-05 | 4.1461e-06 | 0.029194 | 0.029194 | 0.029194 | 0.98662 | -0.093899 | 0.98722 | -0.08961 | 10.8127
44 | 0.017997 | 0.0045102 | -0.017992 | -0.0045084 | 5.1531e-06 | 1.839e-06 | 0.02715 | 0.02715 | 0.02715 | 0.98638 | -0.095589 | 0.98609 | -0.097658 | 10.0555
45 | -0.024206 | -0.006068 | 0.024208 | 0.0060686 | 1.3876e-06 | 5.1234e-07 | 0.036486 | 0.036486 | 0.036486 | 0.98722 | -0.08961 | 0.98728 | -0.089197 | 13.5133
46 | 0.016908 | 0.0042367 | -0.016901 | -0.0042342 | 7.0607e-06 | 2.494e-06 | 0.025514 | 0.025514 | 0.025514 | 0.98609 | -0.097658 | 0.98566 | -0.10068 | 9.4497
47 | 0.0059605 | 0.0014922 | -0.0059603 | -0.0014922 | 2.7209e-07 | 3.6006e-08 | 0.0089978 | 0.0089978 | 0.0089978 | 0.98566 | -0.10068 | 0.98562 | -0.10101 | 3.3325
48 | -0.0013448 | -0.00033705 | 0.0013448 | 0.00033703 | 2.7961e-09 | -1.2772e-08 | 0.0020306 | 0.0020306 | 0.0020306 | 0.9855 | -0.10184 | 0.9855 | -0.10183 | 0.75206
49 | 0.0027106 | 0.0006788 | -0.0027105 | -0.00067889 | 1.0153e-07 | -8.7497e-08 | 0.0040699 | 0.00407 | 0.00407 | 0.99098 | -0.063105 | 0.99095 | -0.063376 | 1.5074
50 | -0.031001 | -0.0077741 | 0.031026 | 0.0077834 | 2.4788e-05 | 9.2963e-06 | 0.046504 | 0.046504 | 0.046504 | 0.99199 | -0.055983 | 0.99281 | -0.050218 | 17.2236
51 | 0.0016829 | 0.00042134 | -0.0016828 | -0.00042153 | 6.525e-08 | -1.8586e-07 | 0.0025269 | 0.002527 | 0.002527 | 0.99095 | -0.063376 | 0.99091 | -0.063657 | 0.93592
52 | -0.034058 | -0.0085433 | 0.034058 | 0.0085435 | 2.8219e-07 | 1.0629e-07 | 0.051048 | 0.051048 | 0.051048 | 0.99281 | -0.050218 | 0.99282 | -0.050159 | 18.9068
53 | 0.01343 | 0.0033661 | -0.013424 | -0.0033641 | 6.0178e-06 | 2.001e-06 | 0.020034 | 0.020034 | 0.020034 | 0.99749 | -0.017436 | 0.99703 | -0.020674 | 7.42
54 | -0.016931 | -0.0042437 | 0.016938 | 0.0042461 | 6.7926e-06 | 2.3897e-06 | 0.025258 | 0.025257 | 0.025258 | 0.99749 | -0.017436 | 0.99791 | -0.01454 | 9.3546
55 | 0.012219 | 0.0030623 | -0.012215 | -0.0030609 | 4.3326e-06 | 1.3942e-06 | 0.018237 | 0.018237 | 0.018237 | 0.99703 | -0.020674 | 0.99667 | -0.023236 | 6.7544
56 | -0.016938 | -0.0042461 | 0.01695 | 0.0042502 | 1.1899e-05 | 4.1856e-06 | 0.025257 | 0.025257 | 0.025257 | 0.99791 | -0.01454 | 0.99863 | -0.009471 | 9.3546
57 | 0.010919 | 0.0027361 | -0.010916 | -0.002735 | 3.3635e-06 | 1.0294e-06 | 0.016302 | 0.016302 | 0.016302 | 0.99667 | -0.023236 | 0.99635 | -0.025463 | 6.0378
58 | 0.09211 | 0.02327 | -0.09201 | -0.023232 | 9.9793e-05 | 3.8271e-05 | 0.13731 | 0.13731 | 0.13731 | 0.99863 | -0.009471 | 0.99751 | -0.017181 | 50.8573
59 | -0.10906 | -0.02752 | 0.10914 | 0.027549 | 7.5005e-05 | 2.861e-05 | 0.16257 | 0.16257 | 0.16257 | 0.99863 | -0.009471 | 0.99934 | -0.0045742 | 30.1059
60 | 0.0094797 | 0.0023751 | -0.0094767 | -0.0023743 | 3.0438e-06 | 8.5385e-07 | 0.014157 | 0.014157 | 0.014157 | 0.99635 | -0.025463 | 0.99602 | -0.027784 | 5.2435
61 | -0.1127 | -0.028443 | 0.11278 | 0.028471 | 7.242e-05 | 2.7638e-05 | 0.16789 | 0.16789 | 0.16789 | 0.99934 | -0.0045742 | 1 | 0 | 31.0902
62 | -0.00083595 | -0.00020951 | 0.00083597 | 0.00020928 | 1.8816e-08 | -2.3403e-07 | 0.0012621 | 0.001262 | 0.0012621 | 0.98559 | -0.10062 | 0.98561 | -0.10045 | 0.46744
63 | 0.0228 | 0.0057199 | -0.02279 | -0.0057159 | 1.0801e-05 | 3.9683e-06 | 0.034425 | 0.034425 | 0.034425 | 0.98561 | -0.10045 | 0.98513 | -0.10387 | 12.7499
64 | -0.023636 | -0.0059291 | 0.023646 | 0.0059326 | 9.2889e-06 | 3.4236e-06 | 0.035687 | 0.035687 | 0.035687 | 0.98561 | -0.10045 | 0.98601 | -0.09762 | 13.2172
65 | 0.0081201 | 0.0020343 | -0.0081178 | -0.0020337 | 2.3548e-06 | 5.7203e-07 | 0.012131 | 0.012131 | 0.012131 | 0.99602 | -0.027784 | 0.99572 | -0.02988 | 4.493
66 | 0.084281 | 0.021225 | -0.08416 | -0.021179 | 0.00012094 | 4.6355e-05 | 0.12545 | 0.12545 | 0.12545 | 1 | 0 | 0.99852 | -0.010281 | 46.4622
67 | 0.022189 | 0.0055653 | -0.022174 | -0.0055597 | 1.5358e-05 | 5.6283e-06 | 0.033517 | 0.033517 | 0.033517 | 0.98513 | -0.10387 | 0.98443 | -0.10887 | 12.4138
68 | -0.024622 | -0.0061774 | 0.024636 | 0.0061824 | 1.3591e-05 | 5.0259e-06 | 0.037161 | 0.03716 | 0.037161 | 0.98601 | -0.09762 | 0.98657 | -0.093643 | 13.7632
69 | 0.0043978 | 0.0011019 | -0.0043977 | -0.001102 | 1.3897e-07 | -9.9934e-09 | 0.0066639 | 0.0066639 | 0.0066639 | 0.98199 | -0.12622 | 0.98196 | -0.12645 | 2.4681
70 | 0.0021654 | 0.00054248 | -0.0021653 | -0.00054259 | 7.4905e-08 | -1.1223e-07 | 0.0032812 | 0.0032813 | 0.0032813 | 0.98196 | -0.12645 | 0.98192 | -0.1267 | 1.2153
71 | 0.00097323 | 0.00024384 | -0.00097322 | -0.00024391 | 8.3312e-09 | -7.4439e-08 | 0.0014748 | 0.0014748 | 0.0014748 | 0.98192 | -0.1267 | 0.98192 | -0.12676 | 0.54624
72 | 0.0028774 | 0.0007209 | -0.0028772 | -0.00072106 | 2.1272e-07 | -1.5766e-07 | 0.0043014 | 0.0043015 | 0.0043015 | 0.99539 | -0.032231 | 0.99531 | -0.032765 | 1.5931
73 | -0.0028774 | -0.0007209 | 0.0028775 | 0.00072082 | 1.0477e-07 | -7.767e-08 | 0.0043014 | 0.0043014 | 0.0043014 | 0.99539 | -0.032231 | 0.99543 | -0.031968 | 1.5931
74 | 0.0018901 | 0.00047367 | -0.0018901 | -0.0004737 | 1.4967e-08 | -3.3283e-08 | 0.0028258 | 0.0028258 | 0.0028258 | 0.99531 | -0.032765 | 0.9953 | -0.032823 | 1.0466
75 | -0.0028775 | -0.00072082 | 0.0028777 | 0.00072066 | 2.1906e-07 | -1.6243e-07 | 0.0043014 | 0.0043013 | 0.0043014 | 0.99543 | -0.031968 | 0.9955 | -0.031417 | 1.5931
76 | 0.0063015 | 0.0015785 | -0.0063009 | -0.0015784 | 6.7899e-07 | 1.0156e-07 | 0.0094168 | 0.0094169 | 0.0094169 | 0.99572 | -0.02988 | 0.99561 | -0.03066 | 3.4877
77 | 0.0046988 | 0.0011769 | -0.0046983 | -0.0011769 | 4.9245e-07 | -1.8677e-08 | 0.0070225 | 0.0070226 | 0.0070226 | 0.99561 | -0.03066 | 0.9955 | -0.031417 | 2.601
78 | -0.03036 | -0.0076203 | 0.03038 | 0.0076277 | 1.978e-05 | 7.4115e-06 | 0.045615 | 0.045615 | 0.045615 | 0.99046 | -0.066719 | 0.99113 | -0.06203 | 16.8946
79 | 0.027493 | 0.0069017 | -0.027439 | -0.0068818 | 5.3393e-05 | 1.9892e-05 | 0.041308 | 0.041308 | 0.041308 | 0.99046 | -0.066719 | 0.98848 | -0.080728 | 15.2993
80 | -0.033205 | -0.0083357 | 0.033228 | 0.0083445 | 2.3627e-05 | 8.891e-06 | 0.049856 | 0.049856 | 0.049856 | 0.99113 | -0.06203 | 0.99186 | -0.05691 | 18.4652
81 | 0.025547 | 0.0064078 | -0.025517 | -0.0063967 | 2.9964e-05 | 1.1109e-05 | 0.038459 | 0.038459 | 0.038459 | 0.98848 | -0.080728 | 0.98728 | -0.089197 | 14.2441
82 | 0.0018927 | 0.00047407 | -0.0018926 | -0.00047433 | 1.2074e-07 | -2.591e-07 | 0.0028491 | 0.0028492 | 0.0028492 | 0.98848 | -0.080728 | 0.98841 | -0.081189 | 1.0553
83 | -0.036097 | -0.0090635 | 0.036143 | 0.0090811 | 4.6729e-05 | 1.7643e-05 | 0.054159 | 0.054159 | 0.054159 | 0.99186 | -0.05691 | 0.99318 | -0.047606 | 20.0591
84 | -0.039222 | -0.0098526 | 0.039222 | 0.0098526 | 1.2086e-07 | 4.576e-08 | 0.058771 | 0.058771 | 0.058771 | 0.99318 | -0.047606 | 0.99318 | -0.047584 | 21.7672
85 | -0.041032 | -0.010306 | 0.041076 | 0.010323 | 4.453e-05 | 1.6882e-05 | 0.061483 | 0.061483 | 0.061483 | 0.99318 | -0.047584 | 0.99429 | -0.039787 | 22.7715
86 | 0.0014202 | 0.00035591 | -0.0014202 | -0.00035594 | 8.6007e-09 | -3.2835e-08 | 0.0021741 | 0.0021742 | 0.0021742 | 0.97202 | -0.19703 | 0.97201 | -0.19708 | 0.80524
87 | -0.0044461 | -0.0011143 | 0.004447 | 0.0011142 | 9.535e-07 | -4.2239e-08 | 0.0068062 | 0.0068061 | 0.0068062 | 0.97202 | -0.19703 | 0.97224 | -0.19548 | 2.5208
88 | -0.011376 | -0.0028497 | 0.011381 | 0.0028512 | 4.5334e-06 | 1.4463e-06 | 0.017411 | 0.017411 | 0.017411 | 0.97224 | -0.19548 | 0.97264 | -0.1926 | 6.4485
89 | 0.0069293 | 0.0017355 | -0.0069292 | -0.0017355 | 1.3965e-07 | 2.9035e-08 | 0.010605 | 0.010605 | 0.010605 | 0.97224 | -0.19548 | 0.97222 | -0.19563 | 3.9278
90 | -0.013537 | -0.0033914 | 0.013543 | 0.0033935 | 6.1266e-06 | 2.0721e-06 | 0.02071 | 0.02071 | 0.02071 | 0.97264 | -0.1926 | 0.97309 | -0.18933 | 7.6703
91 | 0.0021563 | 0.0005402 | -0.0021562 | -0.00054039 | 1.3309e-07 | -1.9204e-07 | 0.0032988 | 0.0032989 | 0.0032989 | 0.97264 | -0.1926 | 0.97257 | -0.19305 | 1.2218
92 | 0.0055782 | 0.0013969 | -0.0055772 | -0.0013968 | 9.9356e-07 | 1.113e-07 | 0.0085373 | 0.0085374 | 0.0085374 | 0.97222 | -0.19563 | 0.97204 | -0.19692 | 3.162
93 | -0.013543 | -0.0033935 | 0.013548 | 0.0033951 | 4.7619e-06 | 1.6104e-06 | 0.02071 | 0.02071 | 0.02071 | 0.97309 | -0.18933 | 0.97344 | -0.18679 | 7.6702
94 | 0.0043229 | 0.0010825 | -0.0043224 | -0.0010825 | 4.906e-07 | -3.3844e-08 | 0.0066173 | 0.0066174 | 0.0066174 | 0.97204 | -0.19692 | 0.97192 | -0.19774 | 2.4509
95 | 0.0015198 | 0.00038077 | -0.0015198 | -0.00038089 | 3.5606e-08 | -1.1774e-07 | 0.0023231 | 0.0023232 | 0.0023232 | 0.97344 | -0.18679 | 0.97342 | -0.18696 | 0.86043
96 | -0.018712 | -0.0046892 | 0.018723 | 0.0046932 | 1.0914e-05 | 3.9317e-06 | 0.028604 | 0.028604 | 0.028604 | 0.97344 | -0.18679 | 0.97403 | -0.18258 | 10.594
97 | 0.0026377 | 0.00066025 | -0.002637 | -0.00066082 | 6.8278e-07 | -5.6875e-07 | 0.004038 | 0.0040383 | 0.0040383 | 0.97192 | -0.19774 | 0.97166 | -0.19961 | 1.4957
98 | -0.02045 | -0.0051271 | 0.020456 | 0.0051292 | 5.9867e-06 | 2.175e-06 | 0.030921 | 0.030921 | 0.030921 | 0.98413 | -0.11098 | 0.98443 | -0.10887 | 11.4523
99 | 0.0016828 | 0.00042153 | -0.0016828 | -0.00042156 | 1.2273e-08 | -3.4955e-08 | 0.002527 | 0.002527 | 0.002527 | 0.99091 | -0.063657 | 0.9909 | -0.06371 | 0.93592
100 | 0.0016828 | 0.00042156 | -0.0016828 | -0.00042174 | 6.123e-08 | -1.7438e-07 | 0.002527 | 0.0025271 | 0.0025271 | 0.9909 | -0.06371 | 0.99086 | -0.063972 | 0.93595
101 | -0.035521 | -0.00891 | 0.035549 | 0.0089207 | 2.8296e-05 | 1.0676e-05 | 0.053241 | 0.05324 | 0.053241 | 0.99282 | -0.050159 | 0.99364 | -0.044419 | 19.7187
102 | -0.037039 | -0.0092941 | 0.037063 | 0.0093031 | 2.3821e-05 | 9.0013e-06 | 0.055471 | 0.055471 | 0.055471 | 0.99364 | -0.044419 | 0.99429 | -0.039787 | 20.5449
103 | -0.078139 | -0.019626 | 0.078205 | 0.019651 | 6.5709e-05 | 2.5173e-05 | 0.11695 | 0.11695 | 0.11695 | 0.99429 | -0.039787 | 0.99516 | -0.033744 | 43.3164
104 | 0.027693 | 0.0069507 | -0.027687 | -0.0069481 | 6.8304e-06 | 2.5468e-06 | 0.041745 | 0.041745 | 0.041745 | 0.98723 | -0.088977 | 0.98698 | -0.090754 | 15.461
105 | 0.082012 | 0.02064 | -0.081907 | -0.0206 | 0.00010522 | 4.0321e-05 | 0.12225 | 0.12225 | 0.12225 | 0.99852 | -0.010281 | 0.9972 | -0.019483 | 45.2765
106 | 0.079608 | 0.020024 | -0.07945 | -0.019964 | 0.00015799 | 6.0533e-05 | 0.11882 | 0.11882 | 0.11882 | 0.9972 | -0.019483 | 0.99516 | -0.033744 | 44.0061
107 | -0.028136 | -0.0070517 | 0.028183 | 0.0070694 | 4.7325e-05 | 1.769e-05 | 0.042983 | 0.042983 | 0.042983 | 0.97403 | -0.18258 | 0.97572 | -0.17045 | 15.9196
108 | -0.028901 | -0.0072494 | 0.02891 | 0.0072526 | 8.4021e-06 | 3.145e-06 | 0.044078 | 0.044078 | 0.044078 | 0.97572 | -0.17045 | 0.97601 | -0.16836 | 16.3252
109 | 0.0034261 | 0.00085846 | -0.0034258 | -0.00085857 | 3.204e-07 | -1.1194e-07 | 0.0052234 | 0.0052234 | 0.0052234 | 0.97601 | -0.16836 | 0.97592 | -0.16903 | 1.9346
110 | -0.032336 | -0.008111 | 0.032377 | 0.0081265 | 4.0999e-05 | 1.5431e-05 | 0.049301 | 0.049301 | 0.049301 | 0.97601 | -0.16836 | 0.97729 | -0.15922 | 18.2597
111 | 0.0013439 | 0.00033678 | -0.0013439 | -0.0003368 | 3.6504e-09 | -1.6006e-08 | 0.002049 | 0.002049 | 0.002049 | 0.97592 | -0.16903 | 0.97591 | -0.16905 | 0.7589
112 | -0.033747 | -0.0084698 | 0.033774 | 0.0084803 | 2.7876e-05 | 1.0509e-05 | 0.051387 | 0.051387 | 0.051387 | 0.97729 | -0.15922 | 0.97812 | -0.15328 | 19.0321
113 | 0.033874 | 0.0085179 | -0.033774 | -0.0084803 | 9.9867e-05 | 3.7647e-05 | 0.051386 | 0.051387 | 0.051387 | 0.9811 | -0.13206 | 0.97812 | -0.15328 | 19.0321
114 | 0.002637 | 0.00066082 | -0.0026369 | -0.00066088 | 6.7804e-08 | -5.6449e-08 | 0.0040383 | 0.0040383 | 0.0040383 | 0.97166 | -0.19961 | 0.97164 | -0.1998 | 1.4957
115 | -0.025289 | -0.006346 | 0.025299 | 0.0063498 | 1.0146e-05 | 3.7595e-06 | 0.038145 | 0.038145 | 0.038145 | 0.98657 | -0.093643 | 0.98698 | -0.090754 | 14.1278

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.2005 | 0.050359

## res_load
| p_mw | q_mvar
0 | 0.0016087 | 0.00040317
1 | 0.0011886 | 0.00029789
2 | 0.0013708 | 0.00034355
3 | 0.0017456 | 0.0004375
4 | 0.0021532 | 0.00053964
5 | 0.0018837 | 0.00047211
6 | 0.001488 | 0.00037293
7 | 0.0017574 | 0.00044044
8 | 0.0018531 | 0.00046443
9 | 0.0012377 | 0.00031018
10 | 0.00073543 | 0.00018432
11 | 0.00078747 | 0.00019736
12 | 0.00066179 | 0.00016586
13 | 0.0015326 | 0.0003841
14 | 0.00069209 | 0.00017345
15 | 0.00080755 | 0.00020239
16 | 0.00038605 | 9.6754e-05
17 | 0.0012129 | 0.00030398
18 | 0.0036072 | 0.00090405
19 | 0.00075661 | 0.00018962
20 | 0.00058118 | 0.00014566
21 | 0.0024986 | 0.00062622
22 | 0.0026564 | 0.00066577
23 | 0.0028542 | 0.00071534
24 | 0.0018248 | 0.00045733
25 | 0.0011582 | 0.00029026
26 | 0.0025782 | 0.00064617
27 | 0.0022839 | 0.0005724
28 | 0.0037189 | 0.00093203
29 | 0.0031035 | 0.0007778
30 | 0.012622 | 0.0031635
31 | 0.0030922 | 0.00077498
32 | 0.001283 | 0.00032155
33 | 0.00077181 | 0.00019343
34 | 0.0013367 | 0.00033502
35 | 0.0013556 | 0.00033974
36 | 0.0048377 | 0.0012124
37 | 0.0010841 | 0.00027169
38 | 0.01094 | 0.0027419
39 | 0.0013448 | 0.00033705
40 | 0.0011615 | 0.00029109
41 | 0.001345 | 0.0003371
42 | 0.0068973 | 0.0017286
43 | 0.0012433 | 0.0003116
44 | 0.0010276 | 0.00025755
45 | 0.0030322 | 0.00075994
46 | 0.0035016 | 0.00087759
47 | 0.0012043 | 0.00030183
48 | 0.0012959 | 0.00032479
49 | 0.001436 | 0.0003599
50 | 0.0023257 | 0.00058287
51 | 0.0035696 | 0.00089463
52 | 0.00083595 | 0.00020951
53 | 0.0013565 | 0.00033998
54 | 0.0026431 | 0.00066244
55 | 0.00060068 | 0.00015054
56 | 0.00097676 | 0.0002448
57 | 0.0022323 | 0.00055947
58 | 0.001192 | 0.00029875
59 | 0.0009871 | 0.00024739
60 | 0.0018162 | 0.00045519
61 | 0.001602 | 0.00040151
62 | 0.0013454 | 0.0003372
63 | 0.0028672 | 0.0007186
64 | 0.0028246 | 0.00070792
65 | 0.0028685 | 0.00071892
66 | 0.0013091 | 0.0003281
67 | 0.0018926 | 0.00047433
68 | 0.0030783 | 0.00077149
69 | 0.0018099 | 0.0004536
70 | 0.0030258 | 0.00075834
71 | 0.0014202 | 0.00035594
72 | 0.0013509 | 0.00033858
73 | 0.0021562 | 0.00054039
74 | 0.0012543 | 0.00031436
75 | 0.0036445 | 0.00091339
76 | 0.0016848 | 0.00042224
77 | 0.00097511 | 0.00024439
78 | 0.0017177 | 0.00043049
79 | 0.0018206 | 0.00045628
80 | 0.0014627 | 0.00036659
81 | 0.0014897 | 0.00037336
82 | 0.0016828 | 0.00042174
83 | 0.0017816 | 0.00044651
84 | 0.0021484 | 0.00053844
85 | 0.0022987 | 0.0005761
86 | 0.0012455 | 0.00031215
87 | 0.00071814 | 0.00017998
88 | 0.0015198 | 0.00038089
89 | 0.0020819 | 0.00052178
90 | 0.0013698 | 0.0003433
91 | 0.00079388 | 0.00019896
92 | 0.0026369 | 0.00066088
93 | 0.00097322 | 0.00024391
94 | 0.0018901 | 0.0004737
95 | 0.00065283 | 0.00016362
96 | 0.0023876 | 0.00059839
97 | 0.0013439 | 0.0003368

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1