## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2422-21_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2422-21_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2422-21_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2422-21_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2422-21_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2422-21_0_3_node_76 | 0.4 | n |  | TRUE
6 | bus_LV_2422-21_0_3_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_2422-21_0_3_node_77 | 0.4 | n |  | TRUE
8 | bus_LV_2422-21_0_3_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_2422-21_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2422-21_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2422-21_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2422-21_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2422-21_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2422-21_0_3_node_125 | 0.4 | n |  | TRUE
15 | bus_LV_2422-21_0_3_node_87 | 0.4 | n |  | TRUE
16 | bus_LV_2422-21_0_3_node_91 | 0.4 | n |  | TRUE
17 | bus_LV_2422-21_0_3_node_88 | 0.4 | n |  | TRUE
18 | bus_LV_2422-21_0_3_node_92 | 0.4 | n |  | TRUE
19 | bus_LV_2422-21_0_3_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2422-21_0_3_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_2422-21_0_3_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2422-21_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2422-21_0_3_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_2422-21_0_3_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_2422-21_0_3_node_94 | 0.4 | n |  | TRUE
26 | bus_LV_2422-21_0_3_node_70 | 0.4 | n |  | TRUE
27 | bus_LV_2422-21_0_3_node_99 | 0.4 | n |  | TRUE
28 | bus_LV_2422-21_0_3_node_95 | 0.4 | n |  | TRUE
29 | bus_LV_2422-21_0_3_node_67 | 0.4 | n |  | TRUE
30 | bus_LV_2422-21_0_3_node_100 | 0.4 | n |  | TRUE
31 | bus_LV_2422-21_0_3_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_2422-21_0_3_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_2422-21_0_3_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_2422-21_0_3_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_2422-21_0_3_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_2422-21_0_3_node_102 | 0.4 | n |  | TRUE
37 | bus_LV_2422-21_0_3_node_97 | 0.4 | n |  | TRUE
38 | bus_LV_2422-21_0_3_node_53 | 0.4 | n |  | TRUE
39 | bus_LV_2422-21_0_3_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_2422-21_0_3_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_2422-21_0_3_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_2422-21_0_3_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_2422-21_0_3_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_2422-21_0_3_node_89 | 0.4 | n |  | TRUE
45 | bus_LV_2422-21_0_3_node_52 | 0.4 | n |  | TRUE
46 | bus_LV_2422-21_0_3_node_90 | 0.4 | n |  | TRUE
47 | bus_LV_2422-21_0_3_node_50 | 0.4 | n |  | TRUE
48 | bus_LV_2422-21_0_3_node_98 | 0.4 | n |  | TRUE
49 | bus_LV_2422-21_0_3_node_123 | 0.4 | n |  | TRUE
50 | bus_LV_2422-21_0_3_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_2422-21_0_3_node_27 | 0.4 | n |  | TRUE
52 | bus_LV_2422-21_0_3_node_28 | 0.4 | n |  | TRUE
53 | bus_LV_2422-21_0_3_node_29 | 0.4 | n |  | TRUE
54 | bus_LV_2422-21_0_3_node_47 | 0.4 | n |  | TRUE
55 | bus_LV_2422-21_0_3_node_108 | 0.4 | n |  | TRUE
56 | bus_LV_2422-21_0_3_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_2422-21_0_3_node_32 | 0.4 | n |  | TRUE
58 | bus_LV_2422-21_0_3_node_114 | 0.4 | n |  | TRUE
59 | bus_LV_2422-21_0_3_node_33 | 0.4 | n |  | TRUE
60 | bus_LV_2422-21_0_3_node_34 | 0.4 | n |  | TRUE
61 | bus_LV_2422-21_0_3_node_35 | 0.4 | n |  | TRUE
62 | bus_LV_2422-21_0_3_node_36 | 0.4 | n |  | TRUE
63 | bus_LV_2422-21_0_3_node_37 | 0.4 | n |  | TRUE
64 | bus_LV_2422-21_0_3_node_113 | 0.4 | n |  | TRUE
65 | bus_LV_2422-21_0_3_node_116 | 0.4 | n |  | TRUE
66 | bus_LV_2422-21_0_3_node_112 | 0.4 | n |  | TRUE
67 | bus_LV_2422-21_0_3_node_38 | 0.4 | n |  | TRUE
68 | bus_LV_2422-21_0_3_node_39 | 0.4 | n |  | TRUE
69 | bus_LV_2422-21_0_3_node_40 | 0.4 | n |  | TRUE
70 | bus_LV_2422-21_0_3_node_41 | 0.4 | n |  | TRUE
71 | bus_LV_2422-21_0_3_node_42 | 0.4 | n |  | TRUE
72 | bus_LV_2422-21_0_3_node_64 | 0.4 | n |  | TRUE
73 | bus_LV_2422-21_0_3_node_74 | 0.4 | n |  | TRUE
74 | bus_LV_2422-21_0_3_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_2422-21_0_3_node_72 | 0.4 | n |  | TRUE
76 | bus_LV_2422-21_0_3_node_43 | 0.4 | n |  | TRUE
77 | bus_LV_2422-21_0_3_node_44 | 0.4 | n |  | TRUE
78 | bus_LV_2422-21_0_3_node_46 | 0.4 | n |  | TRUE
79 | bus_LV_2422-21_0_3_node_48 | 0.4 | n |  | TRUE
80 | bus_LV_2422-21_0_3_node_101 | 0.4 | n |  | TRUE
81 | bus_LV_2422-21_0_3_node_81 | 0.4 | n |  | TRUE
82 | bus_LV_2422-21_0_3_node_79 | 0.4 | n |  | TRUE
83 | bus_LV_2422-21_0_3_node_80 | 0.4 | n |  | TRUE
84 | bus_LV_2422-21_0_3_node_49 | 0.4 | n |  | TRUE
85 | bus_LV_2422-21_0_3_node_51 | 0.4 | n |  | TRUE
86 | bus_LV_2422-21_0_3_node_54 | 0.4 | n |  | TRUE
87 | bus_LV_2422-21_0_3_node_55 | 0.4 | n |  | TRUE
88 | bus_LV_2422-21_0_3_node_56 | 0.4 | n |  | TRUE
89 | bus_LV_2422-21_0_3_node_57 | 0.4 | n |  | TRUE
90 | bus_LV_2422-21_0_3_node_58 | 0.4 | n |  | TRUE
91 | bus_LV_2422-21_0_3_node_78 | 0.4 | n |  | TRUE
92 | bus_LV_2422-21_0_3_node_59 | 0.4 | n |  | TRUE
93 | bus_LV_2422-21_0_3_node_60 | 0.4 | n |  | TRUE
94 | bus_LV_2422-21_0_3_node_61 | 0.4 | n |  | TRUE
95 | bus_LV_2422-21_0_3_node_62 | 0.4 | n |  | TRUE
96 | bus_LV_2422-21_0_3_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_2422-21_0_3_node_85 | 0.4 | n |  | TRUE
98 | bus_LV_2422-21_0_3_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_2422-21_0_3_node_66 | 0.4 | n |  | TRUE
100 | bus_LV_2422-21_0_3_node_68 | 0.4 | n |  | TRUE
101 | bus_LV_2422-21_0_3_node_69 | 0.4 | n |  | TRUE
102 | bus_LV_2422-21_0_3_node_82 | 0.4 | n |  | TRUE
103 | bus_LV_2422-21_0_3_node_83 | 0.4 | n |  | TRUE
104 | bus_LV_2422-21_0_3_node_71 | 0.4 | n |  | TRUE
105 | bus_LV_2422-21_0_3_node_73 | 0.4 | n |  | TRUE
106 | bus_LV_2422-21_0_3_node_75 | 0.4 | n |  | TRUE
107 | bus_LV_2422-21_0_3_node_109 | 0.4 | n |  | TRUE
108 | bus_LV_2422-21_0_3_node_115 | 0.4 | n |  | TRUE
109 | bus_LV_2422-21_0_3_node_110 | 0.4 | n |  | TRUE
110 | bus_LV_2422-21_0_3_node_126 | 0.4 | n |  | TRUE
111 | bus_LV_2422-21_0_3_node_93 | 0.4 | n |  | TRUE
112 | bus_LV_2422-21_0_3_node_105 | 0.4 | n |  | TRUE
113 | bus_LV_2422-21_0_3_node_107 | 0.4 | n |  | TRUE
114 | bus_LV_2422-21_0_3_node_103 | 0.4 | n |  | TRUE
115 | bus_LV_2422-21_0_3_node_96 | 0.4 | n |  | TRUE
116 | bus_LV_2422-21_0_3_node_117 | 0.4 | n |  | TRUE
117 | bus_LV_2422-21_0_3_node_122 | 0.4 | n |  | TRUE
118 | bus_LV_2422-21_0_3_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_2422-21_0_3_node_106 | 0.4 | n |  | TRUE
120 | bus_LV_2422-21_0_3_node_119 | 0.4 | n |  | TRUE
121 | bus_LV_2422-21_0_3_node_120 | 0.4 | n |  | TRUE
122 | bus_LV_2422-21_0_3_node_111 | 0.4 | n |  | TRUE
123 | bus_LV_2422-21_0_3_node_118 | 0.4 | n |  | TRUE
124 | bus_MV_333_0_node_42 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2422-21_0_3_load_0 | 0 | 0.0011299 | 0.00028318 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2422-21_0_3_load_1 | 1 | 0.0014115 | 0.00035375 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2422-21_0_3_load_2 | 2 | 0.0018394 | 0.000461 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2422-21_0_3_load_3 | 3 | 0.0012322 | 0.00030882 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2422-21_0_3_load_4 | 4 | 0.0015557 | 0.0003899 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2422-21_0_3_load_76 | 5 | 0.0019466 | 0.00048787 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2422-21_0_3_load_26 | 6 | 0.0019177 | 0.00048063 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2422-21_0_3_load_77 | 7 | 0.0023662 | 0.00059302 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2422-21_0_3_load_30 | 8 | 0.0016546 | 0.00041469 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2422-21_0_3_load_5 | 9 | 0.001346 | 0.00033734 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2422-21_0_3_load_7 | 11 | 0.0013687 | 0.00034302 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2422-21_0_3_load_8 | 12 | 0.0013319 | 0.00033382 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2422-21_0_3_load_125 | 14 | 0.0025636 | 0.0006425 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2422-21_0_3_load_87 | 15 | 0.0016047 | 0.00040218 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2422-21_0_3_load_91 | 16 | 0.0015606 | 0.00039111 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2422-21_0_3_load_88 | 17 | 0.0012566 | 0.00031493 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2422-21_0_3_load_92 | 18 | 0.0029383 | 0.00073641 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2422-21_0_3_load_10 | 19 | 0.0024783 | 0.00062111 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2422-21_0_3_load_11 | 20 | 0.0023969 | 0.00060071 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2422-21_0_3_load_13 | 22 | 0.0032863 | 0.00082363 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2422-21_0_3_load_14 | 23 | 0.0074263 | 0.0018612 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2422-21_0_3_load_15 | 24 | 0.0022694 | 0.00056876 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2422-21_0_3_load_94 | 25 | 0.0032054 | 0.00080334 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2422-21_0_3_load_70 | 26 | 0.0018374 | 0.00046051 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2422-21_0_3_load_99 | 27 | 0.0016024 | 0.00040159 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2422-21_0_3_load_95 | 28 | 0.002275 | 0.00057016 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2422-21_0_3_load_100 | 30 | 0.0031993 | 0.00080181 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2422-21_0_3_load_16 | 31 | 0.0019359 | 0.00048519 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2422-21_0_3_load_17 | 32 | 0.0014366 | 0.00036006 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2422-21_0_3_load_18 | 33 | 0.0023844 | 0.00059758 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2422-21_0_3_load_19 | 34 | 0.0030729 | 0.00077015 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2422-21_0_3_load_20 | 35 | 0.00179 | 0.00044862 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2422-21_0_3_load_102 | 36 | 0.0027106 | 0.00067933 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2422-21_0_3_load_97 | 37 | 0.0016241 | 0.00040703 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2422-21_0_3_load_53 | 38 | 0.0032659 | 0.00081851 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2422-21_0_3_load_21 | 39 | 0.0023007 | 0.0005766 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2422-21_0_3_load_22 | 40 | 0.0017935 | 0.00044949 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2422-21_0_3_load_23 | 41 | 0.0026704 | 0.00066925 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2422-21_0_3_load_24 | 42 | 0.0018724 | 0.00046928 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2422-21_0_3_load_89 | 44 | 0.0028569 | 0.000716 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2422-21_0_3_load_90 | 46 | 0.0023672 | 0.00059326 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2422-21_0_3_load_50 | 47 | 0.0022197 | 0.00055631 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2422-21_0_3_load_98 | 48 | 0.0012615 | 0.00031617 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2422-21_0_3_load_31 | 50 | 0.0015136 | 0.00037936 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2422-21_0_3_load_27 | 51 | 0.0012855 | 0.00032217 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2422-21_0_3_load_28 | 52 | 0.0020101 | 0.00050377 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2422-21_0_3_load_29 | 53 | 0.0025209 | 0.00063179 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2422-21_0_3_load_32 | 57 | 0.0015392 | 0.00038575 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2422-21_0_3_load_114 | 58 | 0.0039692 | 0.00099476 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2422-21_0_3_load_33 | 59 | 0.0031351 | 0.00078573 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2422-21_0_3_load_34 | 60 | 0.0031991 | 0.00080177 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2422-21_0_3_load_36 | 62 | 0.0023871 | 0.00059827 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2422-21_0_3_load_37 | 63 | 0.003108 | 0.00077894 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2422-21_0_3_load_38 | 67 | 0.00077901 | 0.00019524 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2422-21_0_3_load_39 | 68 | 0.0016188 | 0.00040571 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2422-21_0_3_load_40 | 69 | 0.00078177 | 0.00019593 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2422-21_0_3_load_41 | 70 | 0.0029374 | 0.00073618 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2422-21_0_3_load_42 | 71 | 0.00097034 | 0.00024319 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2422-21_0_3_load_64 | 72 | 0.0034046 | 0.00085328 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2422-21_0_3_load_74 | 73 | 0.0008133 | 0.00020383 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2422-21_0_3_load_63 | 74 | 0.0027877 | 0.00069867 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2422-21_0_3_load_43 | 76 | 0.0015276 | 0.00038285 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2422-21_0_3_load_44 | 77 | 0.0013102 | 0.00032837 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2422-21_0_3_load_46 | 78 | 0.0015514 | 0.00038882 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2422-21_0_3_load_48 | 79 | 0.00093938 | 0.00023543 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2422-21_0_3_load_101 | 80 | 0.0024572 | 0.00061584 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2422-21_0_3_load_81 | 81 | 0.0035725 | 0.00089536 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2422-21_0_3_load_79 | 82 | 0.001452 | 0.0003639 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2422-21_0_3_load_80 | 83 | 0.0056588 | 0.0014182 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2422-21_0_3_load_49 | 84 | 0.0026649 | 0.00066789 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2422-21_0_3_load_54 | 86 | 0.0024368 | 0.00061071 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2422-21_0_3_load_55 | 87 | 0.0013705 | 0.00034348 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2422-21_0_3_load_56 | 88 | 0.0020182 | 0.00050581 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2422-21_0_3_load_57 | 89 | 0.0019577 | 0.00049065 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2422-21_0_3_load_58 | 90 | 0.0018457 | 0.00046258 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2422-21_0_3_load_78 | 91 | 0.0019527 | 0.0004894 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2422-21_0_3_load_59 | 92 | 0.0030389 | 0.00076162 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2422-21_0_3_load_60 | 93 | 0.0030386 | 0.00076154 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2422-21_0_3_load_61 | 94 | 0.0019397 | 0.00048614 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2422-21_0_3_load_62 | 95 | 0.0030414 | 0.00076224 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2422-21_0_3_load_85 | 97 | 0.0019095 | 0.00047857 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2422-21_0_3_load_66 | 99 | 0.0012403 | 0.00031086 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2422-21_0_3_load_68 | 100 | 0.0029912 | 0.00074967 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2422-21_0_3_load_69 | 101 | 0.0022264 | 0.00055799 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2422-21_0_3_load_83 | 103 | 0.0026833 | 0.00067249 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2422-21_0_3_load_71 | 104 | 0.001532 | 0.00038394 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2422-21_0_3_load_73 | 105 | 0.001226 | 0.00030727 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2422-21_0_3_load_75 | 106 | 0.0038531 | 0.00096569 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2422-21_0_3_load_109 | 107 | 0.0026238 | 0.00065759 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2422-21_0_3_load_126 | 110 | 0.0092875 | 0.0023277 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2422-21_0_3_load_107 | 113 | 0.0037556 | 0.00094123 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2422-21_0_3_load_103 | 114 | 0.0054541 | 0.0013669 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2422-21_0_3_load_96 | 115 | 0.00079775 | 0.00019994 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2422-21_0_3_load_117 | 116 | 0.0013157 | 0.00032974 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2422-21_0_3_load_122 | 117 | 0.0020266 | 0.00050792 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2422-21_0_3_load_104 | 118 | 0.0062234 | 0.0015597 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2422-21_0_3_load_106 | 119 | 0.0015256 | 0.00038235 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2422-21_0_3_load_119 | 120 | 0.0024137 | 0.00060492 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2422-21_0_3_load_111 | 122 | 0.00085477 | 0.00021423 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2422-21_0_3_load_118 | 123 | 0.0013201 | 0.00033084 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 90 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2422-21_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.015747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2422-21_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0032171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2422-21_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.008975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2422-21_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.017543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2422-21_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.011535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2422-21_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0063792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2422-21_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.0078404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2422-21_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.0022115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2422-21_0_3_line_8 | NAYY 4x150 SE | 7 | 36 | 0.012183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2422-21_0_3_line_9 | NAYY 4x150 SE | 8 | 50 | 0.010948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2422-21_0_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.016282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2422-21_0_3_line_11 | NAYY 4x150 SE | 9 | 11 | 0.015832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2422-21_0_3_line_12 | NAYY 4x150 SE | 10 | 12 | 0.019203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2422-21_0_3_line_13 | NAYY 4x150 SE | 10 | 13 | 0.06145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2422-21_0_3_line_14 | NAYY 4x150 SE | 10 | 14 | 0.059082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2422-21_0_3_line_15 | NAYY 4x150 SE | 12 | 15 | 0.00076954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2422-21_0_3_line_16 | NAYY 4x150 SE | 13 | 16 | 0.022319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2422-21_0_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.0076997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2422-21_0_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.025689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2422-21_0_3_line_19 | NAYY 4x150 SE | 18 | 111 | 0.0014147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2422-21_0_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.029189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2422-21_0_3_line_21 | NAYY 4x150 SE | 19 | 21 | 0.026316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2422-21_0_3_line_22 | NAYY 4x150 SE | 20 | 22 | 0.016074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2422-21_0_3_line_23 | NAYY 4x150 SE | 21 | 23 | 0.020568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2422-21_0_3_line_24 | NAYY 4x150 SE | 21 | 24 | 0.017885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2422-21_0_3_line_25 | NAYY 4x150 SE | 23 | 25 | 0.0071065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2422-21_0_3_line_26 | NAYY 4x150 SE | 24 | 26 | 0.0181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2422-21_0_3_line_27 | NAYY 4x150 SE | 24 | 27 | 0.012103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2422-21_0_3_line_28 | NAYY 4x150 SE | 25 | 28 | 0.017439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2422-21_0_3_line_29 | NAYY 4x150 SE | 26 | 29 | 0.006689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2422-21_0_3_line_30 | NAYY 4x150 SE | 27 | 30 | 0.0070464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2422-21_0_3_line_31 | NAYY 4x150 SE | 28 | 115 | 0.014534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2422-21_0_3_line_32 | NAYY 4x150 SE | 29 | 101 | 0.023468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2422-21_0_3_line_33 | NAYY 4x150 SE | 29 | 99 | 0.013852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2422-21_0_3_line_34 | NAYY 4x150 SE | 31 | 32 | 0.02604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2422-21_0_3_line_35 | NAYY 4x150 SE | 31 | 33 | 0.0026342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2422-21_0_3_line_36 | NAYY 4x150 SE | 32 | 34 | 0.0035714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2422-21_0_3_line_37 | NAYY 4x150 SE | 33 | 35 | 0.0002401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2422-21_0_3_line_38 | NAYY 4x150 SE | 34 | 36 | 0.02276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2422-21_0_3_line_39 | NAYY 4x150 SE | 35 | 37 | 0.0023752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2422-21_0_3_line_40 | NAYY 4x150 SE | 37 | 38 | 0.024213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2422-21_0_3_line_41 | NAYY 4x150 SE | 38 | 85 | 0.054466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2422-21_0_3_line_42 | NAYY 4x150 SE | 39 | 40 | 0.015469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2422-21_0_3_line_43 | NAYY 4x150 SE | 39 | 41 | 0.0043845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2422-21_0_3_line_44 | NAYY 4x150 SE | 40 | 42 | 0.0021359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2422-21_0_3_line_45 | NAYY 4x150 SE | 41 | 43 | 0.040579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2422-21_0_3_line_46 | NAYY 4x150 SE | 42 | 44 | 0.015359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2422-21_0_3_line_47 | NAYY 4x150 SE | 43 | 45 | 0.045878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2422-21_0_3_line_48 | NAYY 4x150 SE | 44 | 46 | 0.012894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2422-21_0_3_line_49 | NAYY 4x150 SE | 45 | 47 | 0.01228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2422-21_0_3_line_50 | NAYY 4x150 SE | 46 | 89 | 0.029689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2422-21_0_3_line_51 | NAYY 4x150 SE | 47 | 84 | 0.027843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2422-21_0_3_line_52 | NAYY 4x150 SE | 48 | 49 | 0.0060219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2422-21_0_3_line_53 | NAYY 4x150 SE | 49 | 117 | 0.0076447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2422-21_0_3_line_54 | NAYY 4x150 SE | 50 | 57 | 0.010958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2422-21_0_3_line_55 | NAYY 4x150 SE | 51 | 52 | 0.0099832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2422-21_0_3_line_56 | NAYY 4x150 SE | 52 | 53 | 0.0058992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2422-21_0_3_line_57 | NAYY 4x150 SE | 53 | 54 | 0.0099489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2422-21_0_3_line_58 | NAYY 4x150 SE | 54 | 55 | 0.030447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
59 | LV_2422-21_0_3_line_59 | NAYY 4x150 SE | 54 | 56 | 0.045361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
60 | LV_2422-21_0_3_line_60 | NAYY 4x150 SE | 55 | 58 | 0.029001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2422-21_0_3_line_61 | NAYY 4x150 SE | 56 | 79 | 0.013745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
62 | LV_2422-21_0_3_line_62 | NAYY 4x150 SE | 56 | 76 | 0.03314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
63 | LV_2422-21_0_3_line_63 | NAYY 4x150 SE | 58 | 98 | 0.01022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2422-21_0_3_line_64 | NAYY 4x150 SE | 59 | 60 | 0.025784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2422-21_0_3_line_65 | NAYY 4x150 SE | 59 | 61 | 0.0093599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2422-21_0_3_line_66 | NAYY 4x150 SE | 61 | 62 | 0.056162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2422-21_0_3_line_67 | NAYY 4x150 SE | 61 | 63 | 0.019948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2422-21_0_3_line_68 | NAYY 4x150 SE | 62 | 64 | 0.0074646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2422-21_0_3_line_69 | NAYY 4x150 SE | 64 | 65 | 0.015141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2422-21_0_3_line_70 | NAYY 4x150 SE | 64 | 66 | 0.015677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2422-21_0_3_line_71 | NAYY 4x150 SE | 65 | 123 | 0.0095728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2422-21_0_3_line_72 | NAYY 4x150 SE | 65 | 116 | 0.022495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2422-21_0_3_line_73 | NAYY 4x150 SE | 66 | 122 | 0.017437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2422-21_0_3_line_74 | NAYY 4x150 SE | 67 | 68 | 0.0047514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2422-21_0_3_line_75 | NAYY 4x150 SE | 67 | 69 | 0.016275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2422-21_0_3_line_76 | NAYY 4x150 SE | 68 | 70 | 0.0175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2422-21_0_3_line_77 | NAYY 4x150 SE | 69 | 71 | 0.019172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2422-21_0_3_line_78 | NAYY 4x150 SE | 70 | 72 | 0.033353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2422-21_0_3_line_79 | NAYY 4x150 SE | 71 | 73 | 0.019628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2422-21_0_3_line_80 | NAYY 4x150 SE | 72 | 74 | 0.0081401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2422-21_0_3_line_81 | NAYY 4x150 SE | 73 | 75 | 0.014186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2422-21_0_3_line_82 | NAYY 4x150 SE | 75 | 106 | 0.012327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2422-21_0_3_line_83 | NAYY 4x150 SE | 75 | 104 | 0.067491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2422-21_0_3_line_84 | NAYY 4x150 SE | 76 | 77 | 0.017237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
85 | LV_2422-21_0_3_line_85 | NAYY 4x150 SE | 77 | 78 | 0.020685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
86 | LV_2422-21_0_3_line_86 | NAYY 4x150 SE | 78 | 80 | 0.0017704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
87 | LV_2422-21_0_3_line_87 | NAYY 4x150 SE | 79 | 81 | 0.0097111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
88 | LV_2422-21_0_3_line_88 | NAYY 4x150 SE | 80 | 82 | 0.016415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
89 | LV_2422-21_0_3_line_89 | NAYY 4x150 SE | 81 | 83 | 0.011484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
90 | LV_2422-21_0_3_line_90 | NAYY 4x150 SE | 82 | 91 | 0.013556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
91 | LV_2422-21_0_3_line_91 | NAYY 4x150 SE | 83 | 102 | 0.04191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
92 | LV_2422-21_0_3_line_92 | NAYY 4x150 SE | 84 | 85 | 0.023624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2422-21_0_3_line_93 | NAYY 4x150 SE | 86 | 87 | 0.02128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2422-21_0_3_line_94 | NAYY 4x150 SE | 86 | 88 | 0.0016998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2422-21_0_3_line_95 | NAYY 4x150 SE | 87 | 89 | 0.0019905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2422-21_0_3_line_96 | NAYY 4x150 SE | 88 | 90 | 0.017713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2422-21_0_3_line_97 | NAYY 4x150 SE | 90 | 91 | 0.0060652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
98 | LV_2422-21_0_3_line_98 | NAYY 4x150 SE | 92 | 93 | 0.0024619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2422-21_0_3_line_99 | NAYY 4x150 SE | 92 | 94 | 0.01279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2422-21_0_3_line_100 | NAYY 4x150 SE | 93 | 95 | 0.027683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2422-21_0_3_line_101 | NAYY 4x150 SE | 95 | 96 | 0.01363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2422-21_0_3_line_102 | NAYY 4x150 SE | 96 | 97 | 0.019192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2422-21_0_3_line_103 | NAYY 4x150 SE | 96 | 98 | 0.020995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2422-21_0_3_line_104 | NAYY 4x150 SE | 97 | 107 | 0.0082306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2422-21_0_3_line_105 | NAYY 4x150 SE | 98 | 108 | 0.050509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2422-21_0_3_line_106 | NAYY 4x150 SE | 99 | 100 | 0.012396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2422-21_0_3_line_107 | NAYY 4x150 SE | 101 | 102 | 0.0238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2422-21_0_3_line_108 | NAYY 4x150 SE | 102 | 103 | 0.00416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2422-21_0_3_line_109 | NAYY 4x150 SE | 103 | 106 | 0.020109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2422-21_0_3_line_110 | NAYY 4x150 SE | 104 | 105 | 0.00043621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2422-21_0_3_line_111 | NAYY 4x150 SE | 107 | 109 | 0.003822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2422-21_0_3_line_112 | NAYY 4x150 SE | 108 | 110 | 0.0259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2422-21_0_3_line_113 | NAYY 4x150 SE | 109 | 121 | 0.01444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2422-21_0_3_line_114 | NAYY 4x150 SE | 111 | 112 | 0.027841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2422-21_0_3_line_115 | NAYY 4x150 SE | 112 | 113 | 0.033084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2422-21_0_3_line_116 | NAYY 4x150 SE | 112 | 114 | 0.014121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2422-21_0_3_line_117 | NAYY 4x150 SE | 113 | 121 | 0.022268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2422-21_0_3_line_118 | NAYY 4x150 SE | 114 | 118 | 0.013345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2422-21_0_3_line_119 | NAYY 4x150 SE | 115 | 116 | 0.0070691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2422-21_0_3_line_120 | NAYY 4x150 SE | 117 | 123 | 0.0082315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2422-21_0_3_line_121 | NAYY 4x150 SE | 118 | 119 | 0.019053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2422-21_0_3_line_122 | NAYY 4x150 SE | 119 | 120 | 0.0079973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2422-21_0_3_trafo_58 | 0.25 MVA 20/0.4 kV | 124 | 90 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2619559.7064 | 1241031.0904 | 2619565.6027 | 1241016.4887
1 | 2619559.7064 | 1241031.0904 | 2619558.5019 | 1241034.0735
2 | 2619568.9633 | 1241008.1666 | 2619565.6027 | 1241016.4887
3 | 2619551.9333 | 1241050.3402 | 2619558.5019 | 1241034.0735
4 | 2619568.9633 | 1241008.1666 | 2619573.2823 | 1240997.4707
5 | 2619551.9333 | 1241050.3402 | 2619549.5447 | 1241056.2553
6 | 2619576.218 | 1240990.2006 | 2619573.2823 | 1240997.4707
7 | 2619548.7166 | 1241058.306 | 2619549.5447 | 1241056.2553
8 | 2619576.218 | 1240990.2006 | 2619580.7798 | 1240978.9036
9 | 2619544.6174 | 1241068.4576 | 2619548.7166 | 1241058.306
10 | 2619513.3709 | 1240951.3458 | 2619528.9644 | 1240956.0305
11 | 2619544.1267 | 1240960.5858 | 2619528.9644 | 1240956.0305
12 | 2619513.3709 | 1240951.3458 | 2619508.195 | 1240969.8378
13 | 2619453.9226 | 1240935.33 | 2619473.9442 | 1240939.4981 | 2619513.3709 | 1240951.3458
14 | 2619513.3709 | 1240951.3458 | 2619529.8877 | 1240894.6199
15 | 2619508.195 | 1240969.8378 | 2619507.9875 | 1240970.5788
16 | 2619453.9226 | 1240935.33 | 2619452.8732 | 1240957.6241
17 | 2619505.9121 | 1240977.9936 | 2619507.9875 | 1240970.5788
18 | 2619452.8732 | 1240957.6241 | 2619451.6654 | 1240983.2847
19 | 2619451.5989 | 1240984.6978 | 2619451.6654 | 1240983.2847
20 | 2619730.467 | 1241063.5853 | 2619757.381 | 1241074.8822
21 | 2619706.2023 | 1241053.4005 | 2619730.467 | 1241063.5853
22 | 2619772.2026 | 1241081.1034 | 2619757.381 | 1241074.8822
23 | 2619706.2023 | 1241053.4005 | 2619714.7957 | 1241034.714
24 | 2619698.2034 | 1241069.4063 | 2619706.2023 | 1241053.4005
25 | 2619717.7649 | 1241028.2574 | 2619714.7957 | 1241034.714
26 | 2619698.2034 | 1241069.4063 | 2619688.1234 | 1241084.44
27 | 2619698.2034 | 1241069.4063 | 2619687.4563 | 1241063.8405
28 | 2619717.7649 | 1241028.2574 | 2619725.051 | 1241012.4135
29 | 2619684.3983 | 1241089.9957 | 2619688.1234 | 1241084.44
30 | 2619681.1992 | 1241060.6001 | 2619687.4563 | 1241063.8405
31 | 2619731.1235 | 1240999.2087 | 2619725.051 | 1241012.4135
32 | 2619684.3983 | 1241089.9957 | 2619668.6517 | 1241107.3961
33 | 2619684.3983 | 1241089.9957 | 2619671.9461 | 1241083.9287
34 | 2619595.77 | 1240928.9024 | 2619590.082 | 1240954.314
35 | 2619596.3454 | 1240926.3319 | 2619595.77 | 1240928.9024
36 | 2619589.3019 | 1240957.7992 | 2619590.082 | 1240954.314
37 | 2619596.3454 | 1240926.3319 | 2619596.3978 | 1240926.0976
38 | 2619589.3019 | 1240957.7992 | 2619589.3019 | 1240957.7992 | 2619580.7798 | 1240978.9036
39 | 2619596.9167 | 1240923.7797 | 2619596.3978 | 1240926.0976
40 | 2619596.9167 | 1240923.7797 | 2619602.2055 | 1240900.1515
41 | 2619614.1025 | 1240847.0003 | 2619602.2055 | 1240900.1515
42 | 2619678.7131 | 1240938.9645 | 2619673.1102 | 1240953.3831
43 | 2619680.3012 | 1240934.8777 | 2619678.7131 | 1240938.9645
44 | 2619673.1102 | 1240953.3831 | 2619672.3366 | 1240955.3739
45 | 2619697.8982 | 1240898.9984 | 2619692.1037 | 1240904.5049 | 2619680.3012 | 1240934.8777
46 | 2619666.7735 | 1240969.6901 | 2619672.3366 | 1240955.3739
47 | 2619676.0987 | 1240858.601 | 2619697.8982 | 1240898.9984
48 | 2619666.7735 | 1240969.6901 | 2619662.1031 | 1240981.709
49 | 2619676.0987 | 1240858.601 | 2619663.8989 | 1240860.006
50 | 2619662.1031 | 1240981.709 | 2619661.6023 | 1240982.9977 | 2619648.4565 | 1241008.0664
51 | 2619636.9597 | 1240852.9701 | 2619663.8989 | 1240860.006
52 | 2619733.6022 | 1240954.9962 | 2619730.293 | 1240949.9651
53 | 2619733.6022 | 1240954.9962 | 2619738.0466 | 1240961.2163
54 | 2619544.6174 | 1241068.4576 | 2619540.5142 | 1241078.6188
55 | 2619525.8692 | 1241179.0614 | 2619533.3982 | 1241172.5057
56 | 2619533.3982 | 1241172.5057 | 2619533.3982 | 1241172.5057 | 2619535.8079 | 1241167.1211
57 | 2619539.8719 | 1241158.0401 | 2619535.8079 | 1241167.1211
58 | 2619539.8719 | 1241158.0401 | 2619532.9226 | 1241156.1828 | 2619515.4032 | 1241140.8045
59 | 2619539.8719 | 1241158.0401 | 2619583.1022 | 1241143.9066
60 | 2619515.4032 | 1241140.8045 | 2619493.9563 | 1241121.2837
61 | 2619583.1022 | 1241143.9066 | 2619596.3702 | 1241140.3168
62 | 2619583.1022 | 1241143.9066 | 2619585.3 | 1241128.5041 | 2619593.4651 | 1241112.9335
63 | 2619486.398 | 1241114.4041 | 2619493.9563 | 1241121.2837
64 | 2619764.3476 | 1241025.8587 | 2619783.8804 | 1241031.9224 | 2619788.8536 | 1241033.8433
65 | 2619797.5848 | 1241037.2158 | 2619788.8536 | 1241033.8433
66 | 2619797.5848 | 1241037.2158 | 2619780.5127 | 1241017.0241 | 2619762.039 | 1240993.7431
67 | 2619797.5848 | 1241037.2158 | 2619811.2002 | 1241051.7946
68 | 2619757.3991 | 1240987.8958 | 2619762.039 | 1240993.7431
69 | 2619748.3973 | 1240975.7027 | 2619753.681 | 1240982.8469 | 2619757.3991 | 1240987.8958
70 | 2619757.3991 | 1240987.8958 | 2619764.6956 | 1240985.4073 | 2619772.6929 | 1240985.8786
71 | 2619748.3973 | 1240975.7027 | 2619742.832 | 1240967.9138
72 | 2619748.3973 | 1240975.7027 | 2619736.0008 | 1240988.603 | 2619734.0771 | 1240992.7862
73 | 2619772.6929 | 1240985.8786 | 2619779.5032 | 1240969.8269
74 | 2619767.6189 | 1241112.5959 | 2619762.9286 | 1241113.3555
75 | 2619746.8635 | 1241115.9574 | 2619762.9286 | 1241113.3555
76 | 2619784.5463 | 1241108.1999 | 2619782.3315 | 1241108.9434 | 2619768.7569 | 1241112.4116 | 2619767.6189 | 1241112.5959
77 | 2619746.8635 | 1241115.9574 | 2619727.9379 | 1241119.0226
78 | 2619784.5463 | 1241108.1999 | 2619805.8668 | 1241133.8484
79 | 2619708.5625 | 1241122.1607 | 2619727.9379 | 1241119.0226
80 | 2619805.8668 | 1241133.8484 | 2619814.0027 | 1241134.1113
81 | 2619694.5587 | 1241124.4287 | 2619708.5625 | 1241122.1607
82 | 2619694.5587 | 1241124.4287 | 2619682.278 | 1241125.4966
83 | 2619694.5587 | 1241124.4287 | 2619719.9122 | 1241125.4911 | 2619746.878 | 1241128.2155 | 2619754.6536 | 1241131.6657 | 2619758.9664 | 1241136.5355
84 | 2619593.4651 | 1241112.9335 | 2619601.4702 | 1241097.668
85 | 2619601.4702 | 1241097.668 | 2619611.0763 | 1241079.3494
86 | 2619611.8985 | 1241077.7814 | 2619611.0763 | 1241079.3494
87 | 2619605.7444 | 1241137.7806 | 2619596.3702 | 1241140.3168
88 | 2619611.8985 | 1241077.7814 | 2619619.5219 | 1241063.2439
89 | 2619616.8294 | 1241134.7815 | 2619605.7444 | 1241137.7806
90 | 2619625.8174 | 1241051.2387 | 2619619.5219 | 1241063.2439
91 | 2619658.1003 | 1241127.5991 | 2619620.778 | 1241133.7131 | 2619616.8294 | 1241134.7815
92 | 2619614.1025 | 1240847.0003 | 2619636.9597 | 1240852.9701
93 | 2619637.6495 | 1241028.6751 | 2619647.5321 | 1241009.8292
94 | 2619636.8601 | 1241030.1805 | 2619637.6495 | 1241028.6751
95 | 2619648.4565 | 1241008.0664 | 2619647.5321 | 1241009.8292
96 | 2619636.8601 | 1241030.1805 | 2619628.6341 | 1241045.8672
97 | 2619628.6341 | 1241045.8672 | 2619625.8174 | 1241051.2387
98 | 2619487.6736 | 1241059.9065 | 2619486.7248 | 1241062.1782
99 | 2619492.6029 | 1241048.105 | 2619487.6736 | 1241059.9065
100 | 2619476.0551 | 1241087.7229 | 2619486.7248 | 1241062.1782
101 | 2619470.802 | 1241100.2998 | 2619476.0551 | 1241087.7229
102 | 2619470.802 | 1241100.2998 | 2619457.6543 | 1241086.3181
103 | 2619486.398 | 1241114.4041 | 2619470.802 | 1241100.2998
104 | 2619457.6543 | 1241086.3181 | 2619452.016 | 1241080.3221
105 | 2619466.2043 | 1241160.7004 | 2619469.3959 | 1241153.3951 | 2619486.398 | 1241114.4041
106 | 2619660.8028 | 1241078.4994 | 2619671.9461 | 1241083.9287
107 | 2619658.1003 | 1241127.5991 | 2619659.6007 | 1241117.3976 | 2619668.6517 | 1241107.3961
108 | 2619658.1003 | 1241127.5991 | 2619662.2447 | 1241127.2387
109 | 2619682.278 | 1241125.4966 | 2619662.2447 | 1241127.2387
110 | 2619759.2556 | 1241136.862 | 2619758.9664 | 1241136.5355
111 | 2619449.3977 | 1241077.5377 | 2619452.016 | 1241080.3221
112 | 2619466.2043 | 1241160.7004 | 2619453.0404 | 1241158.9007 | 2619447.3331 | 1241158.693 | 2619445.1453 | 1241159.5864 | 2619443.8927 | 1241161.1611 | 2619442.8568 | 1241163.537
113 | 2619449.3977 | 1241077.5377 | 2619439.498 | 1241066.9988
114 | 2619451.5989 | 1240984.6978 | 2619448.0006 | 1241012.3034
115 | 2619448.0006 | 1241012.3034 | 2619442.9186 | 1241044.9948
116 | 2619448.0006 | 1241012.3034 | 2619461.9107 | 1241014.7364
117 | 2619439.498 | 1241066.9988 | 2619442.9186 | 1241044.9948
118 | 2619461.9107 | 1241014.7364 | 2619475.0556 | 1241017.0355
119 | 2619731.1235 | 1240999.2087 | 2619734.0771 | 1240992.7862
120 | 2619738.0466 | 1240961.2163 | 2619742.832 | 1240967.9138
121 | 2619475.0556 | 1241017.0355 | 2619493.8237 | 1241020.3182
122 | 2619501.7014 | 1241021.6961 | 2619493.8237 | 1241020.3182

## bus_geodata
| x | y | coords
0 | 2619559.7064 | 1241031.0904
1 | 2619565.6027 | 1241016.4887
2 | 2619558.5019 | 1241034.0735
3 | 2619568.9633 | 1241008.1666
4 | 2619551.9333 | 1241050.3402
5 | 2619573.2823 | 1240997.4707
6 | 2619549.5447 | 1241056.2553
7 | 2619576.218 | 1240990.2006
8 | 2619548.7166 | 1241058.306
9 | 2619528.9644 | 1240956.0305
10 | 2619513.3709 | 1240951.3458
11 | 2619544.1267 | 1240960.5858
12 | 2619508.195 | 1240969.8378
13 | 2619453.9226 | 1240935.33
14 | 2619529.8877 | 1240894.6199
15 | 2619507.9875 | 1240970.5788
16 | 2619452.8732 | 1240957.6241
17 | 2619505.9121 | 1240977.9936
18 | 2619451.6654 | 1240983.2847
19 | 2619730.467 | 1241063.5853
20 | 2619757.381 | 1241074.8822
21 | 2619706.2023 | 1241053.4005
22 | 2619772.2026 | 1241081.1034
23 | 2619714.7957 | 1241034.714
24 | 2619698.2034 | 1241069.4063
25 | 2619717.7649 | 1241028.2574
26 | 2619688.1234 | 1241084.44
27 | 2619687.4563 | 1241063.8405
28 | 2619725.051 | 1241012.4135
29 | 2619684.3983 | 1241089.9957
30 | 2619681.1992 | 1241060.6001
31 | 2619595.77 | 1240928.9024
32 | 2619590.082 | 1240954.314
33 | 2619596.3454 | 1240926.3319
34 | 2619589.3019 | 1240957.7992
35 | 2619596.3978 | 1240926.0976
36 | 2619580.7798 | 1240978.9036
37 | 2619596.9167 | 1240923.7797
38 | 2619602.2055 | 1240900.1515
39 | 2619678.7131 | 1240938.9645
40 | 2619673.1102 | 1240953.3831
41 | 2619680.3012 | 1240934.8777
42 | 2619672.3366 | 1240955.3739
43 | 2619697.8982 | 1240898.9984
44 | 2619666.7735 | 1240969.6901
45 | 2619676.0987 | 1240858.601
46 | 2619662.1031 | 1240981.709
47 | 2619663.8989 | 1240860.006
48 | 2619730.293 | 1240949.9651
49 | 2619733.6022 | 1240954.9962
50 | 2619544.6174 | 1241068.4576
51 | 2619525.8692 | 1241179.0614
52 | 2619533.3982 | 1241172.5057
53 | 2619535.8079 | 1241167.1211
54 | 2619539.8719 | 1241158.0401
55 | 2619515.4032 | 1241140.8045
56 | 2619583.1022 | 1241143.9066
57 | 2619540.5142 | 1241078.6188
58 | 2619493.9563 | 1241121.2837
59 | 2619788.8536 | 1241033.8433
60 | 2619764.3476 | 1241025.8587
61 | 2619797.5848 | 1241037.2158
62 | 2619762.039 | 1240993.7431
63 | 2619811.2002 | 1241051.7946
64 | 2619757.3991 | 1240987.8958
65 | 2619748.3973 | 1240975.7027
66 | 2619772.6929 | 1240985.8786
67 | 2619762.9286 | 1241113.3555
68 | 2619767.6189 | 1241112.5959
69 | 2619746.8635 | 1241115.9574
70 | 2619784.5463 | 1241108.1999
71 | 2619727.9379 | 1241119.0226
72 | 2619805.8668 | 1241133.8484
73 | 2619708.5625 | 1241122.1607
74 | 2619814.0027 | 1241134.1113
75 | 2619694.5587 | 1241124.4287
76 | 2619593.4651 | 1241112.9335
77 | 2619601.4702 | 1241097.668
78 | 2619611.0763 | 1241079.3494
79 | 2619596.3702 | 1241140.3168
80 | 2619611.8985 | 1241077.7814
81 | 2619605.7444 | 1241137.7806
82 | 2619619.5219 | 1241063.2439
83 | 2619616.8294 | 1241134.7815
84 | 2619636.9597 | 1240852.9701
85 | 2619614.1025 | 1240847.0003
86 | 2619637.6495 | 1241028.6751
87 | 2619647.5321 | 1241009.8292
88 | 2619636.8601 | 1241030.1805
89 | 2619648.4565 | 1241008.0664
90 | 2619628.6341 | 1241045.8672
91 | 2619625.8174 | 1241051.2387
92 | 2619487.6736 | 1241059.9065
93 | 2619486.7248 | 1241062.1782
94 | 2619492.6029 | 1241048.105
95 | 2619476.0551 | 1241087.7229
96 | 2619470.802 | 1241100.2998
97 | 2619457.6543 | 1241086.3181
98 | 2619486.398 | 1241114.4041
99 | 2619671.9461 | 1241083.9287
100 | 2619660.8028 | 1241078.4994
101 | 2619668.6517 | 1241107.3961
102 | 2619658.1003 | 1241127.5991
103 | 2619662.2447 | 1241127.2387
104 | 2619758.9664 | 1241136.5355
105 | 2619759.2556 | 1241136.862
106 | 2619682.278 | 1241125.4966
107 | 2619452.016 | 1241080.3221
108 | 2619466.2043 | 1241160.7004
109 | 2619449.3977 | 1241077.5377
110 | 2619442.8568 | 1241163.537
111 | 2619451.5989 | 1240984.6978
112 | 2619448.0006 | 1241012.3034
113 | 2619442.9186 | 1241044.9948
114 | 2619461.9107 | 1241014.7364
115 | 2619731.1235 | 1240999.2087
116 | 2619734.0771 | 1240992.7862
117 | 2619738.0466 | 1240961.2163
118 | 2619475.0556 | 1241017.0355
119 | 2619493.8237 | 1241020.3182
120 | 2619501.7014 | 1241021.6961
121 | 2619439.498 | 1241066.9988
122 | 2619779.5032 | 1240969.8269
123 | 2619742.832 | 1240967.9138
124 | 2619583.1022 | 1241143.9066

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97431 | -0.18059 | 0.0011299 | 0.00028318
1 | 0.97457 | -0.17875 | 0.0014115 | 0.00035375
2 | 0.97426 | -0.18093 | 0.0018394 | 0.000461
3 | 0.97473 | -0.17756 | 0.0012322 | 0.00030882
4 | 0.97405 | -0.18244 | 0.0015557 | 0.0003899
5 | 0.97496 | -0.17589 | 0.0019466 | 0.00048787
6 | 0.97399 | -0.18289 | 0.0019177 | 0.00048063
7 | 0.97514 | -0.17459 | 0.0023662 | 0.00059302
8 | 0.97397 | -0.183 | 0.0016546 | 0.00041469
9 | 0.97143 | -0.20112 | 0.001346 | 0.00033734
10 | 0.97149 | -0.20066 | 0 | 0
11 | 0.97139 | -0.20135 | 0.0013687 | 0.00034302
12 | 0.97137 | -0.20151 | 0.0013319 | 0.00033382
13 | 0.97235 | -0.1945 | 0 | 0
14 | 0.97127 | -0.20226 | 0.0025636 | 0.0006425
15 | 0.97137 | -0.20153 | 0.0016047 | 0.00040218
16 | 0.97266 | -0.19226 | 0.0015606 | 0.00039111
17 | 0.97136 | -0.20163 | 0.0012566 | 0.00031493
18 | 0.97307 | -0.18927 | 0.0029383 | 0.00073641
19 | 0.97567 | -0.17064 | 0.0024783 | 0.00062111
20 | 0.97543 | -0.17238 | 0.0023969 | 0.00060071
21 | 0.97599 | -0.16839 | 0 | 0
22 | 0.97535 | -0.17294 | 0.0032863 | 0.00082363
23 | 0.97501 | -0.17537 | 0.0074263 | 0.0018612
24 | 0.97704 | -0.16081 | 0.0022694 | 0.00056876
25 | 0.97475 | -0.17722 | 0.0032054 | 0.00080334
26 | 0.9783 | -0.15181 | 0.0018374 | 0.00046051
27 | 0.97696 | -0.16142 | 0.0016024 | 0.00040159
28 | 0.9742 | -0.1812 | 0.002275 | 0.00057016
29 | 0.97879 | -0.14837 | 0 | 0
30 | 0.97693 | -0.16165 | 0.0031993 | 0.00080181
31 | 0.97725 | -0.15951 | 0.0019359 | 0.00048519
32 | 0.97628 | -0.16642 | 0.0014366 | 0.00036006
33 | 0.97735 | -0.15876 | 0.0023844 | 0.00059758
34 | 0.97616 | -0.16731 | 0.0030729 | 0.00077015
35 | 0.97736 | -0.15869 | 0.00179 | 0.00044862
36 | 0.97547 | -0.17228 | 0.0027106 | 0.00067933
37 | 0.97747 | -0.15791 | 0.0016241 | 0.00040703
38 | 0.97864 | -0.14955 | 0.0032659 | 0.00081851
39 | 0.99059 | -0.065239 | 0.0023007 | 0.0005766
40 | 0.99163 | -0.057975 | 0.0017935 | 0.00044949
41 | 0.99031 | -0.067198 | 0.0026704 | 0.00066925
42 | 0.99178 | -0.056934 | 0.0018724 | 0.00046928
43 | 0.98787 | -0.084273 | 0 | 0
44 | 0.9929 | -0.049168 | 0.0028569 | 0.000716
45 | 0.98511 | -0.10368 | 0 | 0
46 | 0.99389 | -0.042289 | 0.0023672 | 0.00059326
47 | 0.98437 | -0.10889 | 0.0022197 | 0.00055631
48 | 0.97289 | -0.19059 | 0.0012615 | 0.00031617
49 | 0.9729 | -0.19051 | 0 | 0
50 | 0.97393 | -0.18335 | 0.0015136 | 0.00037936
51 | 0.98484 | -0.10541 | 0.0012855 | 0.00032217
52 | 0.98486 | -0.10527 | 0.0020101 | 0.00050377
53 | 0.98489 | -0.10507 | 0.0025209 | 0.00063179
54 | 0.98497 | -0.10448 | 0 | 0
55 | 0.98359 | -0.11424 | 0 | 0
56 | 0.98723 | -0.088632 | 0 | 0
57 | 0.9739 | -0.18353 | 0.0015392 | 0.00038575
58 | 0.98096 | -0.13291 | 0.0039692 | 0.00099476
59 | 0.97175 | -0.19885 | 0.0031351 | 0.00078573
60 | 0.97163 | -0.19972 | 0.0031991 | 0.00080177
61 | 0.97183 | -0.19823 | 0 | 0
62 | 0.97261 | -0.19262 | 0.0023871 | 0.00059827
63 | 0.97174 | -0.19888 | 0.003108 | 0.00077894
64 | 0.97274 | -0.19169 | 0 | 0
65 | 0.97302 | -0.18966 | 0 | 0
66 | 0.97272 | -0.19183 | 0 | 0
67 | 0.98024 | -0.13815 | 0.00077901 | 0.00019524
68 | 0.98016 | -0.13868 | 0.0016188 | 0.00040571
69 | 0.98051 | -0.1362 | 0.00078177 | 0.00019593
70 | 0.97993 | -0.14034 | 0.0029374 | 0.00073618
71 | 0.98085 | -0.13375 | 0.00097034 | 0.00024319
72 | 0.97963 | -0.14249 | 0.0034046 | 0.00085328
73 | 0.98123 | -0.13105 | 0.0008133 | 0.00020383
74 | 0.9796 | -0.14273 | 0.0027877 | 0.00069867
75 | 0.98152 | -0.12897 | 0 | 0
76 | 0.99103 | -0.061999 | 0.0015276 | 0.00038285
77 | 0.99303 | -0.048093 | 0.0013102 | 0.00032837
78 | 0.99545 | -0.031343 | 0.0015514 | 0.00038882
79 | 0.98633 | -0.094935 | 0.00093938 | 0.00023543
80 | 0.99566 | -0.029899 | 0.0024572 | 0.00061584
81 | 0.9857 | -0.099348 | 0.0035725 | 0.00089536
82 | 0.99762 | -0.01634 | 0.001452 | 0.0003639
83 | 0.98499 | -0.10436 | 0.0056588 | 0.0014182
84 | 0.98279 | -0.1201 | 0.0026649 | 0.00066789
85 | 0.98153 | -0.12898 | 0 | 0
86 | 0.99823 | -0.012174 | 0.0024368 | 0.00061071
87 | 0.99643 | -0.024654 | 0.0013705 | 0.00034348
88 | 0.99838 | -0.011138 | 0.0020182 | 0.00050581
89 | 0.99626 | -0.025796 | 0.0019577 | 0.00049065
90 | 1 | 0 | -0.23602 | -0.059553
91 | 0.99926 | -0.0050835 | 0.0019527 | 0.0004894
92 | 0.97802 | -0.15381 | 0.0030389 | 0.00076162
93 | 0.97804 | -0.15369 | 0.0030386 | 0.00076154
94 | 0.97799 | -0.15407 | 0.0019397 | 0.00048614
95 | 0.97836 | -0.15137 | 0.0030414 | 0.00076224
96 | 0.97858 | -0.1498 | 0 | 0
97 | 0.97752 | -0.15739 | 0.0019095 | 0.00047857
98 | 0.98009 | -0.1391 | 0 | 0
99 | 0.9787 | -0.14898 | 0.0012403 | 0.00031086
100 | 0.97865 | -0.14937 | 0.0029912 | 0.00074967
101 | 0.98063 | -0.13528 | 0.0022264 | 0.00055799
102 | 0.98257 | -0.1215 | 0 | 0
103 | 0.98243 | -0.12251 | 0.0026833 | 0.00067249
104 | 0.98125 | -0.1309 | 0.001532 | 0.00038394
105 | 0.98125 | -0.13091 | 0.001226 | 0.00030727
106 | 0.98182 | -0.12682 | 0.0038531 | 0.00096569
107 | 0.97708 | -0.16049 | 0.0026238 | 0.00065759
108 | 0.9794 | -0.14398 | 0 | 0
109 | 0.9769 | -0.16182 | 0 | 0
110 | 0.97905 | -0.14648 | 0.0092875 | 0.0023277
111 | 0.9731 | -0.18906 | 0 | 0
112 | 0.97367 | -0.18496 | 0 | 0
113 | 0.9751 | -0.17466 | 0.0037556 | 0.00094123
114 | 0.97335 | -0.18728 | 0.0054541 | 0.0013669
115 | 0.97379 | -0.18417 | 0.00079775 | 0.00019994
116 | 0.97359 | -0.18556 | 0.0013157 | 0.00032974
117 | 0.97292 | -0.19041 | 0.0020266 | 0.00050792
118 | 0.97315 | -0.18871 | 0.0062234 | 0.0015597
119 | 0.97304 | -0.1895 | 0.0015256 | 0.00038235
120 | 0.97301 | -0.1897 | 0.0024137 | 0.00060492
121 | 0.97619 | -0.16686 | 0 | 0
122 | 0.9727 | -0.19199 | 0.00085477 | 0.00021423
123 | 0.97296 | -0.19013 | 0.0013201 | 0.00033084
124 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.011153 | -0.002795 | 0.011156 | 0.0027959 | 2.851e-06 | 9.0037e-07 | 0.017034 | 0.017033 | 0.017034 | 0.97431 | -0.18059 | 0.97457 | -0.17875 | 6.3087
1 | 0.010023 | 0.0025118 | -0.010023 | -0.0025117 | 4.7042e-07 | 1.4087e-07 | 0.015308 | 0.015308 | 0.015308 | 0.97431 | -0.18059 | 0.97426 | -0.18093 | 5.6696
2 | -0.012567 | -0.0031496 | 0.01257 | 0.0031503 | 2.0621e-06 | 6.8126e-07 | 0.019189 | 0.019189 | 0.019189 | 0.97457 | -0.17875 | 0.97473 | -0.17756 | 7.1069
3 | 0.0081833 | 0.0020507 | -0.0081816 | -0.0020502 | 1.71e-06 | 4.3929e-07 | 0.012498 | 0.012499 | 0.012499 | 0.97426 | -0.18093 | 0.97405 | -0.18244 | 4.6291
4 | -0.013802 | -0.0034591 | 0.013805 | 0.0034602 | 3.1953e-06 | 1.0852e-06 | 0.02107 | 0.02107 | 0.02107 | 0.97473 | -0.17756 | 0.97496 | -0.17589 | 7.8036
5 | 0.0066259 | 0.0016603 | -0.0066255 | -0.0016602 | 4.0783e-07 | 7.7459e-08 | 0.010122 | 0.010122 | 0.010122 | 0.97405 | -0.18244 | 0.97399 | -0.18289 | 3.7489
6 | -0.015752 | -0.0039481 | 0.015754 | 0.0039491 | 2.8276e-06 | 9.8974e-07 | 0.024041 | 0.024041 | 0.024041 | 0.97496 | -0.17589 | 0.97514 | -0.17459 | 8.9039
7 | 0.0047077 | 0.0011796 | -0.0047076 | -0.0011796 | 7.1382e-08 | -6.8755e-11 | 0.0071921 | 0.0071921 | 0.0071921 | 0.97399 | -0.18289 | 0.97397 | -0.183 | 2.6638
8 | -0.018121 | -0.0045421 | 0.018126 | 0.0045442 | 5.8127e-06 | 2.0836e-06 | 0.027651 | 0.027651 | 0.027651 | 0.97514 | -0.17459 | 0.97547 | -0.17228 | 10.2412
9 | 0.003053 | 0.0007649 | -0.0030528 | -0.00076498 | 1.4862e-07 | -7.9083e-08 | 0.0046642 | 0.0046642 | 0.0046642 | 0.97397 | -0.183 | 0.97393 | -0.18335 | 1.7275
10 | -0.0027147 | -0.00068019 | 0.0027149 | 0.00068005 | 1.7568e-07 | -1.3402e-07 | 0.0041583 | 0.0041582 | 0.0041583 | 0.97143 | -0.20112 | 0.97149 | -0.20066 | 1.5401
11 | 0.0013687 | 0.00034284 | -0.0013687 | -0.00034302 | 4.3424e-08 | -1.7929e-07 | 0.0020965 | 0.0020966 | 0.0020966 | 0.97143 | -0.20112 | 0.97139 | -0.20135 | 0.77651
12 | 0.0041938 | 0.0010508 | -0.0041933 | -0.0010508 | 4.9441e-07 | -4.758e-08 | 0.0064234 | 0.0064235 | 0.0064235 | 0.97149 | -0.20066 | 0.97137 | -0.20151 | 2.3791
13 | -0.0094729 | -0.0023728 | 0.0094809 | 0.0023752 | 8.0718e-06 | 2.343e-06 | 0.014509 | 0.014509 | 0.014509 | 0.97149 | -0.20066 | 0.97235 | -0.1945 | 5.3737
14 | 0.0025642 | 0.00064199 | -0.0025636 | -0.0006425 | 5.6865e-07 | -5.1266e-07 | 0.0039273 | 0.0039275 | 0.0039275 | 0.97149 | -0.20066 | 0.97127 | -0.20226 | 1.4546
15 | 0.0028613 | 0.00071702 | -0.0028613 | -0.00071702 | 9.2256e-09 | -5.9778e-09 | 0.0043832 | 0.0043832 | 0.0043832 | 0.97137 | -0.20151 | 0.97137 | -0.20153 | 1.6234
16 | -0.0094809 | -0.0023752 | 0.0094839 | 0.002376 | 2.9316e-06 | 8.5062e-07 | 0.014509 | 0.014509 | 0.014509 | 0.97235 | -0.1945 | 0.97266 | -0.19226 | 5.3736
17 | 0.0012566 | 0.00031484 | -0.0012566 | -0.00031493 | 1.7803e-08 | -8.8465e-08 | 0.0019249 | 0.001925 | 0.001925 | 0.97137 | -0.20153 | 0.97136 | -0.20163 | 0.71295
18 | -0.011044 | -0.0027671 | 0.011049 | 0.0027686 | 4.5761e-06 | 1.4411e-06 | 0.016896 | 0.016896 | 0.016896 | 0.97266 | -0.19226 | 0.97307 | -0.18927 | 6.2578
19 | -0.013987 | -0.003505 | 0.013988 | 0.0035051 | 4.0387e-07 | 1.3776e-07 | 0.021389 | 0.021389 | 0.021389 | 0.97307 | -0.18927 | 0.9731 | -0.18906 | 7.9219
20 | 0.0056848 | 0.0014244 | -0.0056835 | -0.0014242 | 1.3691e-06 | 1.6214e-07 | 0.0086699 | 0.00867 | 0.00867 | 0.97567 | -0.17064 | 0.97543 | -0.17238 | 3.2111
21 | -0.0081631 | -0.0020455 | 0.0081656 | 0.0020462 | 2.5451e-06 | 6.5012e-07 | 0.01245 | 0.012449 | 0.01245 | 0.97567 | -0.17064 | 0.97599 | -0.16839 | 4.6109
22 | 0.0032866 | 0.00082353 | -0.0032863 | -0.00082363 | 2.5213e-07 | -1.0366e-07 | 0.0050136 | 0.0050137 | 0.0050137 | 0.97543 | -0.17238 | 0.97535 | -0.17294 | 1.8569
23 | 0.032398 | 0.0081275 | -0.032366 | -0.0081157 | 3.1317e-05 | 1.1788e-05 | 0.049397 | 0.049397 | 0.049397 | 0.97599 | -0.16839 | 0.97501 | -0.17537 | 18.2953
24 | -0.040563 | -0.010174 | 0.040606 | 0.01019 | 4.2688e-05 | 1.6195e-05 | 0.061847 | 0.061847 | 0.061847 | 0.97599 | -0.16839 | 0.97704 | -0.16081 | 22.9062
25 | 0.02494 | 0.0062545 | -0.024934 | -0.0062521 | 6.4249e-06 | 2.3825e-06 | 0.038064 | 0.038064 | 0.038064 | 0.97501 | -0.17537 | 0.97475 | -0.17722 | 14.0977
26 | -0.047678 | -0.011962 | 0.047737 | 0.011985 | 5.9558e-05 | 2.268e-05 | 0.072616 | 0.072616 | 0.072616 | 0.97704 | -0.16081 | 0.9783 | -0.15181 | 26.8949
27 | 0.0048022 | 0.0012034 | -0.0048018 | -0.0012034 | 4.0395e-07 | 3.8038e-09 | 0.0073135 | 0.0073136 | 0.0073136 | 0.97704 | -0.16081 | 0.97696 | -0.16142 | 2.7087
28 | 0.021728 | 0.0054487 | -0.021716 | -0.0054444 | 1.1973e-05 | 4.3878e-06 | 0.033171 | 0.033171 | 0.033171 | 0.97475 | -0.17722 | 0.9742 | -0.1812 | 12.2854
29 | -0.049575 | -0.012445 | 0.049598 | 0.012454 | 2.3736e-05 | 9.0454e-06 | 0.075411 | 0.075411 | 0.075411 | 0.9783 | -0.15181 | 0.97879 | -0.14837 | 27.93
30 | 0.0031994 | 0.00080177 | -0.0031993 | -0.00080181 | 1.0441e-07 | -4.8072e-08 | 0.004873 | 0.004873 | 0.004873 | 0.97696 | -0.16142 | 0.97693 | -0.16165 | 1.8048
31 | 0.019441 | 0.0048742 | -0.019433 | -0.0048713 | 7.9977e-06 | 2.8951e-06 | 0.029696 | 0.029696 | 0.029696 | 0.9742 | -0.1812 | 0.97379 | -0.18417 | 10.9985
32 | -0.05383 | -0.013515 | 0.053928 | 0.013552 | 9.8092e-05 | 3.7432e-05 | 0.081845 | 0.081845 | 0.081845 | 0.97879 | -0.14837 | 0.98063 | -0.13528 | 30.3129
33 | 0.0042321 | 0.0010604 | -0.0042317 | -0.0010604 | 3.5779e-07 | -3.6469e-08 | 0.0064338 | 0.0064339 | 0.0064339 | 0.97879 | -0.14837 | 0.9787 | -0.14898 | 2.3829
34 | 0.025388 | 0.0063691 | -0.025364 | -0.0063601 | 2.4286e-05 | 9.0147e-06 | 0.03866 | 0.03866 | 0.03866 | 0.97725 | -0.15951 | 0.97628 | -0.16642 | 14.3184
35 | -0.027324 | -0.0068543 | 0.027327 | 0.0068553 | 2.8456e-06 | 1.0614e-06 | 0.041607 | 0.041607 | 0.041607 | 0.97725 | -0.15951 | 0.97735 | -0.15876 | 15.4102
36 | 0.023927 | 0.006 | -0.023924 | -0.0059989 | 2.9641e-06 | 1.0954e-06 | 0.03647 | 0.03647 | 0.03647 | 0.97628 | -0.16642 | 0.97616 | -0.16731 | 13.5075
37 | -0.029711 | -0.0074529 | 0.029712 | 0.007453 | 3.0661e-07 | 1.1492e-07 | 0.045238 | 0.045238 | 0.045238 | 0.97735 | -0.15876 | 0.97736 | -0.15869 | 16.7547
38 | 0.020851 | 0.0052288 | -0.020837 | -0.0052235 | 1.4349e-05 | 5.2346e-06 | 0.031786 | 0.031786 | 0.031786 | 0.97616 | -0.16731 | 0.97547 | -0.17228 | 11.7726
39 | -0.031502 | -0.0079016 | 0.031505 | 0.0079029 | 3.4095e-06 | 1.2816e-06 | 0.047963 | 0.047963 | 0.047963 | 0.97736 | -0.15869 | 0.97747 | -0.15791 | 17.764
40 | -0.033129 | -0.00831 | 0.033168 | 0.0083244 | 3.8433e-05 | 1.4478e-05 | 0.050435 | 0.050435 | 0.050435 | 0.97747 | -0.15791 | 0.97864 | -0.14955 | 18.6797
41 | -0.036433 | -0.0091429 | 0.036538 | 0.0091824 | 0.00010431 | 3.9435e-05 | 0.055401 | 0.055401 | 0.055401 | 0.97864 | -0.14955 | 0.98153 | -0.12898 | 20.5188
42 | -0.046755 | -0.01179 | 0.046803 | 0.011808 | 4.7648e-05 | 1.8127e-05 | 0.070259 | 0.070258 | 0.070259 | 0.99059 | -0.065239 | 0.99163 | -0.057975 | 26.0217
43 | 0.044454 | 0.011213 | -0.044442 | -0.011208 | 1.2209e-05 | 4.6395e-06 | 0.066803 | 0.066803 | 0.066803 | 0.99059 | -0.065239 | 0.99031 | -0.067198 | 24.7417
44 | -0.048596 | -0.012257 | 0.048603 | 0.01226 | 7.0927e-06 | 2.7004e-06 | 0.07295 | 0.07295 | 0.07295 | 0.99163 | -0.057975 | 0.99178 | -0.056934 | 27.0184
45 | 0.041772 | 0.010539 | -0.041672 | -0.010501 | 9.9832e-05 | 3.7876e-05 | 0.06279 | 0.06279 | 0.06279 | 0.99031 | -0.067198 | 0.98787 | -0.084273 | 23.2557
46 | -0.050476 | -0.012729 | 0.050531 | 0.01275 | 5.5007e-05 | 2.0958e-05 | 0.075759 | 0.075759 | 0.075759 | 0.99178 | -0.056934 | 0.9929 | -0.049168 | 28.0589
47 | 0.041672 | 0.010501 | -0.041559 | -0.010458 | 0.00011287 | 4.2826e-05 | 0.06279 | 0.062791 | 0.062791 | 0.98787 | -0.084273 | 0.98511 | -0.10368 | 23.2558
48 | -0.053388 | -0.013466 | 0.053439 | 0.013486 | 5.1547e-05 | 1.9659e-05 | 0.08004 | 0.08004 | 0.08004 | 0.9929 | -0.049168 | 0.99389 | -0.042289 | 29.6446
49 | 0.041559 | 0.010458 | -0.041529 | -0.010447 | 3.0213e-05 | 1.1464e-05 | 0.062791 | 0.062791 | 0.062791 | 0.98511 | -0.10368 | 0.98437 | -0.10889 | 23.2558
50 | -0.055806 | -0.014079 | 0.055936 | 0.014128 | 0.00012943 | 4.9394e-05 | 0.083584 | 0.083584 | 0.083584 | 0.99389 | -0.042289 | 0.99626 | -0.025796 | 30.9572
51 | 0.039309 | 0.0098906 | -0.039248 | -0.0098674 | 6.1374e-05 | 2.3252e-05 | 0.059435 | 0.059435 | 0.059435 | 0.98437 | -0.10889 | 0.98279 | -0.1201 | 22.0131
52 | -0.0012615 | -0.00031617 | 0.0012616 | 0.0003161 | 1.399e-08 | -6.9398e-08 | 0.0019295 | 0.0019295 | 0.0019295 | 0.97289 | -0.19059 | 0.9729 | -0.19051 | 0.71463
53 | -0.0012616 | -0.0003161 | 0.0012616 | 0.00031602 | 1.7759e-08 | -8.8103e-08 | 0.0019295 | 0.0019294 | 0.0019295 | 0.9729 | -0.19051 | 0.97292 | -0.19041 | 0.71462
54 | 0.0015392 | 0.00038563 | -0.0015392 | -0.00038575 | 3.7816e-08 | -1.2182e-07 | 0.0023516 | 0.0023517 | 0.0023517 | 0.97393 | -0.18335 | 0.9739 | -0.18353 | 0.87099
55 | -0.0012855 | -0.00032217 | 0.0012855 | 0.00032205 | 2.3499e-08 | -1.18e-07 | 0.0019422 | 0.0019422 | 0.0019422 | 0.98484 | -0.10541 | 0.98486 | -0.10527 | 0.71935
56 | -0.0032956 | -0.00082583 | 0.0032957 | 0.00082579 | 9.1263e-08 | -3.9969e-08 | 0.0049792 | 0.0049792 | 0.0049792 | 0.98486 | -0.10527 | 0.98489 | -0.10507 | 1.8441
57 | -0.0058165 | -0.0014576 | 0.005817 | 0.0014576 | 4.7942e-07 | 5.7775e-08 | 0.0087878 | 0.0087878 | 0.0087878 | 0.98489 | -0.10507 | 0.98497 | -0.10448 | 3.2548
58 | 0.062774 | 0.015802 | -0.062689 | -0.01577 | 8.5478e-05 | 3.2102e-05 | 0.094859 | 0.094859 | 0.094859 | 0.98497 | -0.10448 | 0.98359 | -0.11424 | 17.5665
59 | -0.068591 | -0.01726 | 0.068743 | 0.017317 | 0.00015204 | 5.7318e-05 | 0.10365 | 0.10365 | 0.10365 | 0.98497 | -0.10448 | 0.98723 | -0.088632 | 19.1938
60 | 0.062689 | 0.01577 | -0.062526 | -0.015708 | 0.00016284 | 6.2262e-05 | 0.094859 | 0.094859 | 0.094859 | 0.98359 | -0.11424 | 0.98096 | -0.13291 | 35.1331
61 | 0.090248 | 0.022721 | -0.090169 | -0.022691 | 7.9395e-05 | 3.0185e-05 | 0.13606 | 0.13606 | 0.13606 | 0.98723 | -0.088632 | 0.98633 | -0.094935 | 25.1972
62 | -0.15899 | -0.040038 | 0.15959 | 0.040266 | 0.00059413 | 0.00022766 | 0.23971 | 0.23971 | 0.23971 | 0.98723 | -0.088632 | 0.99103 | -0.061999 | 44.3909
63 | 0.058557 | 0.014713 | -0.058506 | -0.014694 | 5.0333e-05 | 1.923e-05 | 0.088839 | 0.088839 | 0.088839 | 0.98096 | -0.13291 | 0.98009 | -0.1391 | 32.9032
64 | 0.0031995 | 0.0008016 | -0.0031991 | -0.00080177 | 3.8618e-07 | -1.7085e-07 | 0.0048992 | 0.0048993 | 0.0048993 | 0.97175 | -0.19885 | 0.97163 | -0.19972 | 1.8146
65 | -0.0063346 | -0.0015873 | 0.0063351 | 0.0015874 | 5.4953e-07 | 9.5392e-08 | 0.0096999 | 0.0096999 | 0.0096999 | 0.97175 | -0.19885 | 0.97183 | -0.19823 | 3.5926
66 | -0.0094434 | -0.0023662 | 0.0094508 | 0.0023684 | 7.3265e-06 | 2.1215e-06 | 0.014459 | 0.014459 | 0.014459 | 0.97183 | -0.19823 | 0.97261 | -0.19262 | 5.3552
67 | 0.0031083 | 0.00077881 | -0.003108 | -0.00077894 | 2.8194e-07 | -1.3871e-07 | 0.0047592 | 0.0047593 | 0.0047593 | 0.97183 | -0.19823 | 0.97174 | -0.19888 | 1.7627
68 | -0.011838 | -0.0029666 | 0.011839 | 0.0029671 | 1.5278e-06 | 4.9497e-07 | 0.018111 | 0.018111 | 0.018111 | 0.97261 | -0.19262 | 0.97274 | -0.19169 | 6.7078
69 | -0.012694 | -0.0031809 | 0.012698 | 0.0031821 | 3.5626e-06 | 1.1822e-06 | 0.019418 | 0.019418 | 0.019418 | 0.97274 | -0.19169 | 0.97302 | -0.18966 | 7.192
70 | 0.00085481 | 0.00021383 | -0.00085479 | -0.00021402 | 1.6724e-08 | -1.8817e-07 | 0.0013075 | 0.0013075 | 0.0013075 | 0.97274 | -0.19169 | 0.97272 | -0.19183 | 0.48427
71 | 0.0046087 | 0.0011547 | -0.0046084 | -0.0011547 | 2.9671e-07 | -4.7757e-09 | 0.0070478 | 0.0070479 | 0.0070479 | 0.97302 | -0.18966 | 0.97296 | -0.19013 | 2.6103
72 | -0.017306 | -0.0043368 | 0.017316 | 0.0043403 | 9.8324e-06 | 3.5021e-06 | 0.026466 | 0.026466 | 0.026466 | 0.97302 | -0.18966 | 0.97359 | -0.18556 | 9.8023
73 | 0.00085479 | 0.00021402 | -0.00085477 | -0.00021423 | 1.8603e-08 | -2.0929e-07 | 0.0013075 | 0.0013076 | 0.0013076 | 0.97272 | -0.19183 | 0.9727 | -0.19199 | 0.4843
74 | 0.010753 | 0.0026949 | -0.010753 | -0.0026946 | 7.9004e-07 | 2.4397e-07 | 0.016324 | 0.016324 | 0.016324 | 0.98024 | -0.13815 | 0.98016 | -0.13868 | 6.0458
75 | -0.011532 | -0.0028901 | 0.011535 | 0.0028911 | 3.1123e-06 | 9.9182e-07 | 0.017506 | 0.017506 | 0.017506 | 0.98024 | -0.13815 | 0.98051 | -0.1362 | 6.4838
76 | 0.0091337 | 0.0022889 | -0.0091316 | -0.0022883 | 2.0996e-06 | 5.8702e-07 | 0.013866 | 0.013866 | 0.013866 | 0.98016 | -0.13868 | 0.97993 | -0.14034 | 5.1357
77 | -0.012317 | -0.003087 | 0.012321 | 0.0030884 | 4.1802e-06 | 1.3659e-06 | 0.018693 | 0.018693 | 0.018693 | 0.98051 | -0.1362 | 0.98085 | -0.13375 | 6.9232
78 | 0.0061943 | 0.0015522 | -0.0061924 | -0.0015519 | 1.8413e-06 | 2.8814e-07 | 0.0094059 | 0.009406 | 0.009406 | 0.97993 | -0.14034 | 0.97963 | -0.14249 | 3.4837
79 | -0.013292 | -0.0033316 | 0.013297 | 0.0033333 | 4.9801e-06 | 1.6676e-06 | 0.020165 | 0.020165 | 0.020165 | 0.98085 | -0.13375 | 0.98123 | -0.13105 | 7.4684
80 | 0.0027878 | 0.0006986 | -0.0027877 | -0.00069867 | 9.1082e-08 | -6.7451e-08 | 0.0042345 | 0.0042346 | 0.0042346 | 0.97963 | -0.14249 | 0.9796 | -0.14273 | 1.5684
81 | -0.01411 | -0.0035371 | 0.014114 | 0.0035385 | 4.0531e-06 | 1.3797e-06 | 0.021398 | 0.021398 | 0.021398 | 0.98123 | -0.13105 | 0.98152 | -0.12897 | 7.9251
82 | -0.016873 | -0.0042291 | 0.016878 | 0.0042309 | 5.0331e-06 | 1.78e-06 | 0.02558 | 0.02558 | 0.02558 | 0.98152 | -0.12897 | 0.98182 | -0.12682 | 9.474
83 | 0.0027587 | 0.00069064 | -0.002758 | -0.00069121 | 7.366e-07 | -5.6947e-07 | 0.004182 | 0.0041823 | 0.0041823 | 0.98152 | -0.12897 | 0.98125 | -0.1309 | 1.549
84 | -0.16111 | -0.040649 | 0.16143 | 0.04077 | 0.00031497 | 0.0001207 | 0.242 | 0.242 | 0.242 | 0.99103 | -0.061999 | 0.99303 | -0.048093 | 44.8156
85 | -0.16274 | -0.041098 | 0.16312 | 0.041245 | 0.00038412 | 0.0001472 | 0.24397 | 0.24397 | 0.24397 | 0.99303 | -0.048093 | 0.99545 | -0.031343 | 45.1792
86 | -0.16467 | -0.041634 | 0.16471 | 0.041647 | 3.3506e-05 | 1.2841e-05 | 0.24629 | 0.24629 | 0.24629 | 0.99545 | -0.031343 | 0.99566 | -0.029899 | 45.6086
87 | 0.089229 | 0.022455 | -0.089174 | -0.022435 | 5.4932e-05 | 2.088e-05 | 0.13465 | 0.13465 | 0.13465 | 0.98633 | -0.094935 | 0.9857 | -0.099348 | 24.9348
88 | -0.16716 | -0.042263 | 0.16748 | 0.042385 | 0.00031999 | 0.00012264 | 0.24996 | 0.24996 | 0.24996 | 0.99566 | -0.029899 | 0.99762 | -0.01634 | 46.2887
89 | 0.085602 | 0.021539 | -0.085542 | -0.021516 | 5.9858e-05 | 2.273e-05 | 0.12925 | 0.12925 | 0.12925 | 0.9857 | -0.099348 | 0.98499 | -0.10436 | 23.9361
90 | -0.16894 | -0.042749 | 0.16921 | 0.042852 | 0.00026885 | 0.00010305 | 0.25212 | 0.25212 | 0.25212 | 0.99762 | -0.01634 | 0.99926 | -0.0050835 | 46.6897
91 | 0.079883 | 0.020098 | -0.079693 | -0.020026 | 0.00019052 | 7.2212e-05 | 0.12071 | 0.12071 | 0.12071 | 0.98499 | -0.10436 | 0.98257 | -0.1215 | 22.3531
92 | 0.036583 | 0.0091995 | -0.036538 | -0.0091824 | 4.5244e-05 | 1.7103e-05 | 0.055401 | 0.055401 | 0.055401 | 0.98279 | -0.1201 | 0.98153 | -0.12898 | 20.5187
93 | 0.059377 | 0.015006 | -0.059273 | -0.014966 | 0.00010413 | 3.9773e-05 | 0.088555 | 0.088555 | 0.088555 | 0.99823 | -0.012174 | 0.99643 | -0.024654 | 32.7981
94 | -0.061814 | -0.015617 | 0.061823 | 0.01562 | 9.0141e-06 | 3.4447e-06 | 0.092187 | 0.092187 | 0.092187 | 0.99823 | -0.012174 | 0.99838 | -0.011138 | 34.1434
95 | 0.057903 | 0.014623 | -0.057893 | -0.014619 | 9.2951e-06 | 3.5491e-06 | 0.086508 | 0.086508 | 0.086508 | 0.99643 | -0.024654 | 0.99626 | -0.025796 | 32.0401
96 | -0.063841 | -0.016126 | 0.063942 | 0.016164 | 0.00010016 | 3.8291e-05 | 0.095195 | 0.095195 | 0.095195 | 0.99838 | -0.011138 | 1 | 0 | 35.2574
97 | 0.17128 | 0.043389 | -0.17116 | -0.043342 | 0.00012308 | 4.718e-05 | 0.25503 | 0.25503 | 0.25503 | 1 | 0 | 0.99926 | -0.0050835 | 47.2281
98 | -0.0049787 | -0.0012476 | 0.0049788 | 0.0012476 | 8.8145e-08 | 3.0073e-09 | 0.0075748 | 0.0075748 | 0.0075748 | 0.97802 | -0.15381 | 0.97804 | -0.15369 | 2.8055
99 | 0.0019398 | 0.00048601 | -0.0019397 | -0.00048614 | 6.9513e-08 | -1.3375e-07 | 0.0029513 | 0.0029513 | 0.0029513 | 0.97802 | -0.15381 | 0.97799 | -0.15407 | 1.0931
100 | -0.0080174 | -0.0020092 | 0.0080199 | 0.0020098 | 2.5702e-06 | 6.41e-07 | 0.012198 | 0.012198 | 0.012198 | 0.97804 | -0.15369 | 0.97836 | -0.15137 | 4.5177
101 | -0.011061 | -0.0027721 | 0.011064 | 0.0027728 | 2.4071e-06 | 7.5462e-07 | 0.016823 | 0.016823 | 0.016823 | 0.97836 | -0.15137 | 0.97858 | -0.1498 | 6.2309
102 | 0.038073 | 0.0095631 | -0.038032 | -0.0095479 | 4.0149e-05 | 1.5201e-05 | 0.0579 | 0.0579 | 0.0579 | 0.97858 | -0.1498 | 0.97752 | -0.15739 | 21.4445
103 | -0.049136 | -0.012336 | 0.049209 | 0.012364 | 7.315e-05 | 2.787e-05 | 0.074723 | 0.074723 | 0.074723 | 0.97858 | -0.1498 | 0.98009 | -0.1391 | 27.6753
104 | 0.036123 | 0.0090693 | -0.036107 | -0.0090634 | 1.5532e-05 | 5.8709e-06 | 0.054993 | 0.054993 | 0.054993 | 0.97752 | -0.15739 | 0.97708 | -0.16049 | 20.368
105 | 0.009297 | 0.0023304 | -0.0092907 | -0.0023286 | 6.2797e-06 | 1.7792e-06 | 0.014115 | 0.014116 | 0.014116 | 0.98009 | -0.1391 | 0.9794 | -0.14398 | 5.228
106 | 0.0029914 | 0.00074958 | -0.0029912 | -0.00074967 | 1.6e-07 | -9.4222e-08 | 0.0045481 | 0.0045481 | 0.0045481 | 0.9787 | -0.14898 | 0.97865 | -0.14937 | 1.6845
107 | -0.056155 | -0.01411 | 0.056263 | 0.014151 | 0.00010786 | 4.1185e-05 | 0.085223 | 0.085223 | 0.085223 | 0.98063 | -0.13528 | 0.98257 | -0.1215 | 31.5641
108 | 0.02343 | 0.0058748 | -0.023427 | -0.0058736 | 3.2683e-06 | 1.2044e-06 | 0.035483 | 0.035484 | 0.035484 | 0.98257 | -0.1215 | 0.98243 | -0.12251 | 13.142
109 | 0.020743 | 0.0052011 | -0.020731 | -0.0051966 | 1.2387e-05 | 4.5098e-06 | 0.031419 | 0.031419 | 0.031419 | 0.98243 | -0.12251 | 0.98182 | -0.12682 | 11.6368
110 | 0.001226 | 0.00030726 | -0.001226 | -0.00030727 | 9.41e-10 | -5.1483e-09 | 0.0018592 | 0.0018592 | 0.0018592 | 0.98125 | -0.1309 | 0.98125 | -0.13091 | 0.68859
111 | 0.033484 | 0.0084059 | -0.033477 | -0.0084035 | 6.2026e-06 | 2.3378e-06 | 0.050998 | 0.050998 | 0.050998 | 0.97708 | -0.16049 | 0.9769 | -0.16182 | 18.888
112 | 0.0092907 | 0.0023286 | -0.0092875 | -0.0023277 | 3.2202e-06 | 9.1271e-07 | 0.014116 | 0.014116 | 0.014116 | 0.9794 | -0.14398 | 0.97905 | -0.14648 | 5.228
113 | 0.033477 | 0.0084035 | -0.033454 | -0.0083947 | 2.3434e-05 | 8.8325e-06 | 0.050998 | 0.050998 | 0.050998 | 0.9769 | -0.16182 | 0.97619 | -0.16686 | 18.888
114 | -0.013988 | -0.0035051 | 0.013996 | 0.0035078 | 7.9479e-06 | 2.7108e-06 | 0.021389 | 0.021389 | 0.021389 | 0.9731 | -0.18906 | 0.97367 | -0.18496 | 7.9219
115 | -0.02962 | -0.007424 | 0.029662 | 0.0074398 | 4.2302e-05 | 1.5858e-05 | 0.045267 | 0.045267 | 0.045267 | 0.97367 | -0.18496 | 0.9751 | -0.17466 | 16.7655
116 | 0.015624 | 0.0039161 | -0.015619 | -0.0039144 | 5.024e-06 | 1.7567e-06 | 0.023878 | 0.023878 | 0.023878 | 0.97367 | -0.18496 | 0.97335 | -0.18728 | 8.8437
117 | -0.033418 | -0.0083811 | 0.033454 | 0.0083947 | 3.6139e-05 | 1.3621e-05 | 0.050998 | 0.050998 | 0.050998 | 0.9751 | -0.17466 | 0.97619 | -0.16686 | 18.8881
118 | 0.010165 | 0.0025475 | -0.010163 | -0.0025468 | 2.0109e-06 | 6.076e-07 | 0.01554 | 0.01554 | 0.01554 | 0.97335 | -0.18728 | 0.97315 | -0.18871 | 5.7556
119 | 0.018636 | 0.0046714 | -0.018632 | -0.0046701 | 3.5771e-06 | 1.2879e-06 | 0.028477 | 0.028477 | 0.028477 | 0.97379 | -0.18417 | 0.97359 | -0.18556 | 10.547
120 | -0.0032882 | -0.00082393 | 0.0032883 | 0.00082388 | 1.2991e-07 | -5.2262e-08 | 0.005029 | 0.005029 | 0.005029 | 0.97292 | -0.19041 | 0.97296 | -0.19013 | 1.8626
121 | 0.0039398 | 0.00098713 | -0.0039393 | -0.0009872 | 4.3146e-07 | -7.0747e-08 | 0.0060241 | 0.0060242 | 0.0060242 | 0.97315 | -0.18871 | 0.97304 | -0.1895 | 2.2312
122 | 0.0024137 | 0.00060485 | -0.0024137 | -0.00060492 | 6.7992e-08 | -7.3184e-08 | 0.0036912 | 0.0036912 | 0.0036912 | 0.97304 | -0.1895 | 0.97301 | -0.1897 | 1.3671

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23787 | 0.060016

## res_load
| p_mw | q_mvar
0 | 0.0011299 | 0.00028318
1 | 0.0014115 | 0.00035375
2 | 0.0018394 | 0.000461
3 | 0.0012322 | 0.00030882
4 | 0.0015557 | 0.0003899
5 | 0.0019466 | 0.00048787
6 | 0.0019177 | 0.00048063
7 | 0.0023662 | 0.00059302
8 | 0.0016546 | 0.00041469
9 | 0.001346 | 0.00033734
10 | 0.0013687 | 0.00034302
11 | 0.0013319 | 0.00033382
12 | 0.0025636 | 0.0006425
13 | 0.0016047 | 0.00040218
14 | 0.0015606 | 0.00039111
15 | 0.0012566 | 0.00031493
16 | 0.0029383 | 0.00073641
17 | 0.0024783 | 0.00062111
18 | 0.0023969 | 0.00060071
19 | 0.0032863 | 0.00082363
20 | 0.0074263 | 0.0018612
21 | 0.0022694 | 0.00056876
22 | 0.0032054 | 0.00080334
23 | 0.0018374 | 0.00046051
24 | 0.0016024 | 0.00040159
25 | 0.002275 | 0.00057016
26 | 0.0031993 | 0.00080181
27 | 0.0019359 | 0.00048519
28 | 0.0014366 | 0.00036006
29 | 0.0023844 | 0.00059758
30 | 0.0030729 | 0.00077015
31 | 0.00179 | 0.00044862
32 | 0.0027106 | 0.00067933
33 | 0.0016241 | 0.00040703
34 | 0.0032659 | 0.00081851
35 | 0.0023007 | 0.0005766
36 | 0.0017935 | 0.00044949
37 | 0.0026704 | 0.00066925
38 | 0.0018724 | 0.00046928
39 | 0.0028569 | 0.000716
40 | 0.0023672 | 0.00059326
41 | 0.0022197 | 0.00055631
42 | 0.0012615 | 0.00031617
43 | 0.0015136 | 0.00037936
44 | 0.0012855 | 0.00032217
45 | 0.0020101 | 0.00050377
46 | 0.0025209 | 0.00063179
47 | 0.0015392 | 0.00038575
48 | 0.0039692 | 0.00099476
49 | 0.0031351 | 0.00078573
50 | 0.0031991 | 0.00080177
51 | 0.0023871 | 0.00059827
52 | 0.003108 | 0.00077894
53 | 0.00077901 | 0.00019524
54 | 0.0016188 | 0.00040571
55 | 0.00078177 | 0.00019593
56 | 0.0029374 | 0.00073618
57 | 0.00097034 | 0.00024319
58 | 0.0034046 | 0.00085328
59 | 0.0008133 | 0.00020383
60 | 0.0027877 | 0.00069867
61 | 0.0015276 | 0.00038285
62 | 0.0013102 | 0.00032837
63 | 0.0015514 | 0.00038882
64 | 0.00093938 | 0.00023543
65 | 0.0024572 | 0.00061584
66 | 0.0035725 | 0.00089536
67 | 0.001452 | 0.0003639
68 | 0.0056588 | 0.0014182
69 | 0.0026649 | 0.00066789
70 | 0.0024368 | 0.00061071
71 | 0.0013705 | 0.00034348
72 | 0.0020182 | 0.00050581
73 | 0.0019577 | 0.00049065
74 | 0.0018457 | 0.00046258
75 | 0.0019527 | 0.0004894
76 | 0.0030389 | 0.00076162
77 | 0.0030386 | 0.00076154
78 | 0.0019397 | 0.00048614
79 | 0.0030414 | 0.00076224
80 | 0.0019095 | 0.00047857
81 | 0.0012403 | 0.00031086
82 | 0.0029912 | 0.00074967
83 | 0.0022264 | 0.00055799
84 | 0.0026833 | 0.00067249
85 | 0.001532 | 0.00038394
86 | 0.001226 | 0.00030727
87 | 0.0038531 | 0.00096569
88 | 0.0026238 | 0.00065759
89 | 0.0092875 | 0.0023277
90 | 0.0037556 | 0.00094123
91 | 0.0054541 | 0.0013669
92 | 0.00079775 | 0.00019994
93 | 0.0013157 | 0.00032974
94 | 0.0020266 | 0.00050792
95 | 0.0062234 | 0.0015597
96 | 0.0015256 | 0.00038235
97 | 0.0024137 | 0.00060492
98 | 0.00085477 | 0.00021423
99 | 0.0013201 | 0.00033084

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1