## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2422-22_1_3_node_5 | 0.4 | n |  | TRUE
1 | bus_LV_2422-22_1_3_node_6 | 0.4 | n |  | TRUE
2 | bus_LV_2422-22_1_3_node_8 | 0.4 | n |  | TRUE
3 | bus_LV_2422-22_1_3_node_64 | 0.4 | n |  | TRUE
4 | bus_LV_2422-22_1_3_node_21 | 0.4 | n |  | TRUE
5 | bus_LV_2422-22_1_3_node_85 | 0.4 | n |  | TRUE
6 | bus_LV_2422-22_1_3_node_79 | 0.4 | n |  | TRUE
7 | bus_LV_2422-22_1_3_node_78 | 0.4 | n |  | TRUE
8 | bus_LV_2422-22_1_3_node_41 | 0.4 | n |  | TRUE
9 | bus_LV_2422-22_1_3_node_25 | 0.4 | n |  | TRUE
10 | bus_LV_2422-22_1_3_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_2422-22_1_3_node_23 | 0.4 | n |  | TRUE
12 | bus_LV_2422-22_1_3_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_2422-22_1_3_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_2422-22_1_3_node_35 | 0.4 | n |  | TRUE
15 | bus_LV_2422-22_1_3_node_32 | 0.4 | n |  | TRUE
16 | bus_LV_2422-22_1_3_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_2422-22_1_3_node_28 | 0.4 | n |  | TRUE
18 | bus_LV_2422-22_1_3_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_2422-22_1_3_node_52 | 0.4 | n |  | TRUE
20 | bus_LV_2422-22_1_3_node_53 | 0.4 | n |  | TRUE
21 | bus_LV_2422-22_1_3_node_75 | 0.4 | n |  | TRUE
22 | bus_LV_2422-22_1_3_node_69 | 0.4 | n |  | TRUE
23 | bus_LV_2422-22_1_3_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_2422-22_1_3_node_31 | 0.4 | n |  | TRUE
25 | bus_LV_2422-22_1_3_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_2422-22_1_3_node_34 | 0.4 | n |  | TRUE
27 | bus_LV_2422-22_1_3_node_46 | 0.4 | n |  | TRUE
28 | bus_LV_2422-22_1_3_node_77 | 0.4 | n |  | TRUE
29 | bus_LV_2422-22_1_3_node_76 | 0.4 | n |  | TRUE
30 | bus_LV_2422-22_1_3_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_2422-22_1_3_node_37 | 0.4 | n |  | TRUE
32 | bus_LV_2422-22_1_3_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_2422-22_1_3_node_39 | 0.4 | n |  | TRUE
34 | bus_LV_2422-22_1_3_node_40 | 0.4 | n |  | TRUE
35 | bus_LV_2422-22_1_3_node_66 | 0.4 | n |  | TRUE
36 | bus_LV_2422-22_1_3_node_42 | 0.4 | n |  | TRUE
37 | bus_LV_2422-22_1_3_node_88 | 0.4 | n |  | TRUE
38 | bus_LV_2422-22_1_3_node_67 | 0.4 | n |  | TRUE
39 | bus_LV_2422-22_1_3_node_68 | 0.4 | n |  | TRUE
40 | bus_LV_2422-22_1_3_node_70 | 0.4 | n |  | TRUE
41 | bus_LV_2422-22_1_3_node_71 | 0.4 | n |  | TRUE
42 | bus_LV_2422-22_1_3_node_86 | 0.4 | n |  | TRUE
43 | bus_LV_2422-22_1_3_node_87 | 0.4 | n |  | TRUE
44 | bus_MV_333_0_node_48 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2422-22_1_3_load_5 | 0 | 0.0046218 | 0.0011583 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2422-22_1_3_load_6 | 1 | 0.00088781 | 0.00022251 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2422-22_1_3_load_85 | 5 | 0.0034326 | 0.00086029 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2422-22_1_3_load_78 | 7 | 0.00079211 | 0.00019852 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2422-22_1_3_load_25 | 9 | 0.00048149 | 0.00012067 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2422-22_1_3_load_22 | 10 | 0.00055508 | 0.00013912 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2422-22_1_3_load_23 | 11 | 0.00047922 | 0.0001201 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2422-22_1_3_load_24 | 12 | 0.0010203 | 0.00025572 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2422-22_1_3_load_26 | 13 | 0.017477 | 0.0043802 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2422-22_1_3_load_35 | 14 | 0.0012897 | 0.00032322 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2422-22_1_3_load_27 | 16 | 0.0033916 | 0.00085002 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2422-22_1_3_load_28 | 17 | 0.0033773 | 0.00084644 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2422-22_1_3_load_53 | 20 | 0.0030458 | 0.00076334 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2422-22_1_3_load_75 | 21 | 0.0025207 | 0.00063175 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2422-22_1_3_load_69 | 22 | 0.0033157 | 0.00083099 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2422-22_1_3_load_30 | 23 | 0.00082066 | 0.00020568 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2422-22_1_3_load_31 | 24 | 0.001523 | 0.0003817 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2422-22_1_3_load_33 | 25 | 0.0013129 | 0.00032904 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2422-22_1_3_load_34 | 26 | 0.010229 | 0.0025636 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2422-22_1_3_load_77 | 28 | 0.0044483 | 0.0011149 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2422-22_1_3_load_76 | 29 | 0.0021222 | 0.00053186 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2422-22_1_3_load_36 | 30 | 0.0016928 | 0.00042424 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2422-22_1_3_load_37 | 31 | 0.0026902 | 0.00067423 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2422-22_1_3_load_39 | 33 | 0.0019072 | 0.00047798 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2422-22_1_3_load_40 | 34 | 0.0017089 | 0.00042829 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2422-22_1_3_load_66 | 35 | 0.00059941 | 0.00015023 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2422-22_1_3_load_88 | 37 | 0.020966 | 0.0052546 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2422-22_1_3_load_67 | 38 | 0.0013786 | 0.0003455 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2422-22_1_3_load_70 | 40 | 0.0051045 | 0.0012793 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2422-22_1_3_load_71 | 41 | 0.0022349 | 0.00056012 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2422-22_1_3_load_86 | 42 | 0.0020999 | 0.00052627 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2422-22_1_3_load_87 | 43 | 0.035838 | 0.0089819 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2422-22_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.010566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2422-22_1_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.019874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2422-22_1_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.027161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2422-22_1_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.22525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2422-22_1_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.029773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2422-22_1_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.096717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2422-22_1_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.092916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2422-22_1_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.054966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2422-22_1_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.0095394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2422-22_1_3_line_9 | NAYY 4x150 SE | 8 | 36 | 0.059202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2422-22_1_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.0067786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2422-22_1_3_line_11 | NAYY 4x150 SE | 10 | 11 | 0.033319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_2422-22_1_3_line_12 | NAYY 4x150 SE | 10 | 12 | 0.015911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_2422-22_1_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.0010746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_2422-22_1_3_line_14 | NAYY 4x150 SE | 13 | 14 | 0.016558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_2422-22_1_3_line_15 | NAYY 4x150 SE | 14 | 15 | 0.028493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_2422-22_1_3_line_16 | NAYY 4x150 SE | 15 | 26 | 0.009504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2422-22_1_3_line_17 | NAYY 4x150 SE | 15 | 23 | 0.011305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_2422-22_1_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.029937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2422-22_1_3_line_19 | NAYY 4x150 SE | 17 | 18 | 0.070739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2422-22_1_3_line_20 | NAYY 4x150 SE | 18 | 19 | 0.031995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2422-22_1_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.018421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2422-22_1_3_line_22 | NAYY 4x150 SE | 19 | 21 | 0.020137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2422-22_1_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.032861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2422-22_1_3_line_24 | NAYY 4x150 SE | 21 | 39 | 0.041504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2422-22_1_3_line_25 | NAYY 4x150 SE | 22 | 40 | 0.025089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2422-22_1_3_line_26 | NAYY 4x150 SE | 23 | 24 | 0.0030086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_2422-22_1_3_line_27 | NAYY 4x150 SE | 24 | 25 | 0.014945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_2422-22_1_3_line_28 | NAYY 4x150 SE | 25 | 27 | 0.062318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_2422-22_1_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.038862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2422-22_1_3_line_30 | NAYY 4x150 SE | 27 | 29 | 0.03511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_2422-22_1_3_line_31 | NAYY 4x150 SE | 29 | 39 | 0.017152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_2422-22_1_3_line_32 | NAYY 4x150 SE | 30 | 31 | 0.0016096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2422-22_1_3_line_33 | NAYY 4x150 SE | 30 | 32 | 0.016505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2422-22_1_3_line_34 | NAYY 4x150 SE | 31 | 33 | 0.013534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2422-22_1_3_line_35 | NAYY 4x150 SE | 32 | 34 | 0.039081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2422-22_1_3_line_36 | NAYY 4x150 SE | 34 | 35 | 0.01873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
37 | LV_2422-22_1_3_line_37 | NAYY 4x150 SE | 35 | 38 | 0.024122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
38 | LV_2422-22_1_3_line_38 | NAYY 4x150 SE | 36 | 37 | 0.097082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2422-22_1_3_line_39 | NAYY 4x150 SE | 38 | 39 | 0.014192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
40 | LV_2422-22_1_3_line_40 | NAYY 4x150 SE | 40 | 41 | 0.014813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2422-22_1_3_line_41 | NAYY 4x150 SE | 41 | 42 | 0.017353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2422-22_1_3_line_42 | NAYY 4x150 SE | 42 | 43 | 0.012285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2422-22_1_3_trafo_40 | 0.25 MVA 20/0.4 kV | 44 | 34 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2619479.1227 | 1240477.7259 | 2619479.1227 | 1240477.7259 | 2619469.7487 | 1240472.8513
1 | 2619452.1152 | 1240463.6844 | 2619469.4837 | 1240472.7135 | 2619469.7487 | 1240472.8513
2 | 2619452.1152 | 1240463.6844 | 2619458.9362 | 1240451.8326 | 2619464.0279 | 1240439.3303
3 | 2619465.4011 | 1240315.4018 | 2619461.8848 | 1240322.4613 | 2619450.6007 | 1240337.1559 | 2619432.9021 | 1240359.6232 | 2619435.1181 | 1240364.0777 | 2619429.9771 | 1240370.8318 | 2619421.5971 | 1240371.5049 | 2619420.314 | 1240375.4365 | 2619381.4029 | 1240426.8974 | 2619387.1849 | 1240429.907 | 2619399.0358 | 1240436.0717 | 2619452.1152 | 1240463.6844
4 | 2619464.0279 | 1240439.3303 | 2619482.4776 | 1240415.9632
5 | 2619465.4011 | 1240315.4018 | 2619486.6158 | 1240290.6779 | 2619506.6997 | 1240267.2735 | 2619521.8844 | 1240250.6684 | 2619529.1694 | 1240242.6985
6 | 2619465.4011 | 1240315.4018 | 2619499.3642 | 1240362.1866 | 2619513.3006 | 1240375.6962 | 2619525.7269 | 1240385.2813
7 | 2619566.0368 | 1240201.8384 | 2619529.1694 | 1240242.6985
8 | 2619525.7269 | 1240385.2813 | 2619525.8506 | 1240385.3768 | 2619533.5033 | 1240390.8062
9 | 2619605.5996 | 1240157.7966 | 2619581.5034 | 1240184.7008 | 2619566.0368 | 1240201.8384
10 | 2619533.5033 | 1240390.8062 | 2619539.0318 | 1240394.7285
11 | 2619566.2065 | 1240414.0082 | 2619539.0318 | 1240394.7285
12 | 2619579.1832 | 1240423.2148 | 2619566.2065 | 1240414.0082
13 | 2619579.1832 | 1240423.2148 | 2619580.0596 | 1240423.8366
14 | 2619593.5645 | 1240433.418 | 2619580.0596 | 1240423.8366
15 | 2619616.8029 | 1240449.905 | 2619593.5645 | 1240433.418
16 | 2619616.8029 | 1240449.905 | 2619611.0919 | 1240457.5132
17 | 2619616.8029 | 1240449.905 | 2619623.9935 | 1240441.1818
18 | 2619804.3455 | 1240232.7318 | 2619799.7049 | 1240229.7172 | 2619783.1092 | 1240211.8261
19 | 2619784.1019 | 1240283.1988 | 2619795.4002 | 1240273.5747 | 2619804.9573 | 1240264.612 | 2619813.6098 | 1240254.8347 | 2619817.0286 | 1240249.9764 | 2619817.9451 | 1240247.211 | 2619817.6524 | 1240244.286 | 2619816.3899 | 1240241.947 | 2619814.6508 | 1240239.6843 | 2619809.7172 | 1240236.2212 | 2619804.3455 | 1240232.7318
20 | 2619758.955 | 1240303.0721 | 2619784.1019 | 1240283.1988
21 | 2619784.1019 | 1240283.1988 | 2619772.5189 | 1240268.8755
22 | 2619758.955 | 1240303.0721 | 2619743.1593 | 1240315.5611
23 | 2619751.8557 | 1240243.3239 | 2619772.5189 | 1240268.8755
24 | 2619710.6026 | 1240341.3024 | 2619743.1593 | 1240315.5611
25 | 2619751.8557 | 1240243.3239 | 2619736.0797 | 1240223.8156
26 | 2619623.9935 | 1240441.1818 | 2619625.9071 | 1240438.8602
27 | 2619635.4129 | 1240427.3284 | 2619625.9071 | 1240438.8602
28 | 2619673.0995 | 1240377.7011 | 2619638.0439 | 1240424.1367 | 2619635.4129 | 1240427.3284
29 | 2619673.0995 | 1240377.7011 | 2619644.8305 | 1240351.0349
30 | 2619673.0995 | 1240377.7011 | 2619698.2941 | 1240353.2484
31 | 2619710.6026 | 1240341.3024 | 2619698.2941 | 1240353.2484
32 | 2619663.4406 | 1240255.615 | 2619662.1982 | 1240256.6383
33 | 2619649.4579 | 1240267.1317 | 2619662.1982 | 1240256.6383
34 | 2619673.887 | 1240247.0109 | 2619663.4406 | 1240255.615
35 | 2619649.4579 | 1240267.1317 | 2619674.3175 | 1240297.2873
36 | 2619686.2315 | 1240311.7394 | 2619674.3175 | 1240297.2873
37 | 2619686.2315 | 1240311.7394 | 2619701.5753 | 1240330.3521
38 | 2619605.5996 | 1240157.7966 | 2619649.7989 | 1240131.8038 | 2619656.6406 | 1240129.9697 | 2619662.0121 | 1240131.3994 | 2619676.955 | 1240151.5725 | 2619681.901 | 1240158.1597
39 | 2619710.6026 | 1240341.3024 | 2619701.5753 | 1240330.3521
40 | 2619736.0797 | 1240223.8156 | 2619726.7652 | 1240212.2975
41 | 2619726.7652 | 1240212.2975 | 2619726.7652 | 1240212.2975 | 2619735.0528 | 1240205.3429 | 2619731.1138 | 1240200.1301
42 | 2619723.7076 | 1240190.3292 | 2619731.1138 | 1240200.1301

## bus_geodata
| x | y | coords
0 | 2619479.1227 | 1240477.7259
1 | 2619469.7487 | 1240472.8513
2 | 2619452.1152 | 1240463.6844
3 | 2619464.0279 | 1240439.3303
4 | 2619465.4011 | 1240315.4018
5 | 2619482.4777 | 1240415.9632
6 | 2619529.1694 | 1240242.6985
7 | 2619525.7269 | 1240385.2813
8 | 2619566.0368 | 1240201.8384
9 | 2619533.5033 | 1240390.8062
10 | 2619566.2065 | 1240414.0082
11 | 2619539.0318 | 1240394.7285
12 | 2619579.1832 | 1240423.2148
13 | 2619580.0596 | 1240423.8366
14 | 2619593.5645 | 1240433.418
15 | 2619616.8029 | 1240449.905
16 | 2619783.1092 | 1240211.8261
17 | 2619804.3455 | 1240232.7318
18 | 2619784.1019 | 1240283.1988
19 | 2619758.955 | 1240303.0721
20 | 2619772.5189 | 1240268.8755
21 | 2619743.1593 | 1240315.5611
22 | 2619751.8557 | 1240243.3239
23 | 2619623.9935 | 1240441.1818
24 | 2619625.9071 | 1240438.8602
25 | 2619635.4129 | 1240427.3284
26 | 2619611.0919 | 1240457.5132
27 | 2619673.0995 | 1240377.7011
28 | 2619644.8305 | 1240351.0349
29 | 2619698.2941 | 1240353.2484
30 | 2619662.1982 | 1240256.6383
31 | 2619663.4406 | 1240255.615
32 | 2619649.4579 | 1240267.1317
33 | 2619673.887 | 1240247.0109
34 | 2619674.3175 | 1240297.2873
35 | 2619686.2315 | 1240311.7394
36 | 2619605.5996 | 1240157.7966
37 | 2619681.901 | 1240158.1597
38 | 2619701.5753 | 1240330.3521
39 | 2619710.6026 | 1240341.3024
40 | 2619736.0797 | 1240223.8156
41 | 2619726.7652 | 1240212.2975
42 | 2619731.1138 | 1240200.1301
43 | 2619723.7076 | 1240190.3292
44 | 2619649.4579 | 1240267.1317

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97653 | -0.16477 | 0.0046218 | 0.0011583
1 | 0.9766 | -0.16426 | 0.00088781 | 0.00022251
2 | 0.97676 | -0.16311 | 0 | 0
3 | 0.97663 | -0.16409 | 0 | 0
4 | 0.9797 | -0.14206 | 0 | 0
5 | 0.97648 | -0.16516 | 0.0034326 | 0.00086029
6 | 0.97672 | -0.16324 | 0 | 0
7 | 0.98378 | -0.11323 | 0.00079211 | 0.00019852
8 | 0.97503 | -0.17532 | 0 | 0
9 | 0.98421 | -0.1102 | 0.00048149 | 0.00012067
10 | 0.98529 | -0.10258 | 0.00055508 | 0.00013912
11 | 0.98452 | -0.10802 | 0.00047922 | 0.0001201
12 | 0.98566 | -0.09994 | 0.0010203 | 0.00025572
13 | 0.98569 | -0.099756 | 0.017477 | 0.0043802
14 | 0.9863 | -0.095439 | 0.0012897 | 0.00032322
15 | 0.98738 | -0.087834 | 0 | 0
16 | 0.98548 | -0.10128 | 0.0033916 | 0.00085002
17 | 0.98562 | -0.10024 | 0.0033773 | 0.00084644
18 | 0.98632 | -0.095319 | 0 | 0
19 | 0.98903 | -0.076192 | 0 | 0
20 | 0.98493 | -0.10509 | 0.0030458 | 0.00076334
21 | 0.99074 | -0.064208 | 0.0025207 | 0.00063175
22 | 0.98261 | -0.12156 | 0.0033157 | 0.00083099
23 | 0.98789 | -0.08423 | 0.00082066 | 0.00020568
24 | 0.98803 | -0.083259 | 0.001523 | 0.0003817
25 | 0.98873 | -0.078322 | 0.0013129 | 0.00032904
26 | 0.98724 | -0.08883 | 0.010229 | 0.0025636
27 | 0.99172 | -0.057394 | 0 | 0
28 | 0.99147 | -0.05915 | 0.0044483 | 0.0011149
29 | 0.99352 | -0.044867 | 0.0021222 | 0.00053186
30 | 0.9995 | -0.0034937 | 0.0016928 | 0.00042424
31 | 0.99949 | -0.0035676 | 0.0026902 | 0.00067423
32 | 0.99965 | -0.0024562 | 0 | 0
33 | 0.99945 | -0.0038256 | 0.0019072 | 0.00047798
34 | 1 | 0 | -0.145 | -0.036459
35 | 0.99816 | -0.01269 | 0.00059941 | 0.00015023
36 | 0.97321 | -0.18839 | 0 | 0
37 | 0.97022 | -0.2099 | 0.020966 | 0.0052546
38 | 0.9958 | -0.029029 | 0.0013786 | 0.0003455
39 | 0.99442 | -0.03858 | 0 | 0
40 | 0.98095 | -0.13333 | 0.0051045 | 0.0012793
41 | 0.98009 | -0.1395 | 0.0022349 | 0.00056012
42 | 0.97913 | -0.14635 | 0.0020999 | 0.00052627
43 | 0.97849 | -0.15094 | 0.035838 | 0.0089819
44 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0046218 | -0.0011583 | 0.0046222 | 0.0011583 | 3.27e-07 | -6.4235e-09 | 0.0070427 | 0.0070426 | 0.0070427 | 0.97653 | -0.16477 | 0.9766 | -0.16426 | 2.6084
1 | -0.00551 | -0.0013808 | 0.0055109 | 0.0013809 | 8.7406e-07 | 8.7461e-08 | 0.0083953 | 0.0083952 | 0.0083953 | 0.9766 | -0.16426 | 0.97676 | -0.16311 | 3.1094
2 | 0.0034336 | 0.00085995 | -0.0034331 | -0.00086011 | 4.637e-07 | -1.6157e-07 | 0.0052305 | 0.0052307 | 0.0052307 | 0.97676 | -0.16311 | 0.97663 | -0.16409 | 1.9373
3 | -0.0089444 | -0.0022409 | 0.0089705 | 0.0022481 | 2.6094e-05 | 7.2081e-06 | 0.013626 | 0.013625 | 0.013626 | 0.97676 | -0.16311 | 0.9797 | -0.14206 | 5.0466
4 | 0.0034331 | 0.00086011 | -0.0034326 | -0.00086029 | 5.0831e-07 | -1.7699e-07 | 0.0052307 | 0.0052308 | 0.0052308 | 0.97663 | -0.16409 | 0.97648 | -0.16516 | 1.9373
5 | 0.021165 | 0.0053272 | -0.021102 | -0.0053044 | 6.2398e-05 | 2.2785e-05 | 0.032154 | 0.032155 | 0.032155 | 0.9797 | -0.14206 | 0.97672 | -0.16324 | 11.9091
6 | -0.030135 | -0.0075752 | 0.030257 | 0.0076208 | 0.00012151 | 4.5558e-05 | 0.045779 | 0.045778 | 0.045779 | 0.9797 | -0.14206 | 0.98378 | -0.11323 | 16.9551
7 | 0.021102 | 0.0053044 | -0.021067 | -0.0052914 | 3.5462e-05 | 1.2953e-05 | 0.032155 | 0.032155 | 0.032155 | 0.97672 | -0.16324 | 0.97503 | -0.17532 | 11.9092
8 | -0.031049 | -0.0078193 | 0.031062 | 0.0078243 | 1.3136e-05 | 4.9312e-06 | 0.046977 | 0.046976 | 0.046977 | 0.98378 | -0.11323 | 0.98421 | -0.1102 | 17.3987
9 | 0.021067 | 0.0052914 | -0.021029 | -0.0052775 | 3.8196e-05 | 1.3954e-05 | 0.032155 | 0.032155 | 0.032155 | 0.97503 | -0.17532 | 0.97321 | -0.18839 | 11.9093
10 | -0.031543 | -0.0079449 | 0.031553 | 0.0079485 | 9.6259e-06 | 3.6161e-06 | 0.047704 | 0.047704 | 0.047704 | 0.98421 | -0.1102 | 0.98452 | -0.10802 | 17.6683
11 | 0.032057 | 0.0080772 | -0.032032 | -0.0080686 | 2.4381e-05 | 8.5293e-06 | 0.048428 | 0.048429 | 0.048429 | 0.98529 | -0.10258 | 0.98452 | -0.10802 | 8.9683
12 | -0.032612 | -0.0082163 | 0.032624 | 0.0082205 | 1.2049e-05 | 4.2288e-06 | 0.049267 | 0.049267 | 0.049267 | 0.98529 | -0.10258 | 0.98566 | -0.09994 | 9.1235
13 | -0.033644 | -0.0084762 | 0.033645 | 0.0084765 | 8.6549e-07 | 3.0549e-07 | 0.050807 | 0.050807 | 0.050807 | 0.98566 | -0.09994 | 0.98569 | -0.099756 | 9.4087
14 | -0.051122 | -0.012857 | 0.051153 | 0.012868 | 3.0782e-05 | 1.1417e-05 | 0.077191 | 0.07719 | 0.077191 | 0.98569 | -0.099756 | 0.9863 | -0.095439 | 14.2946
15 | -0.052443 | -0.013191 | 0.052498 | 0.013212 | 5.5672e-05 | 2.0684e-05 | 0.079136 | 0.079136 | 0.079136 | 0.9863 | -0.095439 | 0.98738 | -0.087834 | 14.6548
16 | 0.01023 | 0.002564 | -0.010229 | -0.0025636 | 1.4097e-06 | 4.2064e-07 | 0.015417 | 0.015417 | 0.015417 | 0.98738 | -0.087834 | 0.98724 | -0.08883 | 5.7102
17 | -0.062729 | -0.015776 | 0.06276 | 0.015788 | 3.1533e-05 | 1.1839e-05 | 0.094553 | 0.094553 | 0.094553 | 0.98738 | -0.087834 | 0.98789 | -0.08423 | 17.5099
18 | -0.0033916 | -0.00085002 | 0.0033921 | 0.00084982 | 4.8991e-07 | -1.9306e-07 | 0.0051211 | 0.005121 | 0.0051211 | 0.98548 | -0.10128 | 0.98562 | -0.10024 | 1.8967
19 | -0.0067694 | -0.0016963 | 0.006774 | 0.0016971 | 4.6102e-06 | 8.7095e-07 | 0.01022 | 0.01022 | 0.01022 | 0.98562 | -0.10024 | 0.98632 | -0.095319 | 3.7851
20 | -0.058763 | -0.014772 | 0.05892 | 0.014832 | 0.00015697 | 5.9963e-05 | 0.088669 | 0.088669 | 0.088669 | 0.98632 | -0.095319 | 0.98903 | -0.076192 | 32.8405
21 | 0.051989 | 0.013075 | -0.051918 | -0.013048 | 7.0742e-05 | 2.6974e-05 | 0.07845 | 0.07845 | 0.07845 | 0.98632 | -0.095319 | 0.98493 | -0.10509 | 29.0556
22 | -0.05892 | -0.014832 | 0.059019 | 0.01487 | 9.8791e-05 | 3.7738e-05 | 0.088669 | 0.088669 | 0.088669 | 0.98903 | -0.076192 | 0.99074 | -0.064208 | 32.8405
23 | 0.048873 | 0.012285 | -0.048761 | -0.012242 | 0.00011183 | 4.2594e-05 | 0.073849 | 0.073849 | 0.073849 | 0.98493 | -0.10509 | 0.98261 | -0.12156 | 27.3514
24 | -0.06154 | -0.015502 | 0.061761 | 0.015586 | 0.00022138 | 8.4609e-05 | 0.092455 | 0.092455 | 0.092455 | 0.99074 | -0.064208 | 0.99442 | -0.03858 | 34.2427
25 | 0.045445 | 0.011411 | -0.045371 | -0.011383 | 7.4164e-05 | 2.8207e-05 | 0.068828 | 0.068828 | 0.068828 | 0.98261 | -0.12156 | 0.98095 | -0.13333 | 25.4918
26 | -0.063581 | -0.015994 | 0.063589 | 0.015997 | 8.613e-06 | 3.2357e-06 | 0.095789 | 0.095789 | 0.095789 | 0.98789 | -0.08423 | 0.98803 | -0.083259 | 17.7388
27 | -0.065112 | -0.016379 | 0.065157 | 0.016395 | 4.4857e-05 | 1.687e-05 | 0.098083 | 0.098083 | 0.098083 | 0.98803 | -0.083259 | 0.98873 | -0.078322 | 18.1635
28 | -0.06647 | -0.016724 | 0.066665 | 0.016798 | 0.00019466 | 7.3266e-05 | 0.10006 | 0.10006 | 0.10006 | 0.98873 | -0.078322 | 0.99172 | -0.057394 | 18.5294
29 | 0.0044494 | 0.0011148 | -0.0044483 | -0.0011149 | 1.0808e-06 | -8.5621e-08 | 0.0066759 | 0.0066761 | 0.0066761 | 0.99172 | -0.057394 | 0.99147 | -0.05915 | 2.4726
30 | -0.071114 | -0.017912 | 0.071239 | 0.01796 | 0.00012479 | 4.7089e-05 | 0.10673 | 0.10673 | 0.10673 | 0.99172 | -0.057394 | 0.99352 | -0.044867 | 19.7656
31 | -0.073361 | -0.018491 | 0.073426 | 0.018516 | 6.465e-05 | 2.4421e-05 | 0.10991 | 0.10991 | 0.10991 | 0.99352 | -0.044867 | 0.99442 | -0.03858 | 20.3541
32 | 0.0045975 | 0.0011521 | -0.0045974 | -0.0011521 | 4.7052e-08 | -2.9984e-09 | 0.0068445 | 0.0068445 | 0.0068445 | 0.9995 | -0.0034937 | 0.99949 | -0.0035676 | 2.535
33 | -0.0062902 | -0.0015763 | 0.0062911 | 0.0015764 | 9.032e-07 | 1.3103e-07 | 0.0093646 | 0.0093645 | 0.0093646 | 0.9995 | -0.0034937 | 0.99965 | -0.0024562 | 3.4684
34 | 0.0019072 | 0.00047783 | -0.0019072 | -0.00047798 | 6.8084e-08 | -1.5118e-07 | 0.0028394 | 0.0028394 | 0.0028394 | 0.99949 | -0.0035676 | 0.99945 | -0.0038256 | 1.0516
35 | -0.0062911 | -0.0015764 | 0.0062933 | 0.0015767 | 2.1385e-06 | 3.0997e-07 | 0.0093645 | 0.0093643 | 0.0093645 | 0.99965 | -0.0024562 | 1 | 0 | 3.4683
36 | 0.13791 | 0.034882 | -0.13766 | -0.034788 | 0.00024635 | 9.426e-05 | 0.20532 | 0.20532 | 0.20532 | 1 | 0 | 0.99816 | -0.01269 | 38.0223
37 | 0.13706 | 0.034637 | -0.13675 | -0.034517 | 0.00031451 | 0.00012034 | 0.20443 | 0.20443 | 0.20443 | 0.99816 | -0.01269 | 0.9958 | -0.029029 | 37.8568
38 | 0.021029 | 0.0052775 | -0.020966 | -0.0052546 | 6.2636e-05 | 2.2888e-05 | 0.032155 | 0.032155 | 0.032155 | 0.97321 | -0.18839 | 0.97022 | -0.2099 | 11.9094
39 | 0.13537 | 0.034171 | -0.13519 | -0.034102 | 0.00018133 | 6.9373e-05 | 0.20237 | 0.20237 | 0.20237 | 0.9958 | -0.029029 | 0.99442 | -0.03858 | 37.4754
40 | 0.040266 | 0.010104 | -0.040232 | -0.010091 | 3.449e-05 | 1.3079e-05 | 0.061085 | 0.061085 | 0.061085 | 0.98095 | -0.13333 | 0.98009 | -0.1395 | 22.624
41 | 0.037997 | 0.0095305 | -0.037961 | -0.0095168 | 3.604e-05 | 1.3643e-05 | 0.057692 | 0.057692 | 0.057692 | 0.98009 | -0.1395 | 0.97913 | -0.14635 | 21.3673
42 | 0.035861 | 0.0089905 | -0.035838 | -0.0089819 | 2.2769e-05 | 8.6029e-06 | 0.054501 | 0.054501 | 0.054501 | 0.97913 | -0.14635 | 0.97849 | -0.15094 | 20.1854

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.14671 | 0.036887

## res_load
| p_mw | q_mvar
0 | 0.0046218 | 0.0011583
1 | 0.00088781 | 0.00022251
2 | 0.0034326 | 0.00086029
3 | 0.00079211 | 0.00019852
4 | 0.00048149 | 0.00012067
5 | 0.00055508 | 0.00013912
6 | 0.00047922 | 0.0001201
7 | 0.0010203 | 0.00025572
8 | 0.017477 | 0.0043802
9 | 0.0012897 | 0.00032322
10 | 0.0033916 | 0.00085002
11 | 0.0033773 | 0.00084644
12 | 0.0030458 | 0.00076334
13 | 0.0025207 | 0.00063175
14 | 0.0033157 | 0.00083099
15 | 0.00082066 | 0.00020568
16 | 0.001523 | 0.0003817
17 | 0.0013129 | 0.00032904
18 | 0.010229 | 0.0025636
19 | 0.0044483 | 0.0011149
20 | 0.0021222 | 0.00053186
21 | 0.0016928 | 0.00042424
22 | 0.0026902 | 0.00067423
23 | 0.0019072 | 0.00047798
24 | 0.0017089 | 0.00042829
25 | 0.00059941 | 0.00015023
26 | 0.020966 | 0.0052546
27 | 0.0013786 | 0.0003455
28 | 0.0051045 | 0.0012793
29 | 0.0022349 | 0.00056012
30 | 0.0020999 | 0.00052627
31 | 0.035838 | 0.0089819

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1