## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2422-25_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2422-25_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2422-25_0_3_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_2422-25_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2422-25_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2422-25_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2422-25_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2422-25_0_3_node_65 | 0.4 | n |  | TRUE
8 | bus_LV_2422-25_0_3_node_77 | 0.4 | n |  | TRUE
9 | bus_LV_2422-25_0_3_node_16 | 0.4 | n |  | TRUE
10 | bus_LV_2422-25_0_3_node_24 | 0.4 | n |  | TRUE
11 | bus_LV_2422-25_0_3_node_51 | 0.4 | n |  | TRUE
12 | bus_LV_2422-25_0_3_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_2422-25_0_3_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_2422-25_0_3_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_2422-25_0_3_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_2422-25_0_3_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_2422-25_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2422-25_0_3_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2422-25_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2422-25_0_3_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_2422-25_0_3_node_52 | 0.4 | n |  | TRUE
22 | bus_LV_2422-25_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2422-25_0_3_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_2422-25_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_2422-25_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_2422-25_0_3_node_35 | 0.4 | n |  | TRUE
27 | bus_LV_2422-25_0_3_node_66 | 0.4 | n |  | TRUE
28 | bus_LV_2422-25_0_3_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_2422-25_0_3_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_2422-25_0_3_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_2422-25_0_3_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_2422-25_0_3_node_34 | 0.4 | n |  | TRUE
33 | bus_LV_2422-25_0_3_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_2422-25_0_3_node_88 | 0.4 | n |  | TRUE
35 | bus_LV_2422-25_0_3_node_76 | 0.4 | n |  | TRUE
36 | bus_LV_2422-25_0_3_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_2422-25_0_3_node_86 | 0.4 | n |  | TRUE
38 | bus_LV_2422-25_0_3_node_57 | 0.4 | n |  | TRUE
39 | bus_LV_2422-25_0_3_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_2422-25_0_3_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_2422-25_0_3_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_2422-25_0_3_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_2422-25_0_3_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_2422-25_0_3_node_53 | 0.4 | n |  | TRUE
45 | bus_LV_2422-25_0_3_node_55 | 0.4 | n |  | TRUE
46 | bus_LV_2422-25_0_3_node_64 | 0.4 | n |  | TRUE
47 | bus_LV_2422-25_0_3_node_56 | 0.4 | n |  | TRUE
48 | bus_LV_2422-25_0_3_node_49 | 0.4 | n |  | TRUE
49 | bus_LV_2422-25_0_3_node_75 | 0.4 | n |  | TRUE
50 | bus_LV_2422-25_0_3_node_73 | 0.4 | n |  | TRUE
51 | bus_LV_2422-25_0_3_node_59 | 0.4 | n |  | TRUE
52 | bus_LV_2422-25_0_3_node_71 | 0.4 | n |  | TRUE
53 | bus_LV_2422-25_0_3_node_89 | 0.4 | n |  | TRUE
54 | bus_LV_2422-25_0_3_node_72 | 0.4 | n |  | TRUE
55 | bus_LV_2422-25_0_3_node_74 | 0.4 | n |  | TRUE
56 | bus_LV_2422-25_0_3_node_90 | 0.4 | n |  | TRUE
57 | bus_LV_2422-25_0_3_node_85 | 0.4 | n |  | TRUE
58 | bus_MV_333_0_node_177 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2422-25_0_3_load_0 | 0 | 0.0019934 | 0.00049959 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2422-25_0_3_load_3 | 3 | 0.0023689 | 0.00059369 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2422-25_0_3_load_5 | 5 | 0.0019116 | 0.00047909 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2422-25_0_3_load_6 | 6 | 0.001892 | 0.00047417 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2422-25_0_3_load_65 | 7 | 0.0015073 | 0.00037778 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2422-25_0_3_load_77 | 8 | 0.00089848 | 0.00022518 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2422-25_0_3_load_16 | 9 | 0.001128 | 0.00028271 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2422-25_0_3_load_24 | 10 | 0.0026474 | 0.0006635 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2422-25_0_3_load_51 | 11 | 0.0018969 | 0.00047541 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2422-25_0_3_load_12 | 12 | 0.0010768 | 0.00026988 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2422-25_0_3_load_14 | 13 | 0.0014329 | 0.00035913 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2422-25_0_3_load_33 | 15 | 0.0019506 | 0.00048888 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2422-25_0_3_load_8 | 16 | 0.0011392 | 0.00028551 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2422-25_0_3_load_9 | 17 | 0.00091756 | 0.00022996 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2422-25_0_3_load_10 | 18 | 0.00089941 | 0.00022541 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2422-25_0_3_load_11 | 19 | 0.00087866 | 0.00022021 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2422-25_0_3_load_25 | 20 | 0.0014266 | 0.00035753 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2422-25_0_3_load_52 | 21 | 0.0015344 | 0.00038454 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2422-25_0_3_load_13 | 22 | 0.0011623 | 0.0002913 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2422-25_0_3_load_15 | 23 | 0.0010991 | 0.00027545 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2422-25_0_3_load_17 | 24 | 0.00091553 | 0.00022945 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2422-25_0_3_load_18 | 25 | 0.00156 | 0.00039097 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2422-25_0_3_load_35 | 26 | 0.00094225 | 0.00023615 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2422-25_0_3_load_66 | 27 | 0.0011065 | 0.00027732 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2422-25_0_3_load_19 | 28 | 0.0015409 | 0.0003862 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2422-25_0_3_load_20 | 29 | 0.0020049 | 0.00050246 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2422-25_0_3_load_23 | 31 | 0.0017855 | 0.00044748 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2422-25_0_3_load_34 | 32 | 0.00091129 | 0.00022839 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2422-25_0_3_load_31 | 33 | 0.0017855 | 0.00044748 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2422-25_0_3_load_88 | 34 | 0.0026086 | 0.00065379 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2422-25_0_3_load_76 | 35 | 0.0049949 | 0.0012518 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2422-25_0_3_load_32 | 36 | 0.0017797 | 0.00044604 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2422-25_0_3_load_57 | 38 | 0.0010934 | 0.00027404 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2422-25_0_3_load_36 | 39 | 0.0021492 | 0.00053863 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2422-25_0_3_load_37 | 40 | 0.0018042 | 0.00045217 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2422-25_0_3_load_38 | 41 | 0.0020355 | 0.00051015 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2422-25_0_3_load_39 | 42 | 0.0015316 | 0.00038385 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2422-25_0_3_load_53 | 44 | 0.0016985 | 0.00042568 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2422-25_0_3_load_55 | 45 | 0.0027781 | 0.00069627 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2422-25_0_3_load_49 | 48 | 0.0025473 | 0.00063842 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2422-25_0_3_load_75 | 49 | 0.00165 | 0.00041353 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2422-25_0_3_load_73 | 50 | 0.0033587 | 0.00084176 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2422-25_0_3_load_59 | 51 | 0.0026956 | 0.00067558 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2422-25_0_3_load_71 | 52 | 0.0014956 | 0.00037484 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2422-25_0_3_load_89 | 53 | 0.0010918 | 0.00027363 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2422-25_0_3_load_72 | 54 | 0.0012103 | 0.00030332 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2422-25_0_3_load_90 | 56 | 0.0028888 | 0.000724 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2422-25_0_3_load_85 | 57 | 0.0014682 | 0.00036796 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2422-25_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.005705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2422-25_0_3_line_1 | NAYY 4x150 SE | 1 | 6 | 0.012153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2422-25_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.032045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2422-25_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.02378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2422-25_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.026937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2422-25_0_3_line_5 | NAYY 4x150 SE | 3 | 7 | 0.023257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2422-25_0_3_line_6 | NAYY 4x150 SE | 4 | 8 | 0.010529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2422-25_0_3_line_7 | NAYY 4x150 SE | 4 | 9 | 0.0089367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2422-25_0_3_line_8 | NAYY 4x150 SE | 5 | 10 | 0.023911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2422-25_0_3_line_9 | NAYY 4x150 SE | 6 | 11 | 0.0016232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2422-25_0_3_line_10 | NAYY 4x150 SE | 8 | 12 | 0.0009557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2422-25_0_3_line_11 | NAYY 4x150 SE | 9 | 13 | 0.0016277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2422-25_0_3_line_12 | NAYY 4x150 SE | 10 | 14 | 0.02165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2422-25_0_3_line_13 | NAYY 4x150 SE | 11 | 15 | 0.019275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2422-25_0_3_line_14 | NAYY 4x150 SE | 12 | 18 | 0.0058879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2422-25_0_3_line_15 | NAYY 4x150 SE | 13 | 22 | 0.020034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2422-25_0_3_line_16 | NAYY 4x150 SE | 14 | 31 | 0.023261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2422-25_0_3_line_17 | NAYY 4x150 SE | 14 | 28 | 0.029531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2422-25_0_3_line_18 | NAYY 4x150 SE | 15 | 36 | 0.0031014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2422-25_0_3_line_19 | NAYY 4x150 SE | 16 | 17 | 0.0083428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2422-25_0_3_line_20 | NAYY 4x150 SE | 16 | 18 | 0.011429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2422-25_0_3_line_21 | NAYY 4x150 SE | 17 | 19 | 0.0068459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2422-25_0_3_line_22 | NAYY 4x150 SE | 19 | 20 | 0.0036298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2422-25_0_3_line_23 | NAYY 4x150 SE | 20 | 21 | 0.016082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2422-25_0_3_line_24 | NAYY 4x150 SE | 22 | 23 | 0.0043382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2422-25_0_3_line_25 | NAYY 4x150 SE | 23 | 24 | 0.015787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2422-25_0_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.0087142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2422-25_0_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.012193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2422-25_0_3_line_28 | NAYY 4x150 SE | 26 | 27 | 0.015485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2422-25_0_3_line_29 | NAYY 4x150 SE | 27 | 38 | 0.0087618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2422-25_0_3_line_30 | NAYY 4x150 SE | 28 | 29 | 0.0063491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2422-25_0_3_line_31 | NAYY 4x150 SE | 29 | 30 | 0.025739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2422-25_0_3_line_32 | NAYY 4x150 SE | 30 | 32 | 0.011788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2422-25_0_3_line_33 | NAYY 4x150 SE | 30 | 33 | 0.011713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2422-25_0_3_line_34 | NAYY 4x150 SE | 32 | 34 | 0.021575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2422-25_0_3_line_35 | NAYY 4x150 SE | 32 | 35 | 0.050758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2422-25_0_3_line_36 | NAYY 4x150 SE | 33 | 36 | 0.016062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2422-25_0_3_line_37 | NAYY 4x150 SE | 34 | 37 | 0.024488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2422-25_0_3_line_38 | NAYY 4x150 SE | 35 | 49 | 0.026302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2422-25_0_3_line_39 | NAYY 4x150 SE | 37 | 53 | 0.020008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2422-25_0_3_line_40 | NAYY 4x150 SE | 37 | 57 | 0.0012622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2422-25_0_3_line_41 | NAYY 4x150 SE | 38 | 43 | 0.015312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2422-25_0_3_line_42 | NAYY 4x150 SE | 39 | 40 | 0.0016716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2422-25_0_3_line_43 | NAYY 4x150 SE | 39 | 41 | 0.011875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2422-25_0_3_line_44 | NAYY 4x150 SE | 40 | 42 | 0.019232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2422-25_0_3_line_45 | NAYY 4x150 SE | 41 | 43 | 0.0044852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2422-25_0_3_line_46 | NAYY 4x150 SE | 42 | 44 | 0.011647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2422-25_0_3_line_47 | NAYY 4x150 SE | 43 | 45 | 0.008536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2422-25_0_3_line_48 | NAYY 4x150 SE | 44 | 46 | 0.022512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2422-25_0_3_line_49 | NAYY 4x150 SE | 45 | 47 | 0.016763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2422-25_0_3_line_50 | NAYY 4x150 SE | 46 | 50 | 0.032342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2422-25_0_3_line_51 | NAYY 4x150 SE | 47 | 51 | 0.019167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2422-25_0_3_line_52 | NAYY 4x150 SE | 48 | 49 | 0.001774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2422-25_0_3_line_53 | NAYY 4x150 SE | 50 | 52 | 0.04436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2422-25_0_3_line_54 | NAYY 4x150 SE | 52 | 54 | 0.0015281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2422-25_0_3_line_55 | NAYY 4x150 SE | 54 | 55 | 0.007618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2422-25_0_3_line_56 | NAYY 4x150 SE | 55 | 56 | 0.036246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2422-25_0_3_trafo_1 | 0.25 MVA 20/0.4 kV | 58 | 2 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2
0 | 2619067.101 | 1240566.6034 | 2619062.7503 | 1240570.2937
1 | 2619067.101 | 1240566.6034 | 2619075.5421 | 1240575.3471
2 | 2619036.1002 | 1240592.8984 | 2619020.0066 | 1240565.1879
3 | 2619015.3986 | 1240604.7063 | 2619036.1002 | 1240592.8984
4 | 2619036.1002 | 1240592.8984 | 2619048.3984 | 1240616.8646
5 | 2619008.3266 | 1240545.0769 | 2619020.0066 | 1240565.1879
6 | 2619015.3986 | 1240604.7063 | 2619020.2825 | 1240614.0345
7 | 2619015.3986 | 1240604.7063 | 2619010.8094 | 1240597.038
8 | 2619059.3151 | 1240638.1385 | 2619048.3984 | 1240616.8646
9 | 2619075.5421 | 1240575.3471 | 2619076.6695 | 1240576.515
10 | 2619020.7258 | 1240614.8812 | 2619020.2825 | 1240614.0345
11 | 2619009.9735 | 1240595.6413 | 2619010.8094 | 1240597.038
12 | 2619069.1993 | 1240657.4002 | 2619059.3151 | 1240638.1385
13 | 2619090.0569 | 1240590.3824 | 2619076.6695 | 1240576.515
14 | 2619020.7258 | 1240614.8812 | 2619023.4568 | 1240620.0974
15 | 2618999.6854 | 1240578.4504 | 2619009.9735 | 1240595.6413
16 | 2619069.1993 | 1240657.4002 | 2619081.7671 | 1240676.9733
17 | 2619069.1993 | 1240657.4002 | 2619089.4728 | 1240635.9283
18 | 2619092.2109 | 1240592.6136 | 2619090.0569 | 1240590.3824
19 | 2619028.7582 | 1240630.2228 | 2619032.6279 | 1240637.6139
20 | 2619028.7582 | 1240630.2228 | 2619023.4568 | 1240620.0974
21 | 2619035.8034 | 1240643.6788 | 2619032.6279 | 1240637.6139
22 | 2619035.8034 | 1240643.6788 | 2619037.487 | 1240646.8945
23 | 2619037.487 | 1240646.8945 | 2619044.9466 | 1240661.1422
24 | 2618999.6854 | 1240578.4504 | 2618997.4577 | 1240574.7279
25 | 2618989.3505 | 1240561.1813 | 2618997.4577 | 1240574.7279
26 | 2618989.3505 | 1240561.1813 | 2618984.8756 | 1240553.7039
27 | 2618984.8756 | 1240553.7039 | 2618978.6143 | 1240543.2416
28 | 2618978.6143 | 1240543.2416 | 2618970.6625 | 1240529.9546
29 | 2618966.1631 | 1240522.4363 | 2618970.6625 | 1240529.9546
30 | 2619093.8317 | 1240631.3119 | 2619089.4728 | 1240635.9283
31 | 2619111.5023 | 1240612.5967 | 2619093.8317 | 1240631.3119
32 | 2619111.5023 | 1240612.5967 | 2619120.263 | 1240620.4837
33 | 2619111.5023 | 1240612.5967 | 2619103.3668 | 1240604.1695
34 | 2619120.263 | 1240620.4837 | 2619136.2979 | 1240634.9192
35 | 2619120.263 | 1240620.4837 | 2619154.6035 | 1240583.1057
36 | 2619092.2109 | 1240592.6136 | 2619103.3668 | 1240604.1695
37 | 2619154.4974 | 1240651.3035 | 2619136.2979 | 1240634.9192
38 | 2619154.6035 | 1240583.1057 | 2619150.0018 | 1240568.1037 | 2619143.0296 | 1240560.1065
39 | 2619154.4974 | 1240651.3035 | 2619143.4547 | 1240667.9877
40 | 2619154.4974 | 1240651.3035 | 2619155.4992 | 1240652.0713
41 | 2618958.3003 | 1240509.2979 | 2618966.1631 | 1240522.4363
42 | 2618944.9832 | 1240518.801 | 2618943.6225 | 1240519.772
43 | 2618944.9832 | 1240518.801 | 2618954.6493 | 1240511.9032
44 | 2618943.6225 | 1240519.772 | 2618927.9679 | 1240530.943
45 | 2618958.3003 | 1240509.2979 | 2618954.6493 | 1240511.9032
46 | 2618918.4872 | 1240537.7084 | 2618927.9679 | 1240530.943
47 | 2618958.3003 | 1240509.2979 | 2618965.7857 | 1240505.1953
48 | 2618899.8971 | 1240550.4046 | 2618918.204 | 1240537.9105 | 2618918.4872 | 1240537.7084
49 | 2618980.4853 | 1240497.1387 | 2618965.7857 | 1240505.1953
50 | 2618899.8971 | 1240550.4046 | 2618920.3545 | 1240575.4545
51 | 2618980.4853 | 1240497.1387 | 2618990.1112 | 1240513.713
52 | 2619141.8638 | 1240558.7693 | 2619143.0296 | 1240560.1065
53 | 2618948.4141 | 1240609.813 | 2618920.3545 | 1240575.4545
54 | 2618948.4141 | 1240609.813 | 2618949.3807 | 1240610.9966
55 | 2618954.1997 | 1240616.8966 | 2618952.4148 | 1240614.7118 | 2618949.3807 | 1240610.9966
56 | 2618954.1997 | 1240616.8966 | 2618966.0929 | 1240633.5449 | 2618975.2671 | 1240646.3918

## bus_geodata
| x | y | coords
0 | 2619062.7503 | 1240570.2937
1 | 2619067.101 | 1240566.6034
2 | 2619036.1002 | 1240592.8984
3 | 2619020.0066 | 1240565.1879
4 | 2619015.3986 | 1240604.7063
5 | 2619048.3984 | 1240616.8646
6 | 2619075.5421 | 1240575.3471
7 | 2619008.3266 | 1240545.0769
8 | 2619020.2825 | 1240614.0345
9 | 2619010.8094 | 1240597.038
10 | 2619059.3151 | 1240638.1385
11 | 2619076.6695 | 1240576.515
12 | 2619020.7258 | 1240614.8812
13 | 2619009.9735 | 1240595.6413
14 | 2619069.1993 | 1240657.4002
15 | 2619090.0569 | 1240590.3824
16 | 2619028.7582 | 1240630.2228
17 | 2619032.6279 | 1240637.6139
18 | 2619023.4568 | 1240620.0974
19 | 2619035.8033 | 1240643.6788
20 | 2619037.487 | 1240646.8945
21 | 2619044.9466 | 1240661.1422
22 | 2618999.6854 | 1240578.4504
23 | 2618997.4577 | 1240574.7279
24 | 2618989.3505 | 1240561.1813
25 | 2618984.8756 | 1240553.7039
26 | 2618978.6143 | 1240543.2416
27 | 2618970.6625 | 1240529.9546
28 | 2619089.4728 | 1240635.9283
29 | 2619093.8317 | 1240631.3119
30 | 2619111.5023 | 1240612.5967
31 | 2619081.7671 | 1240676.9733
32 | 2619120.263 | 1240620.4837
33 | 2619103.3668 | 1240604.1695
34 | 2619136.2979 | 1240634.9192
35 | 2619154.6035 | 1240583.1057
36 | 2619092.2109 | 1240592.6136
37 | 2619154.4974 | 1240651.3035
38 | 2618966.1631 | 1240522.4363
39 | 2618944.9832 | 1240518.801
40 | 2618943.6225 | 1240519.772
41 | 2618954.6493 | 1240511.9032
42 | 2618927.9679 | 1240530.943
43 | 2618958.3003 | 1240509.2979
44 | 2618918.4872 | 1240537.7084
45 | 2618965.7857 | 1240505.1953
46 | 2618899.8971 | 1240550.4046
47 | 2618980.4853 | 1240497.1387
48 | 2619141.8638 | 1240558.7693
49 | 2619143.0296 | 1240560.1065
50 | 2618920.3545 | 1240575.4545
51 | 2618990.1112 | 1240513.713
52 | 2618948.4141 | 1240609.813
53 | 2619143.4547 | 1240667.9877
54 | 2618949.3807 | 1240610.9966
55 | 2618954.1997 | 1240616.8966
56 | 2618975.2671 | 1240646.3918
57 | 2619155.4992 | 1240652.0713
58 | 2619015.3986 | 1240604.7063

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99324 | -0.047431 | 0.0019934 | 0.00049959
1 | 0.99325 | -0.047316 | 0 | 0
2 | 1 | 0 | -0.084414 | -0.021001
3 | 0.99982 | -0.0012411 | 0.0023689 | 0.00059369
4 | 0.99854 | -0.010196 | 0 | 0
5 | 0.99859 | -0.0098257 | 0.0019116 | 0.00047909
6 | 0.99329 | -0.04707 | 0.001892 | 0.00047417
7 | 0.99977 | -0.0015914 | 0.0015073 | 0.00037778
8 | 0.99841 | -0.011121 | 0.00089848 | 0.00022518
9 | 0.9981 | -0.013249 | 0.001128 | 0.00028271
10 | 0.99741 | -0.018112 | 0.0026474 | 0.0006635
11 | 0.9933 | -0.047007 | 0.0018969 | 0.00047541
12 | 0.9984 | -0.011197 | 0.0010768 | 0.00026988
13 | 0.99803 | -0.013787 | 0.0014329 | 0.00035913
14 | 0.99642 | -0.025054 | 0 | 0
15 | 0.99346 | -0.045879 | 0.0019506 | 0.00048888
16 | 0.99824 | -0.012273 | 0.0011392 | 0.00028551
17 | 0.99819 | -0.012671 | 0.00091756 | 0.00022996
18 | 0.99834 | -0.011597 | 0.00089941 | 0.00022541
19 | 0.99815 | -0.012934 | 0.00087866 | 0.00022021
20 | 0.99813 | -0.013042 | 0.0014266 | 0.00035753
21 | 0.9981 | -0.013289 | 0.0015344 | 0.00038454
22 | 0.99712 | -0.020128 | 0.0011623 | 0.0002913
23 | 0.99693 | -0.021452 | 0.0010991 | 0.00027545
24 | 0.99627 | -0.026099 | 0.00091553 | 0.00022945
25 | 0.99591 | -0.028586 | 0.00156 | 0.00039097
26 | 0.99545 | -0.031878 | 0.00094225 | 0.00023615
27 | 0.99487 | -0.035915 | 0.0011065 | 0.00027732
28 | 0.99514 | -0.034013 | 0.0015409 | 0.0003862
29 | 0.99488 | -0.035844 | 0.0020049 | 0.00050246
30 | 0.9939 | -0.042753 | 0 | 0
31 | 0.99636 | -0.025472 | 0.0017855 | 0.00044748
32 | 0.99364 | -0.044574 | 0.00091129 | 0.00022839
33 | 0.99371 | -0.044091 | 0.0017855 | 0.00044748
34 | 0.99348 | -0.045702 | 0.0026086 | 0.00065379
35 | 0.99297 | -0.049296 | 0.0049949 | 0.0012518
36 | 0.99349 | -0.045636 | 0.0017797 | 0.00044604
37 | 0.99339 | -0.046337 | 0 | 0
38 | 0.99456 | -0.038103 | 0.0010934 | 0.00027404
39 | 0.99365 | -0.044525 | 0.0021492 | 0.00053863
40 | 0.99361 | -0.044761 | 0.0018042 | 0.00045217
41 | 0.99392 | -0.042586 | 0.0020355 | 0.00051015
42 | 0.99328 | -0.047134 | 0.0015316 | 0.00038385
43 | 0.99404 | -0.041762 | 0 | 0
44 | 0.9931 | -0.048391 | 0.0016985 | 0.00042568
45 | 0.99397 | -0.042234 | 0.0027781 | 0.00069627
46 | 0.99281 | -0.050434 | 0 | 0
47 | 0.99391 | -0.042691 | 0 | 0
48 | 0.99281 | -0.05046 | 0.0025473 | 0.00063842
49 | 0.99281 | -0.050414 | 0.00165 | 0.00041353
50 | 0.99239 | -0.053371 | 0.0033587 | 0.00084176
51 | 0.99383 | -0.043213 | 0.0026956 | 0.00067558
52 | 0.99204 | -0.05589 | 0.0014956 | 0.00037484
53 | 0.99336 | -0.046558 | 0.0010918 | 0.00027363
54 | 0.99203 | -0.055953 | 0.0012103 | 0.00030332
55 | 0.992 | -0.056177 | 0 | 0
56 | 0.99185 | -0.057239 | 0.0028888 | 0.000724
57 | 0.99339 | -0.046356 | 0.0014682 | 0.00036796
58 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0019934 | -0.00049959 | 0.0019934 | 0.00049953 | 3.1749e-08 | -6.1626e-08 | 0.0029864 | 0.0029864 | 0.0029864 | 0.99324 | -0.047431 | 0.99325 | -0.047316 | 1.1061
1 | -0.0019934 | -0.00049953 | 0.0019935 | 0.0004994 | 6.7633e-08 | -1.3129e-07 | 0.0029864 | 0.0029863 | 0.0029864 | 0.99325 | -0.047316 | 0.99329 | -0.04707 | 1.1061
2 | 0.0038769 | 0.00097103 | -0.0038763 | -0.00097119 | 6.6545e-07 | -1.6439e-07 | 0.0057687 | 0.0057689 | 0.0057689 | 1 | 0 | 0.99982 | -0.0012411 | 2.1366
3 | 0.043068 | 0.010817 | -0.043007 | -0.010793 | 6.0958e-05 | 2.3134e-05 | 0.064094 | 0.064094 | 0.064094 | 1 | 0 | 0.99854 | -0.010196 | 23.7386
4 | 0.036669 | 0.0092129 | -0.036618 | -0.009194 | 5.0058e-05 | 1.89e-05 | 0.054571 | 0.054572 | 0.054572 | 1 | 0 | 0.99859 | -0.0098257 | 20.2117
5 | 0.0015074 | 0.0003775 | -0.0015073 | -0.00037778 | 7.3038e-08 | -2.769e-07 | 0.0022434 | 0.0022435 | 0.0022435 | 0.99982 | -0.0012411 | 0.99977 | -0.0015914 | 0.83091
6 | 0.0087737 | 0.0021984 | -0.0087726 | -0.0021981 | 1.1231e-06 | 2.9425e-07 | 0.013074 | 0.013074 | 0.013074 | 0.99854 | -0.010196 | 0.99841 | -0.011121 | 4.8424
7 | 0.034234 | 0.008595 | -0.034219 | -0.0085895 | 1.4516e-05 | 5.4661e-06 | 0.05102 | 0.05102 | 0.05102 | 0.99854 | -0.010196 | 0.9981 | -0.013249 | 18.8963
8 | 0.034707 | 0.0087149 | -0.034667 | -0.0086999 | 3.9917e-05 | 1.504e-05 | 0.051723 | 0.051723 | 0.051723 | 0.99859 | -0.0098257 | 0.99741 | -0.018112 | 19.1567
9 | -0.0038855 | -0.00097357 | 0.0038855 | 0.00097356 | 3.4316e-08 | -7.8122e-09 | 0.0058206 | 0.0058206 | 0.0058206 | 0.99329 | -0.04707 | 0.9933 | -0.047007 | 2.1558
10 | 0.0078741 | 0.0019729 | -0.007874 | -0.0019729 | 8.2128e-08 | 1.909e-08 | 0.011735 | 0.011735 | 0.011735 | 0.99841 | -0.011121 | 0.9984 | -0.011197 | 4.3464
11 | 0.033091 | 0.0083068 | -0.033089 | -0.0083059 | 2.4725e-06 | 9.2968e-07 | 0.049338 | 0.049338 | 0.049338 | 0.9981 | -0.013249 | 0.99803 | -0.013787 | 18.2734
12 | 0.03202 | 0.0080364 | -0.031989 | -0.0080248 | 3.0833e-05 | 1.1577e-05 | 0.047774 | 0.047774 | 0.047774 | 0.99741 | -0.018112 | 0.99642 | -0.025054 | 17.694
13 | -0.0057824 | -0.001449 | 0.0057833 | 0.0014491 | 9.0249e-07 | 9.7576e-08 | 0.0086623 | 0.0086622 | 0.0086623 | 0.9933 | -0.047007 | 0.99346 | -0.045879 | 3.2083
14 | 0.0067972 | 0.001703 | -0.0067968 | -0.001703 | 3.7705e-07 | 6.8025e-08 | 0.01013 | 0.01013 | 0.01013 | 0.9984 | -0.011197 | 0.99834 | -0.011597 | 3.752
15 | 0.031656 | 0.0079467 | -0.031628 | -0.0079363 | 2.7853e-05 | 1.0451e-05 | 0.047202 | 0.047202 | 0.047202 | 0.99803 | -0.013787 | 0.99712 | -0.020128 | 17.4822
16 | 0.0017856 | 0.00044722 | -0.0017855 | -0.00044748 | 1.032e-07 | -2.6327e-07 | 0.0026664 | 0.0026665 | 0.0026665 | 0.99642 | -0.025054 | 0.99636 | -0.025472 | 0.9876
17 | 0.030203 | 0.0075776 | -0.030166 | -0.0075635 | 3.7493e-05 | 1.4036e-05 | 0.045107 | 0.045107 | 0.045107 | 0.99642 | -0.025054 | 0.99514 | -0.034013 | 16.7064
18 | -0.0077339 | -0.0019379 | 0.0077342 | 0.001938 | 2.5969e-07 | 5.9721e-08 | 0.011584 | 0.011584 | 0.011584 | 0.99346 | -0.045879 | 0.99349 | -0.045636 | 4.2903
19 | 0.0047576 | 0.001192 | -0.0047574 | -0.001192 | 2.6182e-07 | -8.3604e-09 | 0.0070918 | 0.0070918 | 0.0070918 | 0.99824 | -0.012273 | 0.99819 | -0.012671 | 2.6266
20 | -0.0058968 | -0.0014775 | 0.0058974 | 0.0014776 | 5.5102e-07 | 6.2499e-08 | 0.0087899 | 0.0087898 | 0.0087899 | 0.99824 | -0.012273 | 0.99834 | -0.011597 | 3.2555
21 | 0.0038398 | 0.00096203 | -0.0038397 | -0.00096207 | 1.3996e-07 | -3.5653e-08 | 0.005724 | 0.005724 | 0.005724 | 0.99819 | -0.012671 | 0.99815 | -0.012934 | 2.12
22 | 0.002961 | 0.00074186 | -0.002961 | -0.00074189 | 4.4133e-08 | -3.047e-08 | 0.0044141 | 0.0044141 | 0.0044141 | 0.99815 | -0.012934 | 0.99813 | -0.013042 | 1.6349
23 | 0.0015344 | 0.00038435 | -0.0015344 | -0.00038454 | 5.2509e-08 | -1.9e-07 | 0.0022874 | 0.0022875 | 0.0022875 | 0.99813 | -0.013042 | 0.9981 | -0.013289 | 0.84722
24 | 0.030465 | 0.007645 | -0.03046 | -0.0076429 | 5.5962e-06 | 2.0958e-06 | 0.045467 | 0.045467 | 0.045467 | 0.99712 | -0.020128 | 0.99693 | -0.021452 | 16.8398
25 | 0.029361 | 0.0073674 | -0.029342 | -0.0073604 | 1.8922e-05 | 7.0721e-06 | 0.043827 | 0.043827 | 0.043827 | 0.99693 | -0.021452 | 0.99627 | -0.026099 | 16.2322
26 | 0.028426 | 0.0071309 | -0.028417 | -0.0071273 | 9.8031e-06 | 3.657e-06 | 0.04246 | 0.04246 | 0.04246 | 0.99627 | -0.026099 | 0.99591 | -0.028586 | 15.7258
27 | 0.026857 | 0.0067363 | -0.026844 | -0.0067317 | 1.2252e-05 | 4.5537e-06 | 0.040129 | 0.040129 | 0.040129 | 0.99591 | -0.028586 | 0.99545 | -0.031878 | 14.8626
28 | 0.025902 | 0.0064956 | -0.025888 | -0.0064902 | 1.4487e-05 | 5.3706e-06 | 0.03872 | 0.03872 | 0.03872 | 0.99545 | -0.031878 | 0.99487 | -0.035915 | 14.3409
29 | 0.024781 | 0.0062129 | -0.024774 | -0.0062101 | 7.5113e-06 | 2.7752e-06 | 0.037065 | 0.037065 | 0.037065 | 0.99487 | -0.035915 | 0.99456 | -0.038103 | 13.728
30 | 0.028625 | 0.0071773 | -0.028617 | -0.0071746 | 7.2585e-06 | 2.7093e-06 | 0.042803 | 0.042803 | 0.042803 | 0.99514 | -0.034013 | 0.99488 | -0.035844 | 15.8531
31 | 0.026613 | 0.0066722 | -0.026587 | -0.0066627 | 2.5448e-05 | 9.4537e-06 | 0.039805 | 0.039805 | 0.039805 | 0.99488 | -0.035844 | 0.9939 | -0.042753 | 14.7425
32 | 0.015284 | 0.00383 | -0.01528 | -0.0038286 | 3.8513e-06 | 1.3285e-06 | 0.022882 | 0.022882 | 0.022882 | 0.9939 | -0.042753 | 0.99364 | -0.044574 | 8.4748
33 | 0.011303 | 0.0028327 | -0.011301 | -0.0028321 | 2.0932e-06 | 6.5332e-07 | 0.016923 | 0.016923 | 0.016923 | 0.9939 | -0.042753 | 0.99371 | -0.044091 | 6.2678
34 | 0.0051697 | 0.0012949 | -0.0051689 | -0.0012949 | 8.0687e-07 | 3.0915e-08 | 0.0077415 | 0.0077416 | 0.0077416 | 0.99364 | -0.044574 | 0.99348 | -0.045702 | 2.8673
35 | 0.0091989 | 0.0023053 | -0.0091929 | -0.0023037 | 6.0107e-06 | 1.6548e-06 | 0.013776 | 0.013776 | 0.013776 | 0.99364 | -0.044574 | 0.99297 | -0.049296 | 5.1022
36 | 0.0095159 | 0.0023846 | -0.0095139 | -0.002384 | 2.0351e-06 | 5.7469e-07 | 0.014249 | 0.014249 | 0.014249 | 0.99371 | -0.044091 | 0.99349 | -0.045636 | 5.2776
37 | 0.0025602 | 0.0006411 | -0.00256 | -0.00064133 | 2.2468e-07 | -2.3065e-07 | 0.0038345 | 0.0038346 | 0.0038346 | 0.99348 | -0.045702 | 0.99339 | -0.046337 | 1.4202
38 | 0.004198 | 0.0010518 | -0.0041973 | -0.0010519 | 6.4951e-07 | -9.0359e-08 | 0.0062908 | 0.0062909 | 0.0062909 | 0.99297 | -0.049296 | 0.99281 | -0.050414 | 2.33
39 | 0.0010918 | 0.00027339 | -0.0010918 | -0.00027363 | 3.3393e-08 | -2.4617e-07 | 0.0016354 | 0.0016355 | 0.0016355 | 0.99339 | -0.046337 | 0.99336 | -0.046558 | 0.60574
40 | 0.0014682 | 0.00036794 | -0.0014682 | -0.00036795 | 3.8091e-09 | -1.4876e-08 | 0.0021992 | 0.0021992 | 0.0021992 | 0.99339 | -0.046337 | 0.99339 | -0.046356 | 0.81451
41 | 0.02368 | 0.0059361 | -0.023668 | -0.0059317 | 1.1993e-05 | 4.4142e-06 | 0.03543 | 0.03543 | 0.03543 | 0.99456 | -0.038103 | 0.99404 | -0.041762 | 13.1221
42 | 0.014003 | 0.0035091 | -0.014002 | -0.0035089 | 4.5866e-07 | 1.5475e-07 | 0.020969 | 0.020969 | 0.020969 | 0.99365 | -0.044525 | 0.99361 | -0.044761 | 7.7663
43 | -0.016152 | -0.0040477 | 0.016156 | 0.0040492 | 4.3351e-06 | 1.5135e-06 | 0.024188 | 0.024187 | 0.024188 | 0.99365 | -0.044525 | 0.99392 | -0.042586 | 8.9583
44 | 0.012198 | 0.0030568 | -0.012194 | -0.0030555 | 4.0045e-06 | 1.2912e-06 | 0.018267 | 0.018267 | 0.018267 | 0.99361 | -0.044761 | 0.99328 | -0.047134 | 6.7657
45 | -0.018192 | -0.0045594 | 0.018194 | 0.0045601 | 2.076e-06 | 7.4031e-07 | 0.027235 | 0.027235 | 0.027235 | 0.99392 | -0.042586 | 0.99404 | -0.041762 | 10.087
46 | 0.010662 | 0.0026716 | -0.01066 | -0.0026711 | 1.8542e-06 | 5.6244e-07 | 0.015973 | 0.015973 | 0.015973 | 0.99328 | -0.047134 | 0.9931 | -0.048391 | 5.9159
47 | 0.0054744 | 0.0013715 | -0.0054741 | -0.0013715 | 3.5769e-07 | 2.6926e-08 | 0.0081947 | 0.0081948 | 0.0081948 | 0.99404 | -0.041762 | 0.99397 | -0.042234 | 3.0351
48 | 0.008962 | 0.0022454 | -0.0089595 | -0.0022447 | 2.5329e-06 | 6.8302e-07 | 0.013428 | 0.013428 | 0.013428 | 0.9931 | -0.048391 | 0.99281 | -0.050434 | 4.9734
49 | 0.0026959 | 0.00067525 | -0.0026958 | -0.0006754 | 1.7037e-07 | -1.5173e-07 | 0.0040358 | 0.0040359 | 0.0040359 | 0.99397 | -0.042234 | 0.99391 | -0.042691 | 1.4948
50 | 0.0089595 | 0.0022447 | -0.0089558 | -0.0022437 | 3.639e-06 | 9.8158e-07 | 0.013428 | 0.013428 | 0.013428 | 0.99281 | -0.050434 | 0.99239 | -0.053371 | 4.9734
51 | 0.0026958 | 0.0006754 | -0.0026956 | -0.00067558 | 1.9481e-07 | -1.7345e-07 | 0.0040359 | 0.004036 | 0.004036 | 0.99391 | -0.042691 | 0.99383 | -0.043213 | 1.4948
52 | -0.0025473 | -0.00063842 | 0.0025473 | 0.0006384 | 1.6136e-08 | -1.6734e-08 | 0.0038179 | 0.0038179 | 0.0038179 | 0.99281 | -0.05046 | 0.99281 | -0.050414 | 1.414
53 | 0.0055972 | 0.001402 | -0.0055952 | -0.0014018 | 1.9496e-06 | 1.7689e-07 | 0.0083922 | 0.0083924 | 0.0083924 | 0.99239 | -0.053371 | 0.99204 | -0.05589 | 3.1083
54 | 0.0040996 | 0.0010269 | -0.0040996 | -0.0010269 | 3.6054e-08 | -5.8627e-09 | 0.006149 | 0.006149 | 0.006149 | 0.99204 | -0.05589 | 0.99203 | -0.055953 | 2.2774
55 | 0.0028893 | 0.00072363 | -0.0028892 | -0.00072369 | 8.9277e-08 | -6.4015e-08 | 0.0043337 | 0.0043337 | 0.0043337 | 0.99203 | -0.055953 | 0.992 | -0.056177 | 1.6051
56 | 0.0028892 | 0.00072369 | -0.0028888 | -0.00072399 | 4.248e-07 | -3.0449e-07 | 0.0043337 | 0.0043339 | 0.0043339 | 0.992 | -0.056177 | 0.99185 | -0.057239 | 1.6051

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.084414 | 0.021001

## res_load
| p_mw | q_mvar
0 | 0.0019934 | 0.00049959
1 | 0.0023689 | 0.00059369
2 | 0.0019116 | 0.00047909
3 | 0.001892 | 0.00047417
4 | 0.0015073 | 0.00037778
5 | 0.00089848 | 0.00022518
6 | 0.001128 | 0.00028271
7 | 0.0026474 | 0.0006635
8 | 0.0018969 | 0.00047541
9 | 0.0010768 | 0.00026988
10 | 0.0014329 | 0.00035913
11 | 0.0019506 | 0.00048888
12 | 0.0011392 | 0.00028551
13 | 0.00091756 | 0.00022996
14 | 0.00089941 | 0.00022541
15 | 0.00087866 | 0.00022021
16 | 0.0014266 | 0.00035753
17 | 0.0015344 | 0.00038454
18 | 0.0011623 | 0.0002913
19 | 0.0010991 | 0.00027545
20 | 0.00091553 | 0.00022945
21 | 0.00156 | 0.00039097
22 | 0.00094225 | 0.00023615
23 | 0.0011065 | 0.00027732
24 | 0.0015409 | 0.0003862
25 | 0.0020049 | 0.00050246
26 | 0.0017855 | 0.00044748
27 | 0.00091129 | 0.00022839
28 | 0.0017855 | 0.00044748
29 | 0.0026086 | 0.00065379
30 | 0.0049949 | 0.0012518
31 | 0.0017797 | 0.00044604
32 | 0.0010934 | 0.00027404
33 | 0.0021492 | 0.00053863
34 | 0.0018042 | 0.00045217
35 | 0.0020355 | 0.00051015
36 | 0.0015316 | 0.00038385
37 | 0.0016985 | 0.00042568
38 | 0.0027781 | 0.00069627
39 | 0.0025473 | 0.00063842
40 | 0.00165 | 0.00041353
41 | 0.0033587 | 0.00084176
42 | 0.0026956 | 0.00067558
43 | 0.0014956 | 0.00037484
44 | 0.0010918 | 0.00027363
45 | 0.0012103 | 0.00030332
46 | 0.0028888 | 0.000724
47 | 0.0014682 | 0.00036796

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1