## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2422-25_1_2_node_7 | 0.4 | n |  | TRUE
1 | bus_LV_2422-25_1_2_node_82 | 0.4 | n |  | TRUE
2 | bus_LV_2422-25_1_2_node_26 | 0.4 | n |  | TRUE
3 | bus_LV_2422-25_1_2_node_27 | 0.4 | n |  | TRUE
4 | bus_LV_2422-25_1_2_node_28 | 0.4 | n |  | TRUE
5 | bus_LV_2422-25_1_2_node_29 | 0.4 | n |  | TRUE
6 | bus_LV_2422-25_1_2_node_30 | 0.4 | n |  | TRUE
7 | bus_LV_2422-25_1_2_node_54 | 0.4 | n |  | TRUE
8 | bus_LV_2422-25_1_2_node_45 | 0.4 | n |  | TRUE
9 | bus_LV_2422-25_1_2_node_48 | 0.4 | n |  | TRUE
10 | bus_LV_2422-25_1_2_node_41 | 0.4 | n |  | TRUE
11 | bus_LV_2422-25_1_2_node_42 | 0.4 | n |  | TRUE
12 | bus_LV_2422-25_1_2_node_43 | 0.4 | n |  | TRUE
13 | bus_LV_2422-25_1_2_node_44 | 0.4 | n |  | TRUE
14 | bus_LV_2422-25_1_2_node_46 | 0.4 | n |  | TRUE
15 | bus_LV_2422-25_1_2_node_67 | 0.4 | n |  | TRUE
16 | bus_LV_2422-25_1_2_node_93 | 0.4 | n |  | TRUE
17 | bus_LV_2422-25_1_2_node_47 | 0.4 | n |  | TRUE
18 | bus_LV_2422-25_1_2_node_50 | 0.4 | n |  | TRUE
19 | bus_LV_2422-25_1_2_node_58 | 0.4 | n |  | TRUE
20 | bus_LV_2422-25_1_2_node_63 | 0.4 | n |  | TRUE
21 | bus_LV_2422-25_1_2_node_60 | 0.4 | n |  | TRUE
22 | bus_LV_2422-25_1_2_node_61 | 0.4 | n |  | TRUE
23 | bus_LV_2422-25_1_2_node_79 | 0.4 | n |  | TRUE
24 | bus_LV_2422-25_1_2_node_78 | 0.4 | n |  | TRUE
25 | bus_LV_2422-25_1_2_node_80 | 0.4 | n |  | TRUE
26 | bus_LV_2422-25_1_2_node_81 | 0.4 | n |  | TRUE
27 | bus_LV_2422-25_1_2_node_83 | 0.4 | n |  | TRUE
28 | bus_LV_2422-25_1_2_node_84 | 0.4 | n |  | TRUE
29 | bus_LV_2422-25_1_2_node_95 | 0.4 | n |  | TRUE
30 | bus_LV_2422-25_1_2_node_92 | 0.4 | n |  | TRUE
31 | bus_LV_2422-25_1_2_node_91 | 0.4 | n |  | TRUE
32 | bus_LV_2422-25_1_2_node_94 | 0.4 | n |  | TRUE
33 | bus_LV_2422-25_1_2_node_96 | 0.4 | n |  | TRUE
34 | bus_LV_2422-25_1_2_node_97 | 0.4 | n |  | TRUE
35 | bus_LV_2422-25_1_2_node_100 | 0.4 | n |  | TRUE
36 | bus_LV_2422-25_1_2_node_98 | 0.4 | n |  | TRUE
37 | bus_LV_2422-25_1_2_node_99 | 0.4 | n |  | TRUE
38 | bus_MV_333_0_node_57 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2422-25_1_2_load_7 | 0 | 0.0034051 | 0.0008534 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2422-25_1_2_load_82 | 1 | 0.0094533 | 0.0023692 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2422-25_1_2_load_26 | 2 | 0.014939 | 0.003744 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2422-25_1_2_load_27 | 3 | 0.0022182 | 0.00055593 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2422-25_1_2_load_28 | 4 | 0.0047349 | 0.0011867 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2422-25_1_2_load_54 | 7 | 0.0042079 | 0.0010546 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2422-25_1_2_load_45 | 8 | 0.028031 | 0.0070252 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2422-25_1_2_load_41 | 10 | 0.0028299 | 0.00070925 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2422-25_1_2_load_42 | 11 | 0.0078612 | 0.0019702 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2422-25_1_2_load_44 | 13 | 0.0017713 | 0.00044392 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2422-25_1_2_load_46 | 14 | 0.0018656 | 0.00046757 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2422-25_1_2_load_67 | 15 | 0.0058496 | 0.001466 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2422-25_1_2_load_47 | 17 | 0.0062229 | 0.0015596 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2422-25_1_2_load_50 | 18 | 0.0014368 | 0.00036009 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2422-25_1_2_load_60 | 21 | 0.0018619 | 0.00046665 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2422-25_1_2_load_61 | 22 | 0.001556 | 0.00038998 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2422-25_1_2_load_79 | 23 | 0.0012259 | 0.00030725 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2422-25_1_2_load_78 | 24 | 0.0013654 | 0.00034219 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2422-25_1_2_load_81 | 26 | 0.0082042 | 0.0020562 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2422-25_1_2_load_95 | 29 | 0.00053143 | 0.00013319 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2422-25_1_2_load_92 | 30 | 0.00050216 | 0.00012585 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2422-25_1_2_load_91 | 31 | 0.00051712 | 0.0001296 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2422-25_1_2_load_94 | 32 | 0.008912 | 0.0022335 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2422-25_1_2_load_100 | 35 | 0.0012158 | 0.0003047 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2422-25_1_2_load_99 | 37 | 0.0019968 | 0.00050045 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2422-25_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0080563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2422-25_1_2_line_1 | NAYY 4x150 SE | 1 | 6 | 0.017086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2422-25_1_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.0070883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2422-25_1_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.03865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2422-25_1_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.017764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2422-25_1_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0080513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2422-25_1_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.0072929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2422-25_1_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.047415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_2422-25_1_2_line_8 | NAYY 4x150 SE | 6 | 9 | 0.044987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2422-25_1_2_line_9 | NAYY 4x150 SE | 7 | 19 | 0.058089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2422-25_1_2_line_10 | NAYY 4x150 SE | 9 | 18 | 0.0079952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2422-25_1_2_line_11 | NAYY 4x150 SE | 9 | 17 | 0.045592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2422-25_1_2_line_12 | NAYY 4x150 SE | 10 | 11 | 0.040994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2422-25_1_2_line_13 | NAYY 4x150 SE | 10 | 12 | 0.023962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2422-25_1_2_line_14 | NAYY 4x150 SE | 11 | 13 | 0.010879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2422-25_1_2_line_15 | NAYY 4x150 SE | 12 | 14 | 0.035619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2422-25_1_2_line_16 | NAYY 4x150 SE | 13 | 15 | 0.030144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2422-25_1_2_line_17 | NAYY 4x150 SE | 14 | 16 | 0.03172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2422-25_1_2_line_18 | NAYY 4x150 SE | 16 | 32 | 0.013868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2422-25_1_2_line_19 | NAYY 4x150 SE | 16 | 31 | 0.030023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2422-25_1_2_line_20 | NAYY 4x150 SE | 19 | 20 | 0.013457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2422-25_1_2_line_21 | NAYY 4x150 SE | 20 | 23 | 0.0458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2422-25_1_2_line_22 | NAYY 4x150 SE | 20 | 22 | 0.065716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2422-25_1_2_line_23 | NAYY 4x150 SE | 21 | 22 | 0.021227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2422-25_1_2_line_24 | NAYY 4x150 SE | 23 | 24 | 0.021473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2422-25_1_2_line_25 | NAYY 4x150 SE | 24 | 25 | 0.01291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2422-25_1_2_line_26 | NAYY 4x150 SE | 25 | 26 | 0.025078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2422-25_1_2_line_27 | NAYY 4x150 SE | 26 | 27 | 0.038766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2422-25_1_2_line_28 | NAYY 4x150 SE | 27 | 28 | 0.026411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2422-25_1_2_line_29 | NAYY 4x150 SE | 28 | 29 | 0.016269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2422-25_1_2_line_30 | NAYY 4x150 SE | 28 | 30 | 0.019584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2422-25_1_2_line_31 | NAYY 4x150 SE | 29 | 33 | 0.030393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2422-25_1_2_line_32 | NAYY 4x150 SE | 32 | 33 | 0.040112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2422-25_1_2_line_33 | NAYY 4x150 SE | 33 | 34 | 0.005658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2422-25_1_2_line_34 | NAYY 4x150 SE | 34 | 35 | 0.009292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2422-25_1_2_line_35 | NAYY 4x150 SE | 34 | 36 | 0.028628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2422-25_1_2_line_36 | NAYY 4x150 SE | 36 | 37 | 0.005857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2422-25_1_2_trafo_45 | 0.25 MVA 20/0.4 kV | 38 | 8 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2619095.5088 | 1240537.9757 | 2619101.1834 | 1240532.2571
1 | 2619110.0974 | 1240517.9997 | 2619105.9007 | 1240527.5033 | 2619101.1834 | 1240532.2571
2 | 2619057.9387 | 1240505.1655 | 2619064.6569 | 1240507.426
3 | 2619102.2189 | 1240516.3404 | 2619072.6277 | 1240510.108 | 2619064.6569 | 1240507.426
4 | 2619041.102 | 1240499.5004 | 2619057.9387 | 1240505.1655
5 | 2619110.0974 | 1240517.9997 | 2619102.2189 | 1240516.3404
6 | 2619041.102 | 1240499.5004 | 2619034.1535 | 1240497.2857
7 | 2619041.102 | 1240499.5004 | 2619072.424 | 1240463.9038
8 | 2619154.801 | 1240524.1027 | 2619127.941 | 1240520.4363 | 2619110.0974 | 1240517.9997
9 | 2618978.0131 | 1240485.1901 | 2618994.9435 | 1240484.7882 | 2619034.1535 | 1240497.2857
10 | 2619154.801 | 1240524.1027 | 2619162.765 | 1240524.8084
11 | 2619154.801 | 1240524.1027 | 2619190.6835 | 1240552.2293
12 | 2619141.235 | 1240433.408 | 2619167.4734 | 1240464.9054
13 | 2619125.8982 | 1240414.9971 | 2619141.235 | 1240433.408
14 | 2619174.4363 | 1240473.264 | 2619167.4734 | 1240464.9054
15 | 2619125.8982 | 1240414.9971 | 2619102.5476 | 1240388.0993
16 | 2619174.4363 | 1240473.264 | 2619193.7296 | 1240496.4244
17 | 2619081.7531 | 1240364.1459 | 2619102.5476 | 1240388.0993
18 | 2619081.7531 | 1240364.1459 | 2619073.1843 | 1240353.2413
19 | 2619081.7531 | 1240364.1459 | 2619057.5293 | 1240381.882
20 | 2618978.0131 | 1240485.1901 | 2618975.1592 | 1240472.0394
21 | 2618975.1592 | 1240472.0394 | 2618971.337 | 1240459.0191 | 2618971.0902 | 1240458.1733 | 2618966.8012 | 1240444.5067 | 2618957.1302 | 1240430.4953
22 | 2618975.1592 | 1240472.0394 | 2618960.3199 | 1240471.0693 | 2618950.6677 | 1240467.6809 | 2618915.1034 | 1240447.7331
23 | 2618915.1034 | 1240447.7331 | 2618899.6252 | 1240462.2591
24 | 2618944.9326 | 1240412.8236 | 2618957.1302 | 1240430.4953
25 | 2618937.5988 | 1240402.1984 | 2618944.9326 | 1240412.8236
26 | 2618937.5988 | 1240402.1984 | 2618957.7952 | 1240387.3311
27 | 2618989.0144 | 1240364.3496 | 2618957.7952 | 1240387.3311
28 | 2618989.0144 | 1240364.3496 | 2619010.1986 | 1240348.4962
29 | 2619010.1986 | 1240348.4962 | 2619023.5181 | 1240339.1539
30 | 2619010.1986 | 1240348.4962 | 2619022.1244 | 1240364.0298
31 | 2619048.4004 | 1240321.7015 | 2619023.5181 | 1240339.1539
32 | 2619048.4004 | 1240321.7015 | 2619073.1843 | 1240353.2413
33 | 2619048.4004 | 1240321.7015 | 2619052.9028 | 1240318.2582
34 | 2619046.4163 | 1240313.2121 | 2619050.332 | 1240313.5359 | 2619052.9028 | 1240318.2582
35 | 2619052.9028 | 1240318.2582 | 2619075.6802 | 1240300.8314
36 | 2619072.2248 | 1240296.0951 | 2619075.6802 | 1240300.8314

## bus_geodata
| x | y | coords
0 | 2619095.5088 | 1240537.9757
1 | 2619101.1834 | 1240532.2571
2 | 2619064.6569 | 1240507.426
3 | 2619057.9387 | 1240505.1655
4 | 2619102.2189 | 1240516.3404
5 | 2619041.102 | 1240499.5004
6 | 2619110.0974 | 1240517.9997
7 | 2619034.1535 | 1240497.2857
8 | 2619072.424 | 1240463.9038
9 | 2619154.801 | 1240524.1027
10 | 2619141.235 | 1240433.408
11 | 2619167.4734 | 1240464.9054
12 | 2619125.8982 | 1240414.9971
13 | 2619174.4363 | 1240473.264
14 | 2619102.5476 | 1240388.0993
15 | 2619193.7296 | 1240496.4244
16 | 2619081.7531 | 1240364.1459
17 | 2619190.6835 | 1240552.2293
18 | 2619162.765 | 1240524.8084
19 | 2618978.0131 | 1240485.1901
20 | 2618975.1592 | 1240472.0394
21 | 2618899.6252 | 1240462.2591
22 | 2618915.1034 | 1240447.7331
23 | 2618957.1302 | 1240430.4953
24 | 2618944.9326 | 1240412.8236
25 | 2618937.5988 | 1240402.1984
26 | 2618957.7952 | 1240387.3311
27 | 2618989.0144 | 1240364.3496
28 | 2619010.1986 | 1240348.4962
29 | 2619023.5181 | 1240339.1539
30 | 2619022.1244 | 1240364.0298
31 | 2619057.5293 | 1240381.882
32 | 2619073.1843 | 1240353.2413
33 | 2619048.4004 | 1240321.7015
34 | 2619052.9028 | 1240318.2582
35 | 2619046.4163 | 1240313.2121
36 | 2619075.6802 | 1240300.8313
37 | 2619072.2248 | 1240296.0951
38 | 2619041.102 | 1240499.5004

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99327 | -0.046971 | 0.0034051 | 0.0008534
1 | 0.99331 | -0.046693 | 0.0094533 | 0.0023692
2 | 0.99527 | -0.032947 | 0.014939 | 0.003744
3 | 0.99568 | -0.030077 | 0.0022182 | 0.00055593
4 | 0.99387 | -0.042801 | 0.0047349 | 0.0011867
5 | 0.99676 | -0.022498 | 0 | 0
6 | 0.99363 | -0.044471 | 0 | 0
7 | 0.9962 | -0.026334 | 0.0042079 | 0.0010546
8 | 1 | 0 | -0.096759 | -0.024208
9 | 0.99313 | -0.04796 | 0 | 0
10 | 0.97435 | -0.18037 | 0.0028299 | 0.00070925
11 | 0.97342 | -0.18705 | 0.0078612 | 0.0019702
12 | 0.975 | -0.17576 | 0 | 0
13 | 0.9733 | -0.18793 | 0.0017713 | 0.00044392
14 | 0.97595 | -0.16891 | 0.0018656 | 0.00046757
15 | 0.97304 | -0.18978 | 0.0058496 | 0.001466
16 | 0.97689 | -0.16221 | 0 | 0
17 | 0.99273 | -0.050833 | 0.0062229 | 0.0015596
18 | 0.99312 | -0.048076 | 0.0014368 | 0.00036009
19 | 0.99213 | -0.054566 | 0 | 0
20 | 0.99119 | -0.061138 | 0 | 0
21 | 0.99081 | -0.063826 | 0.0018619 | 0.00046665
22 | 0.99087 | -0.063424 | 0.001556 | 0.00038998
23 | 0.98821 | -0.081997 | 0.0012259 | 0.00030725
24 | 0.98685 | -0.091549 | 0.0013654 | 0.00034219
25 | 0.98606 | -0.097123 | 0 | 0
26 | 0.98452 | -0.10798 | 0.0082042 | 0.0020562
27 | 0.9826 | -0.12153 | 0 | 0
28 | 0.9813 | -0.1308 | 0 | 0
29 | 0.9805 | -0.13643 | 0.00053143 | 0.00013319
30 | 0.98128 | -0.1309 | 0.00050216 | 0.00012585
31 | 0.97687 | -0.16237 | 0.00051712 | 0.0001296
32 | 0.97731 | -0.15921 | 0.008912 | 0.0022335
33 | 0.97905 | -0.14681 | 0 | 0
34 | 0.97902 | -0.147 | 0 | 0
35 | 0.979 | -0.14712 | 0.0012158 | 0.0003047
36 | 0.97894 | -0.1476 | 0 | 0
37 | 0.97892 | -0.14772 | 0.0019968 | 0.00050045
38 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0034051 | -0.0008534 | 0.0034052 | 0.00085334 | 1.3081e-07 | -5.3967e-08 | 0.0051011 | 0.0051011 | 0.0051011 | 0.99327 | -0.046971 | 0.99331 | -0.046693 | 1.8893
1 | -0.012859 | -0.0032226 | 0.012862 | 0.0032239 | 3.9559e-06 | 1.3003e-06 | 0.019262 | 0.019262 | 0.019262 | 0.99331 | -0.046693 | 0.99363 | -0.044471 | 7.1342
2 | -0.040241 | -0.01009 | 0.040257 | 0.010096 | 1.6011e-05 | 6.0661e-06 | 0.060166 | 0.060166 | 0.060166 | 0.99527 | -0.032947 | 0.99568 | -0.030077 | 22.2838
3 | 0.025302 | 0.0063458 | -0.025268 | -0.0063331 | 3.4517e-05 | 1.2774e-05 | 0.037831 | 0.037831 | 0.037831 | 0.99527 | -0.032947 | 0.99387 | -0.042801 | 14.0116
4 | -0.042476 | -0.010652 | 0.04252 | 0.010669 | 4.4671e-05 | 1.695e-05 | 0.063481 | 0.063481 | 0.063481 | 0.99568 | -0.030077 | 0.99676 | -0.022498 | 23.5115
5 | 0.020533 | 0.0051464 | -0.020528 | -0.0051447 | 4.7481e-06 | 1.7219e-06 | 0.030742 | 0.030742 | 0.030742 | 0.99387 | -0.042801 | 0.99363 | -0.044471 | 11.386
6 | 0.053137 | 0.013424 | -0.053109 | -0.013413 | 2.8664e-05 | 1.0929e-05 | 0.079364 | 0.079364 | 0.079364 | 0.99676 | -0.022498 | 0.9962 | -0.026334 | 29.3941
7 | -0.095658 | -0.024093 | 0.095959 | 0.024208 | 0.00030186 | 0.00011486 | 0.14285 | 0.14284 | 0.14285 | 0.99676 | -0.022498 | 1 | 0 | 26.4528
8 | 0.0076659 | 0.0019208 | -0.0076622 | -0.00192 | 3.6996e-06 | 8.4053e-07 | 0.01148 | 0.01148 | 0.01148 | 0.99363 | -0.044471 | 0.99313 | -0.04796 | 4.2519
9 | 0.048901 | 0.012359 | -0.048707 | -0.012285 | 0.00019358 | 7.3701e-05 | 0.073079 | 0.073079 | 0.073079 | 0.9962 | -0.026334 | 0.99213 | -0.054566 | 27.0664
10 | 0.0014368 | 0.00036 | -0.0014368 | -0.00036009 | 2.3121e-08 | -9.4561e-08 | 0.0021527 | 0.0021528 | 0.0021528 | 0.99313 | -0.04796 | 0.99312 | -0.048076 | 0.79732
11 | 0.0062254 | 0.00156 | -0.0062229 | -0.0015596 | 2.4752e-06 | 3.6229e-07 | 0.0093274 | 0.0093276 | 0.0093276 | 0.99313 | -0.04796 | 0.99273 | -0.050833 | 3.4547
12 | 0.015499 | 0.0038856 | -0.015484 | -0.0038806 | 1.4332e-05 | 5.0022e-06 | 0.02367 | 0.02367 | 0.02367 | 0.97435 | -0.18037 | 0.97342 | -0.18705 | 8.7667
13 | -0.018329 | -0.0045948 | 0.01834 | 0.0045991 | 1.1716e-05 | 4.2074e-06 | 0.027992 | 0.027992 | 0.027992 | 0.97435 | -0.18037 | 0.975 | -0.17576 | 10.3673
14 | 0.0076233 | 0.0019104 | -0.0076224 | -0.0019102 | 9.2184e-07 | 2.1933e-07 | 0.011653 | 0.011653 | 0.011653 | 0.97342 | -0.18705 | 0.9733 | -0.18793 | 4.316
15 | -0.01834 | -0.0045991 | 0.018358 | 0.0046053 | 1.7415e-05 | 6.2535e-06 | 0.027992 | 0.027992 | 0.027992 | 0.975 | -0.17576 | 0.97595 | -0.16891 | 10.3673
16 | 0.0058511 | 0.0014663 | -0.0058496 | -0.001466 | 1.5051e-06 | 2.0437e-07 | 0.0089453 | 0.0089454 | 0.0089454 | 0.9733 | -0.18793 | 0.97304 | -0.18978 | 3.3131
17 | -0.020223 | -0.0050729 | 0.020242 | 0.0050797 | 1.8821e-05 | 6.842e-06 | 0.030836 | 0.030836 | 0.030836 | 0.97595 | -0.16891 | 0.97689 | -0.16221 | 11.4207
18 | -0.020759 | -0.0052089 | 0.020768 | 0.0052121 | 8.6543e-06 | 3.1549e-06 | 0.031623 | 0.031623 | 0.031623 | 0.97689 | -0.16221 | 0.97731 | -0.15921 | 11.7124
19 | 0.00051713 | 0.00012923 | -0.00051712 | -0.0001296 | 1.1622e-08 | -3.714e-07 | 0.00078758 | 0.00078771 | 0.00078771 | 0.97689 | -0.16221 | 0.97687 | -0.16237 | 0.29174
20 | 0.048707 | 0.012285 | -0.048662 | -0.012268 | 4.4846e-05 | 1.7075e-05 | 0.073079 | 0.073079 | 0.073079 | 0.99213 | -0.054566 | 0.99119 | -0.061138 | 27.0664
21 | 0.045243 | 0.011412 | -0.045111 | -0.011362 | 0.00013194 | 5.0158e-05 | 0.067947 | 0.067947 | 0.067947 | 0.99119 | -0.061138 | 0.98821 | -0.081997 | 25.1655
22 | 0.0034192 | 0.00085596 | -0.0034181 | -0.00085639 | 1.0803e-06 | -4.3123e-07 | 0.0051326 | 0.0051329 | 0.0051329 | 0.99119 | -0.061138 | 0.99087 | -0.063424 | 1.9011
23 | -0.0018619 | -0.00046665 | 0.0018621 | 0.00046641 | 1.0357e-07 | -2.3357e-07 | 0.0027963 | 0.0027962 | 0.0027963 | 0.99081 | -0.063826 | 0.99087 | -0.063424 | 1.0357
24 | 0.043885 | 0.011054 | -0.043827 | -0.011032 | 5.8544e-05 | 2.2242e-05 | 0.066101 | 0.066101 | 0.066101 | 0.98821 | -0.081997 | 0.98685 | -0.091549 | 24.4818
25 | 0.042461 | 0.01069 | -0.042428 | -0.010677 | 3.3041e-05 | 1.2543e-05 | 0.064042 | 0.064042 | 0.064042 | 0.98685 | -0.091549 | 0.98606 | -0.097123 | 23.7194
26 | 0.042428 | 0.010677 | -0.042364 | -0.010653 | 6.4183e-05 | 2.4366e-05 | 0.064042 | 0.064042 | 0.064042 | 0.98606 | -0.097123 | 0.98452 | -0.10798 | 23.7194
27 | 0.03416 | 0.0085969 | -0.034095 | -0.0085726 | 6.4513e-05 | 2.4321e-05 | 0.051643 | 0.051643 | 0.051643 | 0.98452 | -0.10798 | 0.9826 | -0.12153 | 19.1269
28 | 0.034095 | 0.0085726 | -0.034052 | -0.0085561 | 4.3953e-05 | 1.6571e-05 | 0.051643 | 0.051643 | 0.051643 | 0.9826 | -0.12153 | 0.9813 | -0.1308 | 19.127
29 | 0.033549 | 0.0084305 | -0.033523 | -0.0084205 | 2.6283e-05 | 9.9034e-06 | 0.050881 | 0.050882 | 0.050882 | 0.9813 | -0.1308 | 0.9805 | -0.13643 | 18.845
30 | 0.00050216 | 0.00012561 | -0.00050216 | -0.00012585 | 7.0849e-09 | -2.4467e-07 | 0.00076138 | 0.00076147 | 0.00076147 | 0.9813 | -0.1308 | 0.98128 | -0.1309 | 0.28203
31 | 0.032992 | 0.0082874 | -0.032944 | -0.0082695 | 4.7555e-05 | 1.7908e-05 | 0.050075 | 0.050075 | 0.050075 | 0.9805 | -0.13643 | 0.97905 | -0.14681 | 18.5464
32 | -0.02968 | -0.0074456 | 0.029731 | 0.0074648 | 5.112e-05 | 1.9158e-05 | 0.045192 | 0.045192 | 0.045192 | 0.97731 | -0.15921 | 0.97905 | -0.14681 | 16.7379
33 | 0.0032129 | 0.00080464 | -0.0032128 | -0.00080468 | 8.4181e-08 | -3.8772e-08 | 0.0048829 | 0.004883 | 0.004883 | 0.97905 | -0.14681 | 0.97902 | -0.147 | 1.8085
34 | 0.0012158 | 0.00030459 | -0.0012158 | -0.0003047 | 1.9798e-08 | -1.0923e-07 | 0.0018478 | 0.0018479 | 0.0018479 | 0.97902 | -0.147 | 0.979 | -0.14712 | 0.6844
35 | 0.001997 | 0.00050009 | -0.0019969 | -0.00050039 | 1.6457e-07 | -2.9666e-07 | 0.0030351 | 0.0030353 | 0.0030353 | 0.97902 | -0.147 | 0.97894 | -0.1476 | 1.1242
36 | 0.0019969 | 0.00050039 | -0.0019968 | -0.00050045 | 3.3671e-08 | -6.0685e-08 | 0.0030353 | 0.0030353 | 0.0030353 | 0.97894 | -0.1476 | 0.97892 | -0.14772 | 1.1242

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.12479 | 0.031233

## res_load
| p_mw | q_mvar
0 | 0.0034051 | 0.0008534
1 | 0.0094533 | 0.0023692
2 | 0.014939 | 0.003744
3 | 0.0022182 | 0.00055593
4 | 0.0047349 | 0.0011867
5 | 0.0042079 | 0.0010546
6 | 0.028031 | 0.0070252
7 | 0.0028299 | 0.00070925
8 | 0.0078612 | 0.0019702
9 | 0.0017713 | 0.00044392
10 | 0.0018656 | 0.00046757
11 | 0.0058496 | 0.001466
12 | 0.0062229 | 0.0015596
13 | 0.0014368 | 0.00036009
14 | 0.0018619 | 0.00046665
15 | 0.001556 | 0.00038998
16 | 0.0012259 | 0.00030725
17 | 0.0013654 | 0.00034219
18 | 0.0082042 | 0.0020562
19 | 0.00053143 | 0.00013319
20 | 0.00050216 | 0.00012585
21 | 0.00051712 | 0.0001296
22 | 0.008912 | 0.0022335
23 | 0.0012158 | 0.0003047
24 | 0.0019968 | 0.00050045

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1