## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2422-26_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2422-26_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2422-26_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2422-26_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2422-26_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2422-26_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2422-26_0_3_node_30 | 0.4 | n |  | TRUE
7 | bus_LV_2422-26_0_3_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_2422-26_0_3_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_2422-26_0_3_node_40 | 0.4 | n |  | TRUE
10 | bus_LV_2422-26_0_3_node_28 | 0.4 | n |  | TRUE
11 | bus_LV_2422-26_0_3_node_20 | 0.4 | n |  | TRUE
12 | bus_LV_2422-26_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2422-26_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2422-26_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2422-26_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2422-26_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2422-26_0_3_node_39 | 0.4 | n |  | TRUE
18 | bus_LV_2422-26_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_2422-26_0_3_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_2422-26_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_2422-26_0_3_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_2422-26_0_3_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_2422-26_0_3_node_38 | 0.4 | n |  | TRUE
24 | bus_LV_2422-26_0_3_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_2422-26_0_3_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_2422-26_0_3_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_2422-26_0_3_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_2422-26_0_3_node_45 | 0.4 | n |  | TRUE
29 | bus_LV_2422-26_0_3_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_2422-26_0_3_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_2422-26_0_3_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2422-26_0_3_node_44 | 0.4 | n |  | TRUE
33 | bus_LV_2422-26_0_3_node_41 | 0.4 | n |  | TRUE
34 | bus_LV_2422-26_0_3_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_2422-26_0_3_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_2422-26_0_3_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_2422-26_0_3_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_2422-26_0_3_node_42 | 0.4 | n |  | TRUE
39 | bus_LV_2422-26_0_3_node_43 | 0.4 | n |  | TRUE
40 | bus_LV_2422-26_0_3_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_2422-26_0_3_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_2422-26_0_3_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_2422-26_0_3_node_33 | 0.4 | n |  | TRUE
44 | bus_MV_333_0_node_62 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2422-26_0_3_load_0 | 0 | 0.00013102 | 3.2836e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2422-26_0_3_load_1 | 1 | 0.00018139 | 4.5461e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2422-26_0_3_load_3 | 3 | 0.023894 | 0.0059884 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2422-26_0_3_load_5 | 5 | 0.000171 | 4.2857e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2422-26_0_3_load_18 | 7 | 0.0065493 | 0.0016414 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2422-26_0_3_load_40 | 9 | 0.013309 | 0.0033356 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2422-26_0_3_load_6 | 12 | 0.00091443 | 0.00022918 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2422-26_0_3_load_7 | 13 | 0.0021355 | 0.00053521 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2422-26_0_3_load_8 | 14 | 0.0021302 | 0.00053389 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2422-26_0_3_load_9 | 15 | 0.0015747 | 0.00039465 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2422-26_0_3_load_39 | 17 | 0.0016801 | 0.00042107 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2422-26_0_3_load_16 | 18 | 0.00097957 | 0.0002455 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2422-26_0_3_load_17 | 19 | 0.0016063 | 0.00040257 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2422-26_0_3_load_14 | 20 | 0.002223 | 0.00055713 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2422-26_0_3_load_24 | 21 | 0.00098495 | 0.00024685 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2422-26_0_3_load_38 | 23 | 0.0010486 | 0.00026281 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2422-26_0_3_load_11 | 24 | 0.001239 | 0.00031053 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2422-26_0_3_load_12 | 25 | 0.0017622 | 0.00044165 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2422-26_0_3_load_15 | 27 | 0.0027091 | 0.00067896 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2422-26_0_3_load_25 | 29 | 0.0014791 | 0.0003707 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2422-26_0_3_load_23 | 30 | 0.0016481 | 0.00041304 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2422-26_0_3_load_21 | 31 | 0.00084478 | 0.00021172 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2422-26_0_3_load_44 | 32 | 0.003684 | 0.00092329 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2422-26_0_3_load_41 | 33 | 0.00085316 | 0.00021382 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2422-26_0_3_load_37 | 34 | 0.00081877 | 0.0002052 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2422-26_0_3_load_29 | 35 | 0.0032977 | 0.00082648 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2422-26_0_3_load_26 | 36 | 0.0028661 | 0.00071832 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2422-26_0_3_load_27 | 37 | 0.015123 | 0.0037902 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2422-26_0_3_load_42 | 38 | 0.016948 | 0.0042475 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2422-26_0_3_load_43 | 39 | 0.002188 | 0.00054838 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2422-26_0_3_load_35 | 40 | 0.03537 | 0.0088645 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2422-26_0_3_load_31 | 41 | 0.00068445 | 0.00017154 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2422-26_0_3_load_32 | 42 | 0.0018503 | 0.00046372 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 38 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2422-26_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.054069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
1 | LV_2422-26_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.020947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
2 | LV_2422-26_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.040392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_2422-26_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.038879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2422-26_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.053426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_2422-26_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.014739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_2422-26_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.020718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2422-26_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.077863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_2422-26_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.030152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2422-26_0_3_line_9 | NAYY 4x150 SE | 6 | 10 | 0.097141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_2422-26_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.032634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_2422-26_0_3_line_11 | NAYY 4x150 SE | 9 | 40 | 0.043718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2422-26_0_3_line_12 | NAYY 4x150 SE | 10 | 38 | 0.041034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_2422-26_0_3_line_13 | NAYY 4x150 SE | 10 | 37 | 0.025468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2422-26_0_3_line_14 | NAYY 4x150 SE | 11 | 32 | 0.012866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2422-26_0_3_line_15 | NAYY 4x150 SE | 11 | 28 | 0.08742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2422-26_0_3_line_16 | NAYY 4x150 SE | 12 | 13 | 0.0051446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2422-26_0_3_line_17 | NAYY 4x150 SE | 12 | 14 | 0.0053401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2422-26_0_3_line_18 | NAYY 4x150 SE | 13 | 15 | 0.011909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2422-26_0_3_line_19 | NAYY 4x150 SE | 14 | 16 | 0.011052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2422-26_0_3_line_20 | NAYY 4x150 SE | 15 | 17 | 0.011956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2422-26_0_3_line_21 | NAYY 4x150 SE | 16 | 18 | 0.022903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2422-26_0_3_line_22 | NAYY 4x150 SE | 16 | 19 | 0.021461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2422-26_0_3_line_23 | NAYY 4x150 SE | 17 | 20 | 0.004561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2422-26_0_3_line_24 | NAYY 4x150 SE | 18 | 21 | 0.0017512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2422-26_0_3_line_25 | NAYY 4x150 SE | 19 | 22 | 0.020334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2422-26_0_3_line_26 | NAYY 4x150 SE | 19 | 23 | 0.030557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2422-26_0_3_line_27 | NAYY 4x150 SE | 20 | 26 | 0.043201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2422-26_0_3_line_28 | NAYY 4x150 SE | 21 | 29 | 0.014496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2422-26_0_3_line_29 | NAYY 4x150 SE | 22 | 30 | 0.0041138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2422-26_0_3_line_30 | NAYY 4x150 SE | 22 | 31 | 0.012318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2422-26_0_3_line_31 | NAYY 4x150 SE | 24 | 25 | 0.010293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2422-26_0_3_line_32 | NAYY 4x150 SE | 24 | 26 | 0.030385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2422-26_0_3_line_33 | NAYY 4x150 SE | 26 | 27 | 0.00032144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2422-26_0_3_line_34 | NAYY 4x150 SE | 27 | 28 | 0.024294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2422-26_0_3_line_35 | NAYY 4x150 SE | 29 | 35 | 0.27236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2422-26_0_3_line_36 | NAYY 4x150 SE | 30 | 33 | 0.027841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2422-26_0_3_line_37 | NAYY 4x150 SE | 33 | 34 | 0.029205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2422-26_0_3_line_38 | NAYY 4x150 SE | 36 | 37 | 0.036808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2422-26_0_3_line_39 | NAYY 4x150 SE | 38 | 39 | 0.056335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2422-26_0_3_line_40 | NAYY 4x150 SE | 40 | 43 | 0.05714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2422-26_0_3_line_41 | NAYY 4x150 SE | 41 | 42 | 0.010825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2422-26_0_3_line_42 | NAYY 4x150 SE | 41 | 43 | 0.022323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2422-26_0_3_trafo_42 | 0.25 MVA 20/0.4 kV | 44 | 38 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2619763.7461 | 1240564.0471 | 2619763.3907 | 1240561.1372 | 2619759.4034 | 1240546.0034 | 2619747.2337 | 1240517.623 | 2619746.5826 | 1240513.0615
1 | 2619764.2568 | 1240584.9327 | 2619764.6568 | 1240571.5034 | 2619763.7461 | 1240564.0471
2 | 2619763.8131 | 1240477.4232 | 2619755.1936 | 1240493.1341 | 2619749.0562 | 1240501.6079 | 2619746.1032 | 1240509.7032 | 2619746.5826 | 1240513.0615
3 | 2619764.2568 | 1240584.9327 | 2619759.6223 | 1240623.5304
4 | 2619764.2568 | 1240584.9327 | 2619803.7732 | 1240579.4717 | 2619817.2406 | 1240580.8175
5 | 2619770.9023 | 1240464.5016 | 2619763.8131 | 1240477.4232
6 | 2619759.6223 | 1240623.5304 | 2619780.1232 | 1240620.5364
7 | 2619884.8914 | 1240605.236 | 2619881.708 | 1240596.2754 | 2619875.4185 | 1240589.1277 | 2619863.5186 | 1240586.5641 | 2619851.8099 | 1240585.6133 | 2619828.5194 | 1240581.9445 | 2619817.2406 | 1240580.8175
8 | 2619770.9023 | 1240464.5016 | 2619746.5896 | 1240446.6676
9 | 2619770.9023 | 1240464.5016 | 2619793.3343 | 1240437.7372 | 2619806.9753 | 1240421.6058 | 2619814.0908 | 1240414.6585 | 2619819.9773 | 1240413.4662 | 2619843.6342 | 1240404.9508
10 | 2619884.8914 | 1240605.236 | 2619891.9032 | 1240604.37 | 2619896.8274 | 1240603.7639 | 2619908.483 | 1240602.5021 | 2619917.3669 | 1240602.5318
11 | 2619746.5896 | 1240446.6676 | 2619739.0041 | 1240441.1034 | 2619714.2779 | 1240417.316
12 | 2619843.6342 | 1240404.9508 | 2619867.8075 | 1240438.1086
13 | 2619843.6342 | 1240404.9508 | 2619851.4033 | 1240401.5412 | 2619857.1415 | 1240399.4924 | 2619867.579 | 1240396.3824
14 | 2619917.3669 | 1240602.5318 | 2619926.1283 | 1240603.0392 | 2619930.1663 | 1240603.6872
15 | 2619917.3669 | 1240602.5318 | 2619918.9524 | 1240596.4555 | 2619921.7695 | 1240590.6057 | 2619929.9913 | 1240585.1743 | 2619940.0512 | 1240579.4933 | 2619958.3766 | 1240568.8925 | 2619985.3669 | 1240551.5722
16 | 2620080.7596 | 1240534.2158 | 2620075.6592 | 1240533.5426
17 | 2620080.7596 | 1240534.2158 | 2620086.0537 | 1240534.9146
18 | 2620075.6592 | 1240533.5426 | 2620063.8525 | 1240531.9843
19 | 2620097.0105 | 1240536.3608 | 2620086.0537 | 1240534.9146
20 | 2620063.8525 | 1240531.9843 | 2620051.9997 | 1240530.4198
21 | 2620097.0105 | 1240536.3608 | 2620100.992 | 1240513.8068
22 | 2620097.0105 | 1240536.3608 | 2620118.0072 | 1240540.7991
23 | 2620047.4779 | 1240529.823 | 2620051.9997 | 1240530.4198
24 | 2620101.2964 | 1240512.0823 | 2620101.2964 | 1240512.0823 | 2620100.992 | 1240513.8068
25 | 2620137.9013 | 1240545.0044 | 2620118.0072 | 1240540.7991
26 | 2620118.0072 | 1240540.7991 | 2620120.4071 | 1240571.2617
27 | 2620006.0983 | 1240538.3002 | 2620021.4478 | 1240531.3364 | 2620032.0416 | 1240528.8593 | 2620047.4779 | 1240529.823
28 | 2620115.6324 | 1240514.232 | 2620101.2964 | 1240512.0823
29 | 2620137.9013 | 1240545.0044 | 2620141.894 | 1240545.9949
30 | 2620137.9013 | 1240545.0044 | 2620146.5028 | 1240536.9062 | 2620146.9802 | 1240536.7441
31 | 2620014.8702 | 1240500.1215 | 2620010.0664 | 1240509.2249
32 | 2620006.0983 | 1240538.3002 | 2620004.1146 | 1240530.1218 | 2620006.5974 | 1240515.7989 | 2620010.0664 | 1240509.2249
33 | 2620006.0983 | 1240538.3002 | 2620005.8276 | 1240538.4735
34 | 2619985.3669 | 1240551.5722 | 2620005.8276 | 1240538.4735
35 | 2620115.6324 | 1240514.232 | 2620215.6105 | 1240260.89
36 | 2620141.894 | 1240545.9949 | 2620168.9156 | 1240552.6987
37 | 2620168.9156 | 1240552.6987 | 2620160.8929 | 1240580.7803
38 | 2619867.579 | 1240396.3824 | 2619869.5769 | 1240395.7872 | 2619875.5095 | 1240394.395 | 2619888.8555 | 1240391.9603 | 2619903.7139 | 1240389.4861
39 | 2619900.9946 | 1240483.6305 | 2619867.8075 | 1240438.1086
40 | 2619673.0995 | 1240377.7011 | 2619714.2779 | 1240417.316
41 | 2619689.1182 | 1240362.1541 | 2619696.886 | 1240354.6151
42 | 2619673.0995 | 1240377.7011 | 2619689.1182 | 1240362.1541

## bus_geodata
| x | y | coords
0 | 2619763.7461 | 1240564.0471
1 | 2619746.5826 | 1240513.0615
2 | 2619764.2568 | 1240584.9327
3 | 2619763.8131 | 1240477.4232
4 | 2619759.6223 | 1240623.5304
5 | 2619817.2406 | 1240580.8175
6 | 2619770.9023 | 1240464.5016
7 | 2619780.1232 | 1240620.5364
8 | 2619884.8914 | 1240605.236
9 | 2619746.5896 | 1240446.6676
10 | 2619843.6342 | 1240404.9508
11 | 2619917.3669 | 1240602.5318
12 | 2620080.7596 | 1240534.2158
13 | 2620075.6592 | 1240533.5426
14 | 2620086.0538 | 1240534.9146
15 | 2620063.8525 | 1240531.9843
16 | 2620097.0105 | 1240536.3608
17 | 2620051.9997 | 1240530.4198
18 | 2620100.992 | 1240513.8068
19 | 2620118.0072 | 1240540.7991
20 | 2620047.4779 | 1240529.823
21 | 2620101.2964 | 1240512.0823
22 | 2620137.9013 | 1240545.0044
23 | 2620120.4071 | 1240571.2617
24 | 2620010.0664 | 1240509.2249
25 | 2620014.8702 | 1240500.1215
26 | 2620006.0983 | 1240538.3002
27 | 2620005.8276 | 1240538.4735
28 | 2619985.3669 | 1240551.5722
29 | 2620115.6324 | 1240514.232
30 | 2620141.894 | 1240545.9949
31 | 2620146.9802 | 1240536.7441
32 | 2619930.1663 | 1240603.6872
33 | 2620168.9156 | 1240552.6987
34 | 2620160.8929 | 1240580.7803
35 | 2620215.6105 | 1240260.89
36 | 2619903.7139 | 1240389.4861
37 | 2619867.579 | 1240396.3824
38 | 2619867.8075 | 1240438.1086
39 | 2619900.9946 | 1240483.6305
40 | 2619714.2779 | 1240417.316
41 | 2619689.1182 | 1240362.1541
42 | 2619696.886 | 1240354.6151
43 | 2619673.0995 | 1240377.7011
44 | 2619843.6342 | 1240404.9508

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98436 | -0.10923 | 0.00013102 | 3.2836e-05
1 | 0.98596 | -0.097954 | 0.00018139 | 4.5461e-05
2 | 0.98375 | -0.1136 | 0 | 0
3 | 0.98716 | -0.089511 | 0.023894 | 0.0059884
4 | 0.98338 | -0.11623 | 0 | 0
5 | 0.98242 | -0.12294 | 0.000171 | 4.2857e-05
6 | 0.98786 | -0.084634 | 0 | 0
7 | 0.98318 | -0.11763 | 0.0065493 | 0.0016414
8 | 0.98051 | -0.13653 | 0 | 0
9 | 0.98562 | -0.10047 | 0.013309 | 0.0033356
10 | 0.99602 | -0.027531 | 0 | 0
11 | 0.9797 | -0.14224 | 0 | 0
12 | 0.9723 | -0.19527 | 0.00091443 | 0.00022918
13 | 0.97243 | -0.19436 | 0.0021355 | 0.00053521
14 | 0.97218 | -0.19615 | 0.0021302 | 0.00053389
15 | 0.97275 | -0.192 | 0.0015747 | 0.00039465
16 | 0.97196 | -0.19774 | 0 | 0
17 | 0.97311 | -0.18944 | 0.0016801 | 0.00042107
18 | 0.97173 | -0.19938 | 0.00097957 | 0.0002455
19 | 0.97174 | -0.19929 | 0.0016063 | 0.00040257
20 | 0.97326 | -0.18838 | 0.002223 | 0.00055713
21 | 0.97172 | -0.19949 | 0.00098495 | 0.00024685
22 | 0.97162 | -0.20019 | 0 | 0
23 | 0.9717 | -0.19963 | 0.0010486 | 0.00026281
24 | 0.97466 | -0.17831 | 0.001239 | 0.00031053
25 | 0.97463 | -0.1785 | 0.0017622 | 0.00044165
26 | 0.97479 | -0.17735 | 0 | 0
27 | 0.9748 | -0.17726 | 0.0027091 | 0.00067896
28 | 0.97587 | -0.16961 | 0 | 0
29 | 0.97162 | -0.20022 | 0.0014791 | 0.0003707
30 | 0.9716 | -0.20033 | 0.0016481 | 0.00041304
31 | 0.9716 | -0.2003 | 0.00084478 | 0.00021172
32 | 0.97964 | -0.14274 | 0.003684 | 0.00092329
33 | 0.97153 | -0.20083 | 0.00085316 | 0.00021382
34 | 0.9715 | -0.20108 | 0.00081877 | 0.0002052
35 | 0.9703 | -0.20977 | 0.0032977 | 0.00082648
36 | 0.99521 | -0.033208 | 0.0028661 | 0.00071832
37 | 0.99537 | -0.032144 | 0.015123 | 0.0037902
38 | 1 | 0 | -0.13894 | -0.034894
39 | 0.99982 | -0.001232 | 0.002188 | 0.00054838
40 | 0.98322 | -0.11754 | 0.03537 | 0.0088645
41 | 0.98292 | -0.11962 | 0.00068445 | 0.00017154
42 | 0.98289 | -0.11983 | 0.0018503 | 0.00046372
43 | 0.98301 | -0.11904 | 0 | 0
44 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.040845 | -0.010273 | 0.040909 | 0.010297 | 6.4338e-05 | 2.3368e-05 | 0.061756 | 0.061756 | 0.061756 | 0.98436 | -0.10923 | 0.98596 | -0.097954 | 11.4364
1 | 0.040714 | 0.010241 | -0.040689 | -0.010232 | 2.4766e-05 | 8.9931e-06 | 0.061558 | 0.061559 | 0.061559 | 0.98436 | -0.10923 | 0.98375 | -0.1136 | 11.3997
2 | -0.041091 | -0.010342 | 0.041139 | 0.01036 | 4.849e-05 | 1.7618e-05 | 0.06203 | 0.062029 | 0.06203 | 0.98596 | -0.097954 | 0.98716 | -0.089511 | 11.487
3 | 0.0065529 | 0.0016421 | -0.0065506 | -0.0016416 | 2.3835e-06 | 4.2331e-07 | 0.0099119 | 0.0099121 | 0.0099121 | 0.98375 | -0.1136 | 0.98338 | -0.11623 | 3.6711
4 | 0.034136 | 0.0085895 | -0.034092 | -0.0085737 | 4.4463e-05 | 1.5746e-05 | 0.051647 | 0.051647 | 0.051647 | 0.98375 | -0.1136 | 0.98242 | -0.12294 | 9.5643
5 | -0.065033 | -0.016348 | 0.065077 | 0.016365 | 4.4205e-05 | 1.6625e-05 | 0.098046 | 0.098046 | 0.098046 | 0.98716 | -0.089511 | 0.98786 | -0.084634 | 18.1568
6 | 0.0065506 | 0.0016416 | -0.0065493 | -0.0016414 | 1.2702e-06 | 2.2574e-07 | 0.0099121 | 0.0099122 | 0.0099122 | 0.98338 | -0.11623 | 0.98318 | -0.11763 | 3.6712
7 | 0.033921 | 0.0085309 | -0.033857 | -0.0085082 | 6.4153e-05 | 2.2706e-05 | 0.051388 | 0.051389 | 0.051389 | 0.98242 | -0.12294 | 0.98051 | -0.13653 | 9.5165
8 | 0.051417 | 0.012912 | -0.051304 | -0.012868 | 0.00011289 | 4.3034e-05 | 0.077459 | 0.077459 | 0.077459 | 0.98786 | -0.084634 | 0.98562 | -0.10047 | 28.6886
9 | -0.11649 | -0.029276 | 0.11743 | 0.029633 | 0.00093355 | 0.00035655 | 0.17551 | 0.1755 | 0.17551 | 0.98786 | -0.084634 | 0.99602 | -0.027531 | 32.501
10 | 0.033857 | 0.0085082 | -0.03383 | -0.0084986 | 2.6889e-05 | 9.5192e-06 | 0.051389 | 0.051389 | 0.051389 | 0.98051 | -0.13653 | 0.9797 | -0.14224 | 9.5165
11 | 0.037995 | 0.0095329 | -0.037905 | -0.009499 | 8.9776e-05 | 3.3973e-05 | 0.057366 | 0.057366 | 0.057366 | 0.98562 | -0.10047 | 0.98322 | -0.11754 | 21.2468
12 | -0.13543 | -0.034145 | 0.13595 | 0.034346 | 0.00052445 | 0.00020064 | 0.2024 | 0.2024 | 0.2024 | 0.99602 | -0.027531 | 1 | 0 | 37.481
13 | 0.018001 | 0.0045123 | -0.017989 | -0.0045082 | 1.1494e-05 | 4.0895e-06 | 0.026893 | 0.026893 | 0.026893 | 0.99602 | -0.027531 | 0.99537 | -0.032144 | 9.9604
14 | 0.0036842 | 0.00092322 | -0.003684 | -0.00092329 | 2.5138e-07 | -6.5312e-08 | 0.0055957 | 0.0055957 | 0.0055957 | 0.9797 | -0.14224 | 0.97964 | -0.14274 | 2.0725
15 | 0.030145 | 0.0075754 | -0.030031 | -0.0075325 | 0.00011439 | 4.2901e-05 | 0.045793 | 0.045794 | 0.045794 | 0.9797 | -0.14224 | 0.97587 | -0.16961 | 16.9607
16 | -0.016619 | -0.0041611 | 0.016621 | 0.0041619 | 2.0765e-06 | 7.3483e-07 | 0.025433 | 0.025433 | 0.025433 | 0.9723 | -0.19527 | 0.97243 | -0.19436 | 9.4195
17 | 0.015705 | 0.003932 | -0.015703 | -0.0039313 | 1.9247e-06 | 6.7404e-07 | 0.024033 | 0.024033 | 0.024033 | 0.9723 | -0.19527 | 0.97218 | -0.19615 | 8.9012
18 | -0.018757 | -0.0046971 | 0.018763 | 0.0046993 | 6.1213e-06 | 2.2065e-06 | 0.028701 | 0.0287 | 0.028701 | 0.97243 | -0.19436 | 0.97275 | -0.192 | 10.6298
19 | 0.013573 | 0.0033974 | -0.01357 | -0.0033964 | 2.9758e-06 | 1.0075e-06 | 0.020773 | 0.020773 | 0.020773 | 0.97218 | -0.19615 | 0.97196 | -0.19774 | 7.6937
20 | -0.020338 | -0.0050939 | 0.020345 | 0.0050966 | 7.22e-06 | 2.6284e-06 | 0.031109 | 0.031109 | 0.031109 | 0.97275 | -0.192 | 0.97311 | -0.18944 | 11.5219
21 | 0.0067478 | 0.0016882 | -0.0067462 | -0.0016879 | 1.5248e-06 | 3.0269e-07 | 0.010329 | 0.010329 | 0.010329 | 0.97196 | -0.19774 | 0.97173 | -0.19938 | 3.8257
22 | 0.0068219 | 0.0017082 | -0.0068205 | -0.0017079 | 1.4606e-06 | 2.9584e-07 | 0.010443 | 0.010444 | 0.010444 | 0.97196 | -0.19774 | 0.97174 | -0.19929 | 3.868
23 | -0.022025 | -0.0055176 | 0.022028 | 0.0055188 | 3.2281e-06 | 1.1849e-06 | 0.033678 | 0.033678 | 0.033678 | 0.97311 | -0.18944 | 0.97326 | -0.18838 | 12.4734
24 | 0.0057667 | 0.0014424 | -0.0057666 | -0.0014423 | 8.5192e-08 | 1.1072e-08 | 0.0088295 | 0.0088295 | 0.0088295 | 0.97173 | -0.19938 | 0.97172 | -0.19949 | 3.2702
25 | 0.0041655 | 0.0010429 | -0.004165 | -0.001043 | 5.1618e-07 | -5.3337e-08 | 0.0063782 | 0.0063783 | 0.0063783 | 0.97174 | -0.19929 | 0.97162 | -0.20019 | 2.3623
26 | 0.0010487 | 0.00026245 | -0.0010486 | -0.00026281 | 4.9164e-08 | -3.5962e-07 | 0.0016057 | 0.0016058 | 0.0016058 | 0.97174 | -0.19929 | 0.9717 | -0.19963 | 0.59474
27 | -0.024251 | -0.006076 | 0.024288 | 0.0060897 | 3.7058e-05 | 1.3716e-05 | 0.037077 | 0.037077 | 0.037077 | 0.97326 | -0.18838 | 0.97479 | -0.17735 | 13.7322
28 | 0.0047816 | 0.0011955 | -0.0047812 | -0.0011955 | 4.8485e-07 | 6.9258e-09 | 0.0073212 | 0.0073213 | 0.0073213 | 0.97172 | -0.19949 | 0.97162 | -0.20022 | 2.7116
29 | 0.0033202 | 0.00083139 | -0.0033201 | -0.00083142 | 6.6365e-08 | -2.5424e-08 | 0.0050846 | 0.0050846 | 0.0050846 | 0.97162 | -0.20019 | 0.9716 | -0.20033 | 1.8832
30 | 0.00084479 | 0.00021157 | -0.00084478 | -0.00021172 | 1.2866e-08 | -1.4761e-07 | 0.0012937 | 0.0012938 | 0.0012938 | 0.97162 | -0.20019 | 0.9716 | -0.2003 | 0.47918
31 | 0.0017622 | 0.00044154 | -0.0017622 | -0.00044165 | 4.649e-08 | -1.104e-07 | 0.0026904 | 0.0026904 | 0.0026904 | 0.97466 | -0.17831 | 0.97463 | -0.1785 | 0.99645
32 | -0.0030012 | -0.00075206 | 0.0030016 | 0.00075184 | 3.9805e-07 | -2.2564e-07 | 0.004582 | 0.0045818 | 0.004582 | 0.97466 | -0.17831 | 0.97479 | -0.17735 | 1.697
33 | -0.02729 | -0.0068415 | 0.02729 | 0.0068416 | 3.4809e-07 | 1.2987e-07 | 0.041659 | 0.041659 | 0.041659 | 0.97479 | -0.17735 | 0.9748 | -0.17726 | 15.4291
34 | -0.029999 | -0.0075206 | 0.030031 | 0.0075325 | 3.1791e-05 | 1.1924e-05 | 0.045794 | 0.045794 | 0.045794 | 0.9748 | -0.17726 | 0.97587 | -0.16961 | 16.9607
35 | 0.0033021 | 0.00082479 | -0.0032977 | -0.00082648 | 4.3456e-06 | -1.6972e-06 | 0.005056 | 0.0050573 | 0.0050573 | 0.97162 | -0.20022 | 0.9703 | -0.20977 | 1.8731
36 | 0.0016721 | 0.00041837 | -0.001672 | -0.00041867 | 1.1391e-07 | -3.0096e-07 | 0.0025606 | 0.0025607 | 0.0025607 | 0.9716 | -0.20033 | 0.97153 | -0.20083 | 0.9484
37 | 0.0008188 | 0.00020485 | -0.00081877 | -0.0002052 | 2.8659e-08 | -3.5061e-07 | 0.001254 | 0.0012541 | 0.0012541 | 0.97153 | -0.20083 | 0.9715 | -0.20108 | 0.46448
38 | -0.0028661 | -0.00071832 | 0.0028665 | 0.000718 | 4.2177e-07 | -3.1613e-07 | 0.0042853 | 0.0042852 | 0.0042853 | 0.99521 | -0.033208 | 0.99537 | -0.032144 | 1.5872
39 | 0.0021884 | 0.00054778 | -0.002188 | -0.00054838 | 3.7274e-07 | -5.9558e-07 | 0.0032562 | 0.0032564 | 0.0032564 | 1 | 0 | 0.99982 | -0.001232 | 1.2061
40 | 0.0025355 | 0.00063442 | -0.002535 | -0.00063494 | 5.2495e-07 | -5.2262e-07 | 0.0038369 | 0.0038372 | 0.0038372 | 0.98322 | -0.11754 | 0.98301 | -0.11904 | 1.4212
41 | 0.0018503 | 0.00046361 | -0.0018503 | -0.00046372 | 5.2999e-08 | -1.1682e-07 | 0.0028011 | 0.0028012 | 0.0028012 | 0.98292 | -0.11962 | 0.98289 | -0.11983 | 1.0375
42 | -0.0025348 | -0.00063515 | 0.002535 | 0.00063494 | 2.051e-07 | -2.0408e-07 | 0.0038373 | 0.0038372 | 0.0038373 | 0.98292 | -0.11962 | 0.98301 | -0.11904 | 1.4212

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.15589 | 0.039141

## res_load
| p_mw | q_mvar
0 | 0.00013102 | 3.2836e-05
1 | 0.00018139 | 4.5461e-05
2 | 0.023894 | 0.0059884
3 | 0.000171 | 4.2857e-05
4 | 0.0065493 | 0.0016414
5 | 0.013309 | 0.0033356
6 | 0.00091443 | 0.00022918
7 | 0.0021355 | 0.00053521
8 | 0.0021302 | 0.00053389
9 | 0.0015747 | 0.00039465
10 | 0.0016801 | 0.00042107
11 | 0.00097957 | 0.0002455
12 | 0.0016063 | 0.00040257
13 | 0.002223 | 0.00055713
14 | 0.00098495 | 0.00024685
15 | 0.0010486 | 0.00026281
16 | 0.001239 | 0.00031053
17 | 0.0017622 | 0.00044165
18 | 0.0027091 | 0.00067896
19 | 0.0014791 | 0.0003707
20 | 0.0016481 | 0.00041304
21 | 0.00084478 | 0.00021172
22 | 0.003684 | 0.00092329
23 | 0.00085316 | 0.00021382
24 | 0.00081877 | 0.0002052
25 | 0.0032977 | 0.00082648
26 | 0.0028661 | 0.00071832
27 | 0.015123 | 0.0037902
28 | 0.016948 | 0.0042475
29 | 0.002188 | 0.00054838
30 | 0.03537 | 0.0088645
31 | 0.00068445 | 0.00017154
32 | 0.0018503 | 0.00046372

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1