## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2427-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2427-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2427-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2427-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2427-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2427-1_0_4_node_43 | 0.4 | n |  | TRUE
6 | bus_LV_2427-1_0_4_node_41 | 0.4 | n |  | TRUE
7 | bus_LV_2427-1_0_4_node_71 | 0.4 | n |  | TRUE
8 | bus_LV_2427-1_0_4_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_2427-1_0_4_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_2427-1_0_4_node_44 | 0.4 | n |  | TRUE
11 | bus_LV_2427-1_0_4_node_91 | 0.4 | n |  | TRUE
12 | bus_LV_2427-1_0_4_node_72 | 0.4 | n |  | TRUE
13 | bus_LV_2427-1_0_4_node_120 | 0.4 | n |  | TRUE
14 | bus_LV_2427-1_0_4_node_45 | 0.4 | n |  | TRUE
15 | bus_LV_2427-1_0_4_node_5 | 0.4 | n |  | TRUE
16 | bus_LV_2427-1_0_4_node_6 | 0.4 | n |  | TRUE
17 | bus_LV_2427-1_0_4_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_2427-1_0_4_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_2427-1_0_4_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_2427-1_0_4_node_48 | 0.4 | n |  | TRUE
21 | bus_LV_2427-1_0_4_node_49 | 0.4 | n |  | TRUE
22 | bus_LV_2427-1_0_4_node_110 | 0.4 | n |  | TRUE
23 | bus_LV_2427-1_0_4_node_122 | 0.4 | n |  | TRUE
24 | bus_LV_2427-1_0_4_node_65 | 0.4 | n |  | TRUE
25 | bus_LV_2427-1_0_4_node_10 | 0.4 | n |  | TRUE
26 | bus_LV_2427-1_0_4_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_2427-1_0_4_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_2427-1_0_4_node_66 | 0.4 | n |  | TRUE
29 | bus_LV_2427-1_0_4_node_67 | 0.4 | n |  | TRUE
30 | bus_LV_2427-1_0_4_node_68 | 0.4 | n |  | TRUE
31 | bus_LV_2427-1_0_4_node_69 | 0.4 | n |  | TRUE
32 | bus_LV_2427-1_0_4_node_70 | 0.4 | n |  | TRUE
33 | bus_LV_2427-1_0_4_node_126 | 0.4 | n |  | TRUE
34 | bus_LV_2427-1_0_4_node_123 | 0.4 | n |  | TRUE
35 | bus_LV_2427-1_0_4_node_115 | 0.4 | n |  | TRUE
36 | bus_LV_2427-1_0_4_node_73 | 0.4 | n |  | TRUE
37 | bus_LV_2427-1_0_4_node_74 | 0.4 | n |  | TRUE
38 | bus_LV_2427-1_0_4_node_75 | 0.4 | n |  | TRUE
39 | bus_LV_2427-1_0_4_node_76 | 0.4 | n |  | TRUE
40 | bus_LV_2427-1_0_4_node_46 | 0.4 | n |  | TRUE
41 | bus_LV_2427-1_0_4_node_107 | 0.4 | n |  | TRUE
42 | bus_LV_2427-1_0_4_node_86 | 0.4 | n |  | TRUE
43 | bus_LV_2427-1_0_4_node_87 | 0.4 | n |  | TRUE
44 | bus_LV_2427-1_0_4_node_88 | 0.4 | n |  | TRUE
45 | bus_LV_2427-1_0_4_node_89 | 0.4 | n |  | TRUE
46 | bus_LV_2427-1_0_4_node_90 | 0.4 | n |  | TRUE
47 | bus_LV_2427-1_0_4_node_127 | 0.4 | n |  | TRUE
48 | bus_LV_2427-1_0_4_node_137 | 0.4 | n |  | TRUE
49 | bus_LV_2427-1_0_4_node_124 | 0.4 | n |  | TRUE
50 | bus_LV_2427-1_0_4_node_116 | 0.4 | n |  | TRUE
51 | bus_LV_2427-1_0_4_node_117 | 0.4 | n |  | TRUE
52 | bus_LV_2427-1_0_4_node_140 | 0.4 | n |  | TRUE
53 | bus_LV_2427-1_0_4_node_125 | 0.4 | n |  | TRUE
54 | bus_LV_2427-1_0_4_node_58 | 0.4 | n |  | TRUE
55 | bus_LV_2427-1_0_4_node_56 | 0.4 | n |  | TRUE
56 | bus_LV_2427-1_0_4_node_111 | 0.4 | n |  | TRUE
57 | bus_LV_2427-1_0_4_node_57 | 0.4 | n |  | TRUE
58 | bus_LV_2427-1_0_4_node_13 | 0.4 | n |  | TRUE
59 | bus_LV_2427-1_0_4_node_105 | 0.4 | n |  | TRUE
60 | bus_LV_2427-1_0_4_node_15 | 0.4 | n |  | TRUE
61 | bus_LV_2427-1_0_4_node_84 | 0.4 | n |  | TRUE
62 | bus_LV_2427-1_0_4_node_82 | 0.4 | n |  | TRUE
63 | bus_LV_2427-1_0_4_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_2427-1_0_4_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_2427-1_0_4_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_2427-1_0_4_node_138 | 0.4 | n |  | TRUE
67 | bus_LV_2427-1_0_4_node_93 | 0.4 | n |  | TRUE
68 | bus_LV_2427-1_0_4_node_62 | 0.4 | n |  | TRUE
69 | bus_LV_2427-1_0_4_node_113 | 0.4 | n |  | TRUE
70 | bus_LV_2427-1_0_4_node_60 | 0.4 | n |  | TRUE
71 | bus_LV_2427-1_0_4_node_92 | 0.4 | n |  | TRUE
72 | bus_LV_2427-1_0_4_node_94 | 0.4 | n |  | TRUE
73 | bus_LV_2427-1_0_4_node_95 | 0.4 | n |  | TRUE
74 | bus_LV_2427-1_0_4_node_96 | 0.4 | n |  | TRUE
75 | bus_LV_2427-1_0_4_node_114 | 0.4 | n |  | TRUE
76 | bus_LV_2427-1_0_4_node_121 | 0.4 | n |  | TRUE
77 | bus_LV_2427-1_0_4_node_118 | 0.4 | n |  | TRUE
78 | bus_LV_2427-1_0_4_node_119 | 0.4 | n |  | TRUE
79 | bus_LV_2427-1_0_4_node_17 | 0.4 | n |  | TRUE
80 | bus_LV_2427-1_0_4_node_18 | 0.4 | n |  | TRUE
81 | bus_LV_2427-1_0_4_node_19 | 0.4 | n |  | TRUE
82 | bus_LV_2427-1_0_4_node_20 | 0.4 | n |  | TRUE
83 | bus_LV_2427-1_0_4_node_21 | 0.4 | n |  | TRUE
84 | bus_LV_2427-1_0_4_node_106 | 0.4 | n |  | TRUE
85 | bus_LV_2427-1_0_4_node_55 | 0.4 | n |  | TRUE
86 | bus_LV_2427-1_0_4_node_22 | 0.4 | n |  | TRUE
87 | bus_LV_2427-1_0_4_node_23 | 0.4 | n |  | TRUE
88 | bus_LV_2427-1_0_4_node_24 | 0.4 | n |  | TRUE
89 | bus_LV_2427-1_0_4_node_25 | 0.4 | n |  | TRUE
90 | bus_LV_2427-1_0_4_node_26 | 0.4 | n |  | TRUE
91 | bus_LV_2427-1_0_4_node_27 | 0.4 | n |  | TRUE
92 | bus_LV_2427-1_0_4_node_134 | 0.4 | n |  | TRUE
93 | bus_LV_2427-1_0_4_node_98 | 0.4 | n |  | TRUE
94 | bus_LV_2427-1_0_4_node_29 | 0.4 | n |  | TRUE
95 | bus_LV_2427-1_0_4_node_97 | 0.4 | n |  | TRUE
96 | bus_LV_2427-1_0_4_node_28 | 0.4 | n |  | TRUE
97 | bus_LV_2427-1_0_4_node_30 | 0.4 | n |  | TRUE
98 | bus_LV_2427-1_0_4_node_31 | 0.4 | n |  | TRUE
99 | bus_LV_2427-1_0_4_node_32 | 0.4 | n |  | TRUE
100 | bus_LV_2427-1_0_4_node_81 | 0.4 | n |  | TRUE
101 | bus_LV_2427-1_0_4_node_36 | 0.4 | n |  | TRUE
102 | bus_LV_2427-1_0_4_node_79 | 0.4 | n |  | TRUE
103 | bus_LV_2427-1_0_4_node_132 | 0.4 | n |  | TRUE
104 | bus_LV_2427-1_0_4_node_34 | 0.4 | n |  | TRUE
105 | bus_LV_2427-1_0_4_node_33 | 0.4 | n |  | TRUE
106 | bus_LV_2427-1_0_4_node_35 | 0.4 | n |  | TRUE
107 | bus_LV_2427-1_0_4_node_37 | 0.4 | n |  | TRUE
108 | bus_LV_2427-1_0_4_node_38 | 0.4 | n |  | TRUE
109 | bus_LV_2427-1_0_4_node_39 | 0.4 | n |  | TRUE
110 | bus_LV_2427-1_0_4_node_40 | 0.4 | n |  | TRUE
111 | bus_LV_2427-1_0_4_node_42 | 0.4 | n |  | TRUE
112 | bus_LV_2427-1_0_4_node_47 | 0.4 | n |  | TRUE
113 | bus_LV_2427-1_0_4_node_85 | 0.4 | n |  | TRUE
114 | bus_LV_2427-1_0_4_node_59 | 0.4 | n |  | TRUE
115 | bus_LV_2427-1_0_4_node_61 | 0.4 | n |  | TRUE
116 | bus_LV_2427-1_0_4_node_63 | 0.4 | n |  | TRUE
117 | bus_LV_2427-1_0_4_node_64 | 0.4 | n |  | TRUE
118 | bus_LV_2427-1_0_4_node_102 | 0.4 | n |  | TRUE
119 | bus_LV_2427-1_0_4_node_108 | 0.4 | n |  | TRUE
120 | bus_LV_2427-1_0_4_node_101 | 0.4 | n |  | TRUE
121 | bus_LV_2427-1_0_4_node_103 | 0.4 | n |  | TRUE
122 | bus_LV_2427-1_0_4_node_104 | 0.4 | n |  | TRUE
123 | bus_LV_2427-1_0_4_node_141 | 0.4 | n |  | TRUE
124 | bus_LV_2427-1_0_4_node_109 | 0.4 | n |  | TRUE
125 | bus_LV_2427-1_0_4_node_83 | 0.4 | n |  | TRUE
126 | bus_LV_2427-1_0_4_node_53 | 0.4 | n |  | TRUE
127 | bus_LV_2427-1_0_4_node_54 | 0.4 | n |  | TRUE
128 | bus_LV_2427-1_0_4_node_112 | 0.4 | n |  | TRUE
129 | bus_LV_2427-1_0_4_node_77 | 0.4 | n |  | TRUE
130 | bus_LV_2427-1_0_4_node_78 | 0.4 | n |  | TRUE
131 | bus_LV_2427-1_0_4_node_80 | 0.4 | n |  | TRUE
132 | bus_LV_2427-1_0_4_node_129 | 0.4 | n |  | TRUE
133 | bus_LV_2427-1_0_4_node_130 | 0.4 | n |  | TRUE
134 | bus_LV_2427-1_0_4_node_100 | 0.4 | n |  | TRUE
135 | bus_LV_2427-1_0_4_node_99 | 0.4 | n |  | TRUE
136 | bus_LV_2427-1_0_4_node_135 | 0.4 | n |  | TRUE
137 | bus_LV_2427-1_0_4_node_136 | 0.4 | n |  | TRUE
138 | bus_LV_2427-1_0_4_node_131 | 0.4 | n |  | TRUE
139 | bus_LV_2427-1_0_4_node_139 | 0.4 | n |  | TRUE
140 | bus_MV_333_0_node_112 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2427-1_0_4_load_0 | 0 | 0.0010404 | 0.00026076 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2427-1_0_4_load_1 | 1 | 0.000479 | 0.00012005 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2427-1_0_4_load_2 | 2 | 0.00078825 | 0.00019755 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2427-1_0_4_load_4 | 4 | 0.0011234 | 0.00028154 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2427-1_0_4_load_43 | 5 | 0.00088772 | 0.00022248 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2427-1_0_4_load_41 | 6 | 0.00065431 | 0.00016398 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2427-1_0_4_load_71 | 7 | 0.0011745 | 0.00029436 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2427-1_0_4_load_16 | 8 | 0.00076454 | 0.00019161 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2427-1_0_4_load_44 | 10 | 0.00021278 | 5.3328e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2427-1_0_4_load_91 | 11 | 0.0017814 | 0.00044645 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2427-1_0_4_load_72 | 12 | 0.00046375 | 0.00011623 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2427-1_0_4_load_120 | 13 | 0.0005748 | 0.00014406 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2427-1_0_4_load_45 | 14 | 0.00031836 | 7.9788e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2427-1_0_4_load_5 | 15 | 0.0010318 | 0.0002586 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2427-1_0_4_load_6 | 16 | 0.00071833 | 0.00018003 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2427-1_0_4_load_8 | 18 | 0.00064278 | 0.0001611 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2427-1_0_4_load_9 | 19 | 0.00050443 | 0.00012642 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2427-1_0_4_load_48 | 20 | 0.0006425 | 0.00016103 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2427-1_0_4_load_122 | 23 | 0.00087916 | 0.00022034 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2427-1_0_4_load_65 | 24 | 0.00085325 | 0.00021385 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2427-1_0_4_load_10 | 25 | 0.0010212 | 0.00025595 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2427-1_0_4_load_11 | 26 | 0.00061324 | 0.00015369 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2427-1_0_4_load_66 | 28 | 0.00060078 | 0.00015057 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2427-1_0_4_load_67 | 29 | 0.00090305 | 0.00022633 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2427-1_0_4_load_68 | 30 | 0.0019011 | 0.00047647 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2427-1_0_4_load_126 | 33 | 0.0016724 | 0.00041914 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2427-1_0_4_load_123 | 34 | 0.0021994 | 0.00055121 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2427-1_0_4_load_115 | 35 | 0.0010278 | 0.00025759 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2427-1_0_4_load_73 | 36 | 0.0018204 | 0.00045624 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2427-1_0_4_load_74 | 37 | 0.001368 | 0.00034286 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2427-1_0_4_load_75 | 38 | 0.001026 | 0.00025715 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2427-1_0_4_load_76 | 39 | 0.0011966 | 0.00029991 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2427-1_0_4_load_46 | 40 | 0.00028226 | 7.0741e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2427-1_0_4_load_107 | 41 | 0.001223 | 0.00030652 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2427-1_0_4_load_86 | 42 | 0.0029951 | 0.00075064 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2427-1_0_4_load_90 | 46 | 0.0018152 | 0.00045494 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2427-1_0_4_load_127 | 47 | 0.0025305 | 0.0006342 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2427-1_0_4_load_137 | 48 | 0.0021056 | 0.0005277 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2427-1_0_4_load_117 | 51 | 0.00051969 | 0.00013025 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2427-1_0_4_load_140 | 52 | 0.0017555 | 0.00043997 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2427-1_0_4_load_125 | 53 | 0.0023532 | 0.00058976 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2427-1_0_4_load_58 | 54 | 0.00051665 | 0.00012949 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2427-1_0_4_load_56 | 55 | 0.00038361 | 9.6142e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2427-1_0_4_load_111 | 56 | 0.001253 | 0.00031404 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2427-1_0_4_load_57 | 57 | 0.0017861 | 0.00044764 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2427-1_0_4_load_13 | 58 | 0.0010953 | 0.00027452 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2427-1_0_4_load_105 | 59 | 0.0022584 | 0.00056601 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2427-1_0_4_load_15 | 60 | 0.0024752 | 0.00062035 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2427-1_0_4_load_82 | 62 | 0.0031103 | 0.00077951 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2427-1_0_4_load_50 | 63 | 0.00071807 | 0.00017996 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2427-1_0_4_load_138 | 66 | 0.00066137 | 0.00016576 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2427-1_0_4_load_93 | 67 | 0.00088899 | 0.0002228 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2427-1_0_4_load_113 | 69 | 0.00097719 | 0.00024491 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2427-1_0_4_load_60 | 70 | 0.0014293 | 0.00035822 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2427-1_0_4_load_92 | 71 | 0.00029636 | 7.4275e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2427-1_0_4_load_94 | 72 | 0.00044404 | 0.00011129 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2427-1_0_4_load_95 | 73 | 0.00036941 | 9.2582e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2427-1_0_4_load_96 | 74 | 0.00037934 | 9.5072e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2427-1_0_4_load_121 | 76 | 0.00064275 | 0.00016109 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2427-1_0_4_load_118 | 77 | 0.0012642 | 0.00031683 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2427-1_0_4_load_17 | 79 | 0.0010138 | 0.00025407 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2427-1_0_4_load_18 | 80 | 0.00073194 | 0.00018344 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2427-1_0_4_load_19 | 81 | 0.00085226 | 0.0002136 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2427-1_0_4_load_20 | 82 | 0.00070858 | 0.00017759 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2427-1_0_4_load_21 | 83 | 0.00079524 | 0.0001993 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2427-1_0_4_load_106 | 84 | 0.0014289 | 0.00035812 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2427-1_0_4_load_22 | 86 | 0.0040093 | 0.0010048 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2427-1_0_4_load_23 | 87 | 0.020839 | 0.0052228 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2427-1_0_4_load_25 | 89 | 0.00036483 | 9.1435e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2427-1_0_4_load_26 | 90 | 0.00055393 | 0.00013883 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2427-1_0_4_load_27 | 91 | 0.0010346 | 0.0002593 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2427-1_0_4_load_134 | 92 | 0.00053338 | 0.00013368 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2427-1_0_4_load_98 | 93 | 0.0060855 | 0.0015252 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2427-1_0_4_load_29 | 94 | 0.00062866 | 0.00015756 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2427-1_0_4_load_97 | 95 | 0.0011927 | 0.00029892 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2427-1_0_4_load_28 | 96 | 0.0013392 | 0.00033564 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2427-1_0_4_load_31 | 98 | 0.0019047 | 0.00047735 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2427-1_0_4_load_32 | 99 | 0.0039346 | 0.0009861 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2427-1_0_4_load_81 | 100 | 0.0022644 | 0.00056751 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2427-1_0_4_load_79 | 102 | 0.0035994 | 0.0009021 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2427-1_0_4_load_132 | 103 | 0.00048828 | 0.00012237 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2427-1_0_4_load_33 | 105 | 0.0019893 | 0.00049856 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2427-1_0_4_load_35 | 106 | 0.003378 | 0.0008466 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2427-1_0_4_load_37 | 107 | 0.0029245 | 0.00073295 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2427-1_0_4_load_38 | 108 | 0.002028 | 0.00050825 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2427-1_0_4_load_40 | 110 | 0.0024821 | 0.00062208 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2427-1_0_4_load_42 | 111 | 0.0024685 | 0.00061868 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2427-1_0_4_load_47 | 112 | 0.0033589 | 0.00084182 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2427-1_0_4_load_85 | 113 | 0.00051843 | 0.00012993 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2427-1_0_4_load_59 | 114 | 0.00090261 | 0.00022622 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2427-1_0_4_load_64 | 117 | 0.0034431 | 0.00086293 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2427-1_0_4_load_102 | 118 | 0.002418 | 0.00060601 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2427-1_0_4_load_108 | 119 | 0.00146 | 0.00036591 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2427-1_0_4_load_101 | 120 | 0.0010742 | 0.00026923 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2427-1_0_4_load_141 | 123 | 0.0011008 | 0.00027589 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2427-1_0_4_load_109 | 124 | 0.0012007 | 0.00030092 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2427-1_0_4_load_83 | 125 | 0.0058573 | 0.001468 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2427-1_0_4_load_53 | 126 | 0.00089211 | 0.00022358 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2427-1_0_4_load_54 | 127 | 0.00090763 | 0.00022747 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2427-1_0_4_load_112 | 128 | 0.00039639 | 9.9345e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2427-1_0_4_load_77 | 129 | 0.0023911 | 0.00059926 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2427-1_0_4_load_78 | 130 | 0.0025806 | 0.00064675 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2427-1_0_4_load_80 | 131 | 0.00026144 | 6.5524e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2427-1_0_4_load_129 | 132 | 0.00026173 | 6.5596e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2427-1_0_4_load_130 | 133 | 0.0019487 | 0.0004884 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2427-1_0_4_load_135 | 136 | 0.00086981 | 0.00021799 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2427-1_0_4_load_136 | 137 | 0.0012531 | 0.00031406 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2427-1_0_4_load_131 | 138 | 0.00055268 | 0.00013851 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2427-1_0_4_load_139 | 139 | 0.002127 | 0.00053307 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2427-1_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0046315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2427-1_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0077127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2427-1_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0074322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2427-1_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0082328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2427-1_0_4_line_4 | NAYY 4x150 SE | 3 | 7 | 0.0070076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2427-1_0_4_line_5 | NAYY 4x150 SE | 4 | 10 | 0.052097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_2427-1_0_4_line_6 | NAYY 4x150 SE | 5 | 6 | 0.02153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2427-1_0_4_line_7 | NAYY 4x150 SE | 6 | 109 | 0.017419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_2427-1_0_4_line_8 | NAYY 4x150 SE | 7 | 11 | 0.019142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2427-1_0_4_line_9 | NAYY 4x150 SE | 8 | 9 | 0.028158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2427-1_0_4_line_10 | NAYY 4x150 SE | 9 | 60 | 0.0077757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2427-1_0_4_line_11 | NAYY 4x150 SE | 10 | 14 | 0.013348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_2427-1_0_4_line_12 | NAYY 4x150 SE | 11 | 68 | 0.019632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2427-1_0_4_line_13 | NAYY 4x150 SE | 12 | 13 | 0.019369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2427-1_0_4_line_14 | NAYY 4x150 SE | 13 | 78 | 0.010509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2427-1_0_4_line_15 | NAYY 4x150 SE | 14 | 40 | 0.013363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_2427-1_0_4_line_16 | NAYY 4x150 SE | 15 | 16 | 0.015512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2427-1_0_4_line_17 | NAYY 4x150 SE | 15 | 17 | 0.020651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2427-1_0_4_line_18 | NAYY 4x150 SE | 16 | 18 | 0.02244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2427-1_0_4_line_19 | NAYY 4x150 SE | 17 | 19 | 0.02428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2427-1_0_4_line_20 | NAYY 4x150 SE | 18 | 20 | 0.0080103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2427-1_0_4_line_21 | NAYY 4x150 SE | 20 | 21 | 0.021415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2427-1_0_4_line_22 | NAYY 4x150 SE | 21 | 59 | 0.028342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2427-1_0_4_line_23 | NAYY 4x150 SE | 21 | 58 | 0.13443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2427-1_0_4_line_24 | NAYY 4x150 SE | 22 | 23 | 0.011327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_2427-1_0_4_line_25 | NAYY 4x150 SE | 22 | 24 | 0.0076106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2427-1_0_4_line_26 | NAYY 4x150 SE | 23 | 136 | 0.0056002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_2427-1_0_4_line_27 | NAYY 4x150 SE | 24 | 83 | 0.011909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2427-1_0_4_line_28 | NAYY 4x150 SE | 25 | 26 | 0.0026137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2427-1_0_4_line_29 | NAYY 4x150 SE | 26 | 27 | 0.027767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2427-1_0_4_line_30 | NAYY 4x150 SE | 27 | 54 | 0.0059249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_2427-1_0_4_line_31 | NAYY 4x150 SE | 27 | 55 | 0.014418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_2427-1_0_4_line_32 | NAYY 4x150 SE | 28 | 29 | 0.029155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2427-1_0_4_line_33 | NAYY 4x150 SE | 28 | 30 | 0.012254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2427-1_0_4_line_34 | NAYY 4x150 SE | 29 | 31 | 0.047971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2427-1_0_4_line_35 | NAYY 4x150 SE | 30 | 32 | 0.0040387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2427-1_0_4_line_36 | NAYY 4x150 SE | 31 | 33 | 0.020157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2427-1_0_4_line_37 | NAYY 4x150 SE | 31 | 34 | 0.0058906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2427-1_0_4_line_38 | NAYY 4x150 SE | 32 | 35 | 0.01561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2427-1_0_4_line_39 | NAYY 4x150 SE | 34 | 49 | 0.02583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2427-1_0_4_line_40 | NAYY 4x150 SE | 35 | 50 | 0.0064962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2427-1_0_4_line_41 | NAYY 4x150 SE | 36 | 37 | 0.018408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_2427-1_0_4_line_42 | NAYY 4x150 SE | 36 | 38 | 0.0018291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_2427-1_0_4_line_43 | NAYY 4x150 SE | 37 | 39 | 0.011411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_2427-1_0_4_line_44 | NAYY 4x150 SE | 38 | 40 | 0.064527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_2427-1_0_4_line_45 | NAYY 4x150 SE | 39 | 41 | 0.0035499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_2427-1_0_4_line_46 | NAYY 4x150 SE | 41 | 49 | 0.029008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_2427-1_0_4_line_47 | NAYY 4x150 SE | 42 | 43 | 0.049895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_2427-1_0_4_line_48 | NAYY 4x150 SE | 42 | 44 | 0.0028805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_2427-1_0_4_line_49 | NAYY 4x150 SE | 43 | 134 | 0.096754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_2427-1_0_4_line_50 | NAYY 4x150 SE | 44 | 45 | 0.031988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2427-1_0_4_line_51 | NAYY 4x150 SE | 44 | 46 | 0.020817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_2427-1_0_4_line_52 | NAYY 4x150 SE | 45 | 47 | 0.053358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2427-1_0_4_line_53 | NAYY 4x150 SE | 46 | 48 | 0.016144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
54 | LV_2427-1_0_4_line_54 | NAYY 4x150 SE | 48 | 53 | 0.0093651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_2427-1_0_4_line_55 | NAYY 4x150 SE | 49 | 53 | 0.01126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
56 | LV_2427-1_0_4_line_56 | NAYY 4x150 SE | 50 | 51 | 0.0050316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2427-1_0_4_line_57 | NAYY 4x150 SE | 51 | 52 | 0.043456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2427-1_0_4_line_58 | NAYY 4x150 SE | 54 | 56 | 0.029751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
59 | LV_2427-1_0_4_line_59 | NAYY 4x150 SE | 55 | 57 | 0.018812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
60 | LV_2427-1_0_4_line_60 | NAYY 4x150 SE | 56 | 128 | 0.039163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_2427-1_0_4_line_61 | NAYY 4x150 SE | 57 | 111 | 0.0075701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
62 | LV_2427-1_0_4_line_62 | NAYY 4x150 SE | 59 | 85 | 0.01791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2427-1_0_4_line_63 | NAYY 4x150 SE | 60 | 61 | 0.029866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2427-1_0_4_line_64 | NAYY 4x150 SE | 61 | 62 | 0.034931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2427-1_0_4_line_65 | NAYY 4x150 SE | 62 | 125 | 0.0099108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2427-1_0_4_line_66 | NAYY 4x150 SE | 63 | 64 | 0.0099298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2427-1_0_4_line_67 | NAYY 4x150 SE | 64 | 65 | 0.032819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2427-1_0_4_line_68 | NAYY 4x150 SE | 65 | 66 | 0.022329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2427-1_0_4_line_69 | NAYY 4x150 SE | 65 | 67 | 0.056798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2427-1_0_4_line_70 | NAYY 4x150 SE | 67 | 73 | 0.034158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2427-1_0_4_line_71 | NAYY 4x150 SE | 67 | 71 | 0.016105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2427-1_0_4_line_72 | NAYY 4x150 SE | 68 | 69 | 0.011711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2427-1_0_4_line_73 | NAYY 4x150 SE | 68 | 70 | 0.026424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2427-1_0_4_line_74 | NAYY 4x150 SE | 69 | 76 | 0.033739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2427-1_0_4_line_75 | NAYY 4x150 SE | 70 | 114 | 0.010513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2427-1_0_4_line_76 | NAYY 4x150 SE | 71 | 72 | 0.0085772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2427-1_0_4_line_77 | NAYY 4x150 SE | 72 | 74 | 0.0033186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2427-1_0_4_line_78 | NAYY 4x150 SE | 73 | 75 | 0.023163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2427-1_0_4_line_79 | NAYY 4x150 SE | 75 | 77 | 0.0059415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2427-1_0_4_line_80 | NAYY 4x150 SE | 76 | 78 | 0.01519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2427-1_0_4_line_81 | NAYY 4x150 SE | 77 | 78 | 0.011168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2427-1_0_4_line_82 | NAYY 4x150 SE | 79 | 80 | 0.011716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2427-1_0_4_line_83 | NAYY 4x150 SE | 79 | 81 | 0.02029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2427-1_0_4_line_84 | NAYY 4x150 SE | 80 | 82 | 0.024194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2427-1_0_4_line_85 | NAYY 4x150 SE | 81 | 83 | 0.0070046 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2427-1_0_4_line_86 | NAYY 4x150 SE | 82 | 84 | 0.001628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2427-1_0_4_line_87 | NAYY 4x150 SE | 84 | 85 | 0.016249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2427-1_0_4_line_88 | NAYY 4x150 SE | 85 | 127 | 0.01223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2427-1_0_4_line_89 | NAYY 4x150 SE | 86 | 87 | 0.076966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2427-1_0_4_line_90 | NAYY 4x150 SE | 86 | 88 | 0.012969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2427-1_0_4_line_91 | NAYY 4x150 SE | 87 | 89 | 0.0044835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2427-1_0_4_line_92 | NAYY 4x150 SE | 88 | 90 | 0.024677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
93 | LV_2427-1_0_4_line_93 | NAYY 4x150 SE | 88 | 91 | 0.020386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
94 | LV_2427-1_0_4_line_94 | NAYY 4x150 SE | 89 | 92 | 0.035183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2427-1_0_4_line_95 | NAYY 4x150 SE | 90 | 93 | 0.012706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_2427-1_0_4_line_96 | NAYY 4x150 SE | 91 | 94 | 0.010999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_2427-1_0_4_line_97 | NAYY 4x150 SE | 93 | 95 | 0.011935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_2427-1_0_4_line_98 | NAYY 4x150 SE | 94 | 96 | 0.0084925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
99 | LV_2427-1_0_4_line_99 | NAYY 4x150 SE | 95 | 135 | 0.078073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_2427-1_0_4_line_100 | NAYY 4x150 SE | 96 | 97 | 0.018553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_2427-1_0_4_line_101 | NAYY 4x150 SE | 97 | 98 | 0.019605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_2427-1_0_4_line_102 | NAYY 4x150 SE | 97 | 99 | 0.0086019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2427-1_0_4_line_103 | NAYY 4x150 SE | 98 | 100 | 0.020055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
104 | LV_2427-1_0_4_line_104 | NAYY 4x150 SE | 99 | 101 | 0.023923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2427-1_0_4_line_105 | NAYY 4x150 SE | 100 | 102 | 0.029489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
106 | LV_2427-1_0_4_line_106 | NAYY 4x150 SE | 101 | 103 | 0.0384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2427-1_0_4_line_107 | NAYY 4x150 SE | 101 | 104 | 0.005045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2427-1_0_4_line_108 | NAYY 4x150 SE | 102 | 129 | 0.0014144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
109 | LV_2427-1_0_4_line_109 | NAYY 4x150 SE | 104 | 105 | 0.01402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2427-1_0_4_line_110 | NAYY 4x150 SE | 105 | 106 | 0.021299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2427-1_0_4_line_111 | NAYY 4x150 SE | 107 | 108 | 0.00037942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2427-1_0_4_line_112 | NAYY 4x150 SE | 107 | 109 | 0.050544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2427-1_0_4_line_113 | NAYY 4x150 SE | 108 | 110 | 0.023277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2427-1_0_4_line_114 | NAYY 4x150 SE | 109 | 111 | 0.033231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
115 | LV_2427-1_0_4_line_115 | NAYY 4x150 SE | 110 | 112 | 0.025572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2427-1_0_4_line_116 | NAYY 4x150 SE | 112 | 113 | 0.005917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2427-1_0_4_line_117 | NAYY 4x150 SE | 113 | 125 | 0.022632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2427-1_0_4_line_118 | NAYY 4x150 SE | 114 | 115 | 0.045493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2427-1_0_4_line_119 | NAYY 4x150 SE | 115 | 116 | 0.012714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2427-1_0_4_line_120 | NAYY 4x150 SE | 115 | 117 | 0.061679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2427-1_0_4_line_121 | NAYY 4x150 SE | 116 | 118 | 0.0021756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2427-1_0_4_line_122 | NAYY 4x150 SE | 116 | 119 | 0.021317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_2427-1_0_4_line_123 | NAYY 4x150 SE | 118 | 120 | 0.024043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_2427-1_0_4_line_124 | NAYY 4x150 SE | 119 | 124 | 0.029823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_2427-1_0_4_line_125 | NAYY 4x150 SE | 120 | 121 | 0.046262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_2427-1_0_4_line_126 | NAYY 4x150 SE | 121 | 122 | 0.007321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_2427-1_0_4_line_127 | NAYY 4x150 SE | 122 | 123 | 0.049324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_2427-1_0_4_line_128 | NAYY 4x150 SE | 126 | 127 | 0.034812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_2427-1_0_4_line_129 | NAYY 4x150 SE | 128 | 134 | 0.055329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
130 | LV_2427-1_0_4_line_130 | NAYY 4x150 SE | 129 | 130 | 0.017352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
131 | LV_2427-1_0_4_line_131 | NAYY 4x150 SE | 130 | 131 | 0.011552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
132 | LV_2427-1_0_4_line_132 | NAYY 4x150 SE | 131 | 132 | 0.00038641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
133 | LV_2427-1_0_4_line_133 | NAYY 4x150 SE | 132 | 133 | 0.020743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
134 | LV_2427-1_0_4_line_134 | NAYY 4x150 SE | 133 | 138 | 0.016778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
135 | LV_2427-1_0_4_line_135 | NAYY 4x150 SE | 134 | 135 | 0.059348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
136 | LV_2427-1_0_4_line_136 | NAYY 4x150 SE | 136 | 137 | 0.027972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
137 | LV_2427-1_0_4_line_137 | NAYY 4x150 SE | 137 | 139 | 0.02787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
138 | LV_2427-1_0_4_line_138 | NAYY 4x150 SE | 138 | 139 | 0.0024563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2427-1_0_4_trafo_41 | 0.25 MVA 20/0.4 kV | 140 | 6 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2614501.9747 | 1238782.3918 | 2614499.7567 | 1238778.326
1 | 2614501.9747 | 1238782.3918 | 2614505.6684 | 1238789.1625
2 | 2614496.1974 | 1238771.8014 | 2614499.7567 | 1238778.326
3 | 2614509.6111 | 1238796.3898 | 2614505.6684 | 1238789.1625
4 | 2614496.1974 | 1238771.8014 | 2614497.138 | 1238764.8572
5 | 2614530.8577 | 1238843.8748 | 2614530.8577 | 1238843.8748 | 2614517.5813 | 1238810.9999 | 2614509.6111 | 1238796.3898
6 | 2614494.4083 | 1238952.988 | 2614485.2609 | 1238972.478
7 | 2614477.8602 | 1238988.2464 | 2614485.2609 | 1238972.478
8 | 2614497.138 | 1238764.8572 | 2614499.2703 | 1238749.1171 | 2614500.4818 | 1238746.0927
9 | 2614334.1982 | 1238883.201 | 2614346.2777 | 1238857.7655
10 | 2614334.1982 | 1238883.201 | 2614331.1891 | 1238890.3708
11 | 2614530.8577 | 1238843.8748 | 2614538.803 | 1238854.6008 | 2614538.803 | 1238854.6008
12 | 2614509.4015 | 1238728.7958 | 2614505.2817 | 1238734.1113 | 2614500.4818 | 1238746.0927
13 | 2614466.8564 | 1238732.1202 | 2614457.9976 | 1238714.8957
14 | 2614455.3449 | 1238704.7274 | 2614457.9976 | 1238714.8957
15 | 2614538.803 | 1238854.6008 | 2614550.3133 | 1238861.3903
16 | 2614273.4192 | 1238994.2732 | 2614259.7161 | 1238987.0031
17 | 2614291.6614 | 1239003.9515 | 2614273.4192 | 1238994.2732
18 | 2614239.893 | 1238976.4861 | 2614259.7161 | 1238987.0031
19 | 2614291.6614 | 1239003.9515 | 2614285.4714 | 1239027.4289
20 | 2614239.893 | 1238976.4861 | 2614232.8169 | 1238972.7319
21 | 2614213.8999 | 1238962.6956 | 2614232.8169 | 1238972.7319
22 | 2614213.8999 | 1238962.6956 | 2614201.0303 | 1238987.9474
23 | 2614213.8999 | 1238962.6956 | 2614192.8761 | 1238829.9174
24 | 2614277.1983 | 1239058.8063 | 2614287.2984 | 1239063.9348
25 | 2614277.1983 | 1239058.8063 | 2614270.8209 | 1239054.653
26 | 2614287.2984 | 1239063.9348 | 2614292.2918 | 1239066.4702
27 | 2614260.8413 | 1239048.1536 | 2614270.8209 | 1239054.653
28 | 2614560.3407 | 1239005.4029 | 2614558.5757 | 1239007.3307
29 | 2614539.825 | 1239027.8106 | 2614558.5757 | 1239007.3307
30 | 2614539.825 | 1239027.8106 | 2614543.8304 | 1239032.1765
31 | 2614539.825 | 1239027.8106 | 2614528.7859 | 1239018.5362
32 | 2614700.7433 | 1238813.6118 | 2614696.8995 | 1238830.9738 | 2614692.4694 | 1238841.4479
33 | 2614700.7433 | 1238813.6118 | 2614703.3919 | 1238801.6479
34 | 2614668.1985 | 1238882.8019 | 2614691.5819 | 1238843.5462 | 2614692.4694 | 1238841.4479
35 | 2614704.2649 | 1238797.7047 | 2614703.3919 | 1238801.6479
36 | 2614668.1985 | 1238882.8019 | 2614657.1469 | 1238865.9441
37 | 2614668.1985 | 1238882.8019 | 2614667.9579 | 1238888.6876
38 | 2614704.2649 | 1238797.7047 | 2614704.6456 | 1238790.5234 | 2614703.7186 | 1238782.1558
39 | 2614666.9028 | 1238914.4961 | 2614667.9579 | 1238888.6876
40 | 2614703.0032 | 1238775.6991 | 2614703.7186 | 1238782.1558
41 | 2614608.0213 | 1238893.9106 | 2614625.3981 | 1238899.9857
42 | 2614606.2947 | 1238893.3069 | 2614608.0213 | 1238893.9106
43 | 2614625.3981 | 1238899.9857 | 2614636.1695 | 1238903.7514
44 | 2614606.2947 | 1238893.3069 | 2614601.6975 | 1238891.6997 | 2614550.3133 | 1238861.3903
45 | 2614636.1695 | 1238903.7514 | 2614639.5205 | 1238904.923
46 | 2614666.9028 | 1238914.4961 | 2614639.5205 | 1238904.923
47 | 2614661.201 | 1239021.8041 | 2614668.0369 | 1238988.4002 | 2614670.6851 | 1238972.8251
48 | 2614671.1679 | 1238969.9854 | 2614670.6851 | 1238972.8251
49 | 2614634.0567 | 1239114.6727 | 2614661.201 | 1239021.8041
50 | 2614671.1679 | 1238969.9854 | 2614678.8013 | 1238965.9461 | 2614696.3025 | 1238950.4018
51 | 2614671.1679 | 1238969.9854 | 2614672.8228 | 1238949.2342
52 | 2614696.3025 | 1238950.4018 | 2614702.1194 | 1238940.7769 | 2614707.6395 | 1238928.8831 | 2614715.896 | 1238901.0835
53 | 2614674.1062 | 1238933.141 | 2614672.8228 | 1238949.2342
54 | 2614672.3623 | 1238924.3445 | 2614674.5002 | 1238928.201 | 2614674.1062 | 1238933.141
55 | 2614666.9028 | 1238914.4961 | 2614672.3623 | 1238924.3445
56 | 2614703.0032 | 1238775.6991 | 2614702.3861 | 1238770.7055
57 | 2614671.7448 | 1238757.1773 | 2614677.1805 | 1238751.9207 | 2614683.4231 | 1238750.7576 | 2614697.2 | 1238758.1961 | 2614701.6907 | 1238765.0781 | 2614702.3861 | 1238770.7055
58 | 2614543.8304 | 1239032.1765 | 2614556.7132 | 1239046.2188 | 2614563.3177 | 1239054.63
59 | 2614528.7859 | 1239018.5362 | 2614514.3826 | 1239006.4354 | 2614514.3826 | 1239006.4354
60 | 2614587.6087 | 1239085.3419 | 2614586.5916 | 1239084.2709 | 2614563.3177 | 1239054.63
61 | 2614507.6064 | 1239003.0607 | 2614514.3826 | 1239006.4354
62 | 2614192.8977 | 1239003.9044 | 2614201.0303 | 1238987.9474
63 | 2614319.6316 | 1238917.9097 | 2614331.1891 | 1238890.3708
64 | 2614319.6316 | 1238917.9097 | 2614351.6444 | 1238931.8857
65 | 2614360.7273 | 1238935.8511 | 2614351.6444 | 1238931.8857
66 | 2614348.2578 | 1238609.9213 | 2614349.0317 | 1238600.0217
67 | 2614366.3969 | 1238637.3041 | 2614348.2578 | 1238609.9213
68 | 2614366.3969 | 1238637.3041 | 2614351.159 | 1238652.0432 | 2614350.5304 | 1238652.9814
69 | 2614423.1306 | 1238640.0031 | 2614366.3969 | 1238637.3041
70 | 2614423.1306 | 1238640.0031 | 2614424.0194 | 1238644.6922 | 2614434.9315 | 1238671.9762
71 | 2614422.2805 | 1238624.0218 | 2614421.8985 | 1238633.5024 | 2614423.1306 | 1238640.0031
72 | 2614509.4015 | 1238728.7958 | 2614500.0913 | 1238721.6918
73 | 2614509.4015 | 1238728.7958 | 2614535.7023 | 1238731.3399
74 | 2614470.4045 | 1238705.9542 | 2614493.8048 | 1238716.895 | 2614500.0913 | 1238721.6918
75 | 2614546.1661 | 1238732.3521 | 2614535.7023 | 1238731.3399
76 | 2614422.2805 | 1238624.0218 | 2614422.6258 | 1238615.4516
77 | 2614422.6258 | 1238615.4516 | 2614422.7595 | 1238612.1357
78 | 2614442.0976 | 1238693.8997 | 2614440.7014 | 1238686.4028 | 2614434.9315 | 1238671.9762
79 | 2614442.0976 | 1238693.8997 | 2614446.6979 | 1238697.6598
80 | 2614455.3449 | 1238704.7274 | 2614469.3276 | 1238705.4507 | 2614470.4045 | 1238705.9542
81 | 2614455.3449 | 1238704.7274 | 2614446.6979 | 1238697.6598
82 | 2614237.9698 | 1239033.2582 | 2614228.1522 | 1239026.8644
83 | 2614254.9717 | 1239044.3309 | 2614237.9698 | 1239033.2582
84 | 2614228.1522 | 1239026.8644 | 2614207.8782 | 1239013.6607
85 | 2614254.9717 | 1239044.3309 | 2614260.8413 | 1239048.1536
86 | 2614206.5139 | 1239012.7722 | 2614207.8782 | 1239013.6607
87 | 2614192.8977 | 1239003.9044 | 2614206.5139 | 1239012.7722
88 | 2614192.8977 | 1239003.9044 | 2614181.5706 | 1238999.2933
89 | 2614404.3306 | 1239051.9066 | 2614477.3893 | 1239076.1191
90 | 2614489.6995 | 1239080.1988 | 2614477.3893 | 1239076.1191
91 | 2614404.3306 | 1239051.9066 | 2614400.0747 | 1239050.4961
92 | 2614489.6995 | 1239080.1988 | 2614512.8524 | 1239088.7361
93 | 2614489.6995 | 1239080.1988 | 2614484.501 | 1239099.9109
94 | 2614367.3123 | 1239037.7339 | 2614389.1947 | 1239046.8904 | 2614400.0747 | 1239050.4961
95 | 2614512.8524 | 1239088.7361 | 2614524.7741 | 1239093.132
96 | 2614484.501 | 1239099.9109 | 2614481.6964 | 1239110.5459
97 | 2614535.9724 | 1239097.2612 | 2614524.7741 | 1239093.132
98 | 2614479.5308 | 1239118.7576 | 2614481.6964 | 1239110.5459
99 | 2614605.4489 | 1239132.3135 | 2614571.467 | 1239111.7065 | 2614546.8228 | 1239101.2621 | 2614535.9724 | 1239097.2612
100 | 2614474.7997 | 1239136.6977 | 2614479.5308 | 1239118.7576
101 | 2614474.7997 | 1239136.6977 | 2614456.2485 | 1239130.3578
102 | 2614474.7997 | 1239136.6977 | 2614472.6573 | 1239145.0285
103 | 2614437.2714 | 1239123.8724 | 2614456.2485 | 1239130.3578
104 | 2614466.6991 | 1239168.1975 | 2614472.6573 | 1239145.0285
105 | 2614409.3664 | 1239114.3359 | 2614437.2714 | 1239123.8724
106 | 2614466.6991 | 1239168.1975 | 2614500.1016 | 1239178.296 | 2614503.028 | 1239180.2232
107 | 2614465.4999 | 1239173.0976 | 2614466.6991 | 1239168.1975
108 | 2614409.3664 | 1239114.3359 | 2614408.0281 | 1239113.8785
109 | 2614465.4999 | 1239173.0976 | 2614451.9636 | 1239169.4459
110 | 2614431.3994 | 1239163.8982 | 2614451.9636 | 1239169.4459
111 | 2614431.5495 | 1238967.068 | 2614431.8945 | 1238967.2258
112 | 2614477.8602 | 1238988.2464 | 2614431.8945 | 1238967.2258
113 | 2614431.5495 | 1238967.068 | 2614417.1971 | 1238960.5045 | 2614410.3277 | 1238957.5055
114 | 2614477.8602 | 1238988.2464 | 2614507.6064 | 1239003.0607
115 | 2614410.3277 | 1238957.5055 | 2614386.8914 | 1238947.2737
116 | 2614381.4686 | 1238944.9063 | 2614386.8914 | 1238947.2737
117 | 2614381.4686 | 1238944.9063 | 2614360.7273 | 1238935.8511
118 | 2614588.7912 | 1238723.3195 | 2614580.7677 | 1238729.0367 | 2614572.6802 | 1238733.0972 | 2614559.8667 | 1238733.6774 | 2614546.1661 | 1238732.3521
119 | 2614588.7912 | 1238723.3195 | 2614594.4008 | 1238711.9039
120 | 2614588.7912 | 1238723.3195 | 2614588.5189 | 1238729.4893 | 2614590.1138 | 1238736.0417 | 2614594.8292 | 1238747.0044 | 2614611.937 | 1238779.6149
121 | 2614594.4008 | 1238711.9039 | 2614595.4505 | 1238709.9983
122 | 2614594.4008 | 1238711.9039 | 2614600.4031 | 1238713.0971 | 2614615.3593 | 1238710.3997
123 | 2614607.0505 | 1238688.9385 | 2614595.4505 | 1238709.9983
124 | 2614615.3593 | 1238710.3997 | 2614618.1014 | 1238709.9052 | 2614635.0094 | 1238705.1659 | 2614643.2668 | 1238700.5145
125 | 2614629.3704 | 1238648.417 | 2614607.0505 | 1238688.9385
126 | 2614632.9031 | 1238641.9995 | 2614629.3704 | 1238648.417
127 | 2614632.9031 | 1238641.9995 | 2614627.2773 | 1238641.4631 | 2614603.1316 | 1238652.1439 | 2614594.2892 | 1238658.6596 | 2614590.7634 | 1238663.8639
128 | 2614149.3279 | 1238986.1678 | 2614181.5706 | 1238999.2933
129 | 2614634.0567 | 1239114.6727 | 2614609.327 | 1239102.1265 | 2614597.7282 | 1239094.9381 | 2614590.137 | 1239088.0041 | 2614587.6087 | 1239085.3419
130 | 2614408.0281 | 1239113.8785 | 2614392.2979 | 1239108.5027 | 2614391.6257 | 1239108.2217
131 | 2614380.9674 | 1239103.766 | 2614391.6257 | 1239108.2217
132 | 2614380.6109 | 1239103.6169 | 2614380.9674 | 1239103.766
133 | 2614380.6109 | 1239103.6169 | 2614361.4725 | 1239095.6161
134 | 2614345.9924 | 1239089.1447 | 2614361.4725 | 1239095.6161
135 | 2614605.4489 | 1239132.3135 | 2614625.2405 | 1239147.7605 | 2614634.0567 | 1239114.6727
136 | 2614318.0122 | 1239077.4475 | 2614294.7983 | 1239067.7429 | 2614292.2918 | 1239066.4702
137 | 2614318.0122 | 1239077.4475 | 2614343.7262 | 1239088.1973
138 | 2614345.9924 | 1239089.1447 | 2614343.7262 | 1239088.1973

## bus_geodata
| x | y | coords
0 | 2614501.9747 | 1238782.3918
1 | 2614499.7567 | 1238778.326
2 | 2614505.6684 | 1238789.1625
3 | 2614496.1974 | 1238771.8014
4 | 2614509.6111 | 1238796.3898
5 | 2614494.4083 | 1238952.988
6 | 2614485.2609 | 1238972.478
7 | 2614497.138 | 1238764.8572
8 | 2614346.2777 | 1238857.7655
9 | 2614334.1982 | 1238883.201
10 | 2614530.8577 | 1238843.8748
11 | 2614500.4818 | 1238746.0927
12 | 2614466.8564 | 1238732.1202
13 | 2614457.9976 | 1238714.8957
14 | 2614538.803 | 1238854.6008
15 | 2614273.4192 | 1238994.2732
16 | 2614259.7161 | 1238987.0031
17 | 2614291.6614 | 1239003.9515
18 | 2614239.893 | 1238976.4861
19 | 2614285.4714 | 1239027.4289
20 | 2614232.8169 | 1238972.7319
21 | 2614213.8999 | 1238962.6956
22 | 2614277.1983 | 1239058.8063
23 | 2614287.2984 | 1239063.9348
24 | 2614270.8209 | 1239054.653
25 | 2614560.3407 | 1239005.4029
26 | 2614558.5757 | 1239007.3307
27 | 2614539.825 | 1239027.8106
28 | 2614700.7433 | 1238813.6118
29 | 2614692.4694 | 1238841.4479
30 | 2614703.3919 | 1238801.6479
31 | 2614668.1985 | 1238882.8019
32 | 2614704.2649 | 1238797.7047
33 | 2614657.1469 | 1238865.9441
34 | 2614667.9579 | 1238888.6876
35 | 2614703.7186 | 1238782.1558
36 | 2614608.0213 | 1238893.9106
37 | 2614625.3981 | 1238899.9857
38 | 2614606.2947 | 1238893.3069
39 | 2614636.1695 | 1238903.7514
40 | 2614550.3133 | 1238861.3903
41 | 2614639.5205 | 1238904.923
42 | 2614670.6851 | 1238972.8251
43 | 2614661.201 | 1239021.8041
44 | 2614671.1679 | 1238969.9854
45 | 2614696.3025 | 1238950.4018
46 | 2614672.8228 | 1238949.2342
47 | 2614715.896 | 1238901.0835
48 | 2614674.1062 | 1238933.141
49 | 2614666.9028 | 1238914.4961
50 | 2614703.0032 | 1238775.6991
51 | 2614702.3861 | 1238770.7055
52 | 2614671.7448 | 1238757.1773
53 | 2614672.3623 | 1238924.3445
54 | 2614543.8304 | 1239032.1765
55 | 2614528.7859 | 1239018.5362
56 | 2614563.3177 | 1239054.63
57 | 2614514.3826 | 1239006.4354
58 | 2614192.8761 | 1238829.9174
59 | 2614201.0303 | 1238987.9474
60 | 2614331.1891 | 1238890.3708
61 | 2614319.6316 | 1238917.9097
62 | 2614351.6444 | 1238931.8857
63 | 2614349.0317 | 1238600.0217
64 | 2614348.2578 | 1238609.9213
65 | 2614366.3969 | 1238637.3041
66 | 2614350.5304 | 1238652.9814
67 | 2614423.1306 | 1238640.0031
68 | 2614509.4015 | 1238728.7958
69 | 2614500.0913 | 1238721.6918
70 | 2614535.7023 | 1238731.3399
71 | 2614422.2805 | 1238624.0218
72 | 2614422.6258 | 1238615.4516
73 | 2614434.9315 | 1238671.9762
74 | 2614422.7595 | 1238612.1357
75 | 2614442.0976 | 1238693.8997
76 | 2614470.4045 | 1238705.9542
77 | 2614446.6979 | 1238697.6598
78 | 2614455.3449 | 1238704.7274
79 | 2614237.9698 | 1239033.2582
80 | 2614228.1522 | 1239026.8644
81 | 2614254.9717 | 1239044.3309
82 | 2614207.8782 | 1239013.6607
83 | 2614260.8413 | 1239048.1536
84 | 2614206.5139 | 1239012.7722
85 | 2614192.8977 | 1239003.9044
86 | 2614477.3893 | 1239076.1191
87 | 2614404.3306 | 1239051.9066
88 | 2614489.6995 | 1239080.1988
89 | 2614400.0747 | 1239050.4961
90 | 2614512.8524 | 1239088.7361
91 | 2614484.501 | 1239099.9109
92 | 2614367.3123 | 1239037.7339
93 | 2614524.7741 | 1239093.132
94 | 2614481.6964 | 1239110.5459
95 | 2614535.9724 | 1239097.2612
96 | 2614479.5308 | 1239118.7576
97 | 2614474.7997 | 1239136.6977
98 | 2614456.2485 | 1239130.3578
99 | 2614472.6573 | 1239145.0285
100 | 2614437.2714 | 1239123.8724
101 | 2614466.6991 | 1239168.1975
102 | 2614409.3664 | 1239114.3359
103 | 2614503.028 | 1239180.2232
104 | 2614465.4999 | 1239173.0976
105 | 2614451.9636 | 1239169.4459
106 | 2614431.3994 | 1239163.8982
107 | 2614431.8945 | 1238967.2258
108 | 2614431.5495 | 1238967.068
109 | 2614477.8602 | 1238988.2464
110 | 2614410.3277 | 1238957.5055
111 | 2614507.6064 | 1239003.0607
112 | 2614386.8914 | 1238947.2737
113 | 2614381.4686 | 1238944.9063
114 | 2614546.1661 | 1238732.3521
115 | 2614588.7912 | 1238723.3195
116 | 2614594.4008 | 1238711.9039
117 | 2614611.937 | 1238779.6149
118 | 2614595.4505 | 1238709.9983
119 | 2614615.3593 | 1238710.3997
120 | 2614607.0505 | 1238688.9385
121 | 2614629.3704 | 1238648.417
122 | 2614632.9031 | 1238641.9995
123 | 2614590.7634 | 1238663.8639
124 | 2614643.2668 | 1238700.5145
125 | 2614360.7273 | 1238935.8511
126 | 2614149.3279 | 1238986.1678
127 | 2614181.5706 | 1238999.2933
128 | 2614587.6087 | 1239085.3419
129 | 2614408.0281 | 1239113.8785
130 | 2614391.6257 | 1239108.2217
131 | 2614380.9674 | 1239103.766
132 | 2614380.6109 | 1239103.6169
133 | 2614361.4725 | 1239095.6161
134 | 2614634.0567 | 1239114.6727
135 | 2614605.4489 | 1239132.3135
136 | 2614292.2918 | 1239066.4702
137 | 2614318.0122 | 1239077.4475
138 | 2614345.9924 | 1239089.1447
139 | 2614343.7262 | 1239088.1973
140 | 2614477.8602 | 1238988.2464

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97502 | -0.17545 | 0.0010404 | 0.00026076
1 | 0.97486 | -0.17663 | 0.000479 | 0.00012005
2 | 0.97531 | -0.1734 | 0.00078825 | 0.00019755
3 | 0.9746 | -0.17848 | 0 | 0
4 | 0.97562 | -0.17116 | 0.0011234 | 0.00028154
5 | 0.99997 | -0.00019098 | 0.00088772 | 0.00022248
6 | 1 | 0 | -0.17652 | -0.044458
7 | 0.97436 | -0.18023 | 0.0011745 | 0.00029436
8 | 0.9947 | -0.037042 | 0.00076454 | 0.00019161
9 | 0.99473 | -0.036824 | 0 | 0
10 | 0.97666 | -0.16374 | 0.00021278 | 5.3328e-05
11 | 0.97373 | -0.18477 | 0.0017814 | 0.00044645
12 | 0.9725 | -0.19359 | 0.00046375 | 0.00011623
13 | 0.97252 | -0.1935 | 0.0005748 | 0.00014406
14 | 0.97683 | -0.16247 | 0.00031836 | 7.9788e-05
15 | 0.97078 | -0.20594 | 0.0010318 | 0.0002586
16 | 0.97082 | -0.20569 | 0.00071833 | 0.00018003
17 | 0.97077 | -0.20605 | 0 | 0
18 | 0.97089 | -0.20515 | 0.00064278 | 0.0001611
19 | 0.97075 | -0.20618 | 0.00050443 | 0.00012642
20 | 0.97093 | -0.2049 | 0.0006425 | 0.00016103
21 | 0.97104 | -0.2041 | 0 | 0
22 | 0.97316 | -0.1888 | 0 | 0
23 | 0.97328 | -0.1879 | 0.00087916 | 0.00022034
24 | 0.97299 | -0.19002 | 0.00085325 | 0.00021385
25 | 0.99324 | -0.046682 | 0.0010212 | 0.00025595
26 | 0.99324 | -0.046655 | 0.00061324 | 0.00015369
27 | 0.99331 | -0.046196 | 0 | 0
28 | 0.97773 | -0.15604 | 0.00060078 | 0.00015057
29 | 0.97798 | -0.15427 | 0.00090305 | 0.00022633
30 | 0.97764 | -0.15671 | 0.0019011 | 0.00047647
31 | 0.97845 | -0.15091 | 0 | 0
32 | 0.97762 | -0.15685 | 0 | 0
33 | 0.9784 | -0.15126 | 0.0016724 | 0.00041914
34 | 0.97852 | -0.15039 | 0.0021994 | 0.00055121
35 | 0.97755 | -0.15739 | 0.0010278 | 0.00025759
36 | 0.97792 | -0.1547 | 0.0018204 | 0.00045624
37 | 0.9782 | -0.15273 | 0.001368 | 0.00034286
38 | 0.97789 | -0.15489 | 0.001026 | 0.00025715
39 | 0.97837 | -0.15145 | 0.0011966 | 0.00029991
40 | 0.97701 | -0.16118 | 0.00028226 | 7.0741e-05
41 | 0.97843 | -0.15103 | 0.001223 | 0.00030652
42 | 0.98037 | -0.13719 | 0.0029951 | 0.00075064
43 | 0.98175 | -0.12734 | 0 | 0
44 | 0.9803 | -0.13773 | 0 | 0
45 | 0.98018 | -0.13857 | 0 | 0
46 | 0.97978 | -0.14144 | 0.0018152 | 0.00045494
47 | 0.97998 | -0.13997 | 0.0025305 | 0.0006342
48 | 0.97939 | -0.14423 | 0.0021056 | 0.0005277
49 | 0.97892 | -0.14754 | 0 | 0
50 | 0.97753 | -0.15754 | 0 | 0
51 | 0.97751 | -0.15766 | 0.00051969 | 0.00013025
52 | 0.9774 | -0.15846 | 0.0017555 | 0.00043997
53 | 0.97917 | -0.14577 | 0.0023532 | 0.00058976
54 | 0.9929 | -0.049031 | 0.00051665 | 0.00012949
55 | 0.99431 | -0.039227 | 0.00038361 | 9.6142e-05
56 | 0.99086 | -0.063251 | 0.001253 | 0.00031404
57 | 0.99563 | -0.03013 | 0.0017861 | 0.00044764
58 | 0.97082 | -0.20567 | 0.0010953 | 0.00027452
59 | 0.97123 | -0.2027 | 0.0022584 | 0.00056601
60 | 0.99474 | -0.036764 | 0.0024752 | 0.00062035
61 | 0.99488 | -0.035787 | 0 | 0
62 | 0.99504 | -0.034643 | 0.0031103 | 0.00077951
63 | 0.97196 | -0.19752 | 0.00071807 | 0.00017996
64 | 0.97197 | -0.19745 | 0 | 0
65 | 0.97201 | -0.1972 | 0 | 0
66 | 0.97198 | -0.19735 | 0.00066137 | 0.00016576
67 | 0.97212 | -0.19636 | 0.00088899 | 0.0002228
68 | 0.97313 | -0.18906 | 0 | 0
69 | 0.973 | -0.19001 | 0.00097719 | 0.00024491
70 | 0.97263 | -0.1927 | 0.0014293 | 0.00035822
71 | 0.97209 | -0.19656 | 0.00029636 | 7.4275e-05
72 | 0.97208 | -0.19663 | 0.00044404 | 0.00011129
73 | 0.97229 | -0.19514 | 0.00036941 | 9.2582e-05
74 | 0.97208 | -0.19664 | 0.00037934 | 9.5072e-05
75 | 0.97242 | -0.19421 | 0 | 0
76 | 0.97267 | -0.19241 | 0.00064275 | 0.00016109
77 | 0.97245 | -0.19398 | 0.0012642 | 0.00031683
78 | 0.97253 | -0.19338 | 0 | 0
79 | 0.97223 | -0.1955 | 0.0010138 | 0.00025407
80 | 0.97203 | -0.19694 | 0.00073194 | 0.00018344
81 | 0.9726 | -0.1928 | 0.00085226 | 0.0002136
82 | 0.97164 | -0.19972 | 0.00070858 | 0.00017759
83 | 0.97274 | -0.19181 | 0.00079524 | 0.0001993
84 | 0.97162 | -0.19989 | 0.0014289 | 0.00035812
85 | 0.97141 | -0.20139 | 0 | 0
86 | 0.9766 | -0.16406 | 0.0040093 | 0.0010048
87 | 0.97415 | -0.18162 | 0.020839 | 0.0052228
88 | 0.97709 | -0.16057 | 0 | 0
89 | 0.97414 | -0.18166 | 0.00036483 | 9.1435e-05
90 | 0.97798 | -0.15415 | 0.00055393 | 0.00013883
91 | 0.9766 | -0.16404 | 0.0010346 | 0.0002593
92 | 0.97412 | -0.18186 | 0.00053338 | 0.00013368
93 | 0.97845 | -0.15083 | 0.0060855 | 0.0015252
94 | 0.97634 | -0.16588 | 0.00062866 | 0.00015756
95 | 0.97892 | -0.14746 | 0.0011927 | 0.00029892
96 | 0.97615 | -0.16728 | 0.0013392 | 0.00033564
97 | 0.97573 | -0.17025 | 0 | 0
98 | 0.97539 | -0.17272 | 0.0019047 | 0.00047735
99 | 0.97561 | -0.17113 | 0.0039346 | 0.0009861
100 | 0.97506 | -0.17512 | 0.0022644 | 0.00056751
101 | 0.97541 | -0.17261 | 0 | 0
102 | 0.9746 | -0.17841 | 0.0035994 | 0.0009021
103 | 0.97538 | -0.1728 | 0.00048828 | 0.00012237
104 | 0.97537 | -0.17289 | 0 | 0
105 | 0.97526 | -0.17368 | 0.0019893 | 0.00049856
106 | 0.97515 | -0.17443 | 0.003378 | 0.0008466
107 | 0.99685 | -0.021894 | 0.0029245 | 0.00073295
108 | 0.99684 | -0.021973 | 0.002028 | 0.00050825
109 | 0.99855 | -0.0099647 | 0 | 0
110 | 0.99622 | -0.02632 | 0.0024821 | 0.00062208
111 | 0.99616 | -0.026431 | 0.0024685 | 0.00061868
112 | 0.99563 | -0.030463 | 0.0033589 | 0.00084182
113 | 0.99552 | -0.031222 | 0.00051843 | 0.00012993
114 | 0.97245 | -0.19399 | 0.00090261 | 0.00022622
115 | 0.97173 | -0.19914 | 0 | 0
116 | 0.9716 | -0.20012 | 0 | 0
117 | 0.97142 | -0.20139 | 0.0034431 | 0.00086293
118 | 0.97158 | -0.20023 | 0.002418 | 0.00060601
119 | 0.97151 | -0.20072 | 0.00146 | 0.00036591
120 | 0.97151 | -0.20078 | 0.0010742 | 0.00026923
121 | 0.97143 | -0.20132 | 0 | 0
122 | 0.97142 | -0.20141 | 0 | 0
123 | 0.97134 | -0.20198 | 0.0011008 | 0.00027589
124 | 0.97146 | -0.2011 | 0.0012007 | 0.00030092
125 | 0.99513 | -0.034008 | 0.0058573 | 0.001468
126 | 0.97133 | -0.20195 | 0.00089211 | 0.00022358
127 | 0.97138 | -0.20162 | 0.00090763 | 0.00022747
128 | 0.98819 | -0.08189 | 0.00039639 | 9.9345e-05
129 | 0.97458 | -0.17855 | 0.0023911 | 0.00059926
130 | 0.97436 | -0.18012 | 0.0025806 | 0.00064675
131 | 0.97423 | -0.18107 | 0.00026144 | 6.5524e-05
132 | 0.97423 | -0.1811 | 0.00026173 | 6.5596e-05
133 | 0.974 | -0.18275 | 0.0019487 | 0.0004884
134 | 0.98444 | -0.10832 | 0 | 0
135 | 0.98205 | -0.12517 | 0 | 0
136 | 0.97332 | -0.18759 | 0.00086981 | 0.00021799
137 | 0.97355 | -0.18593 | 0.0012531 | 0.00031406
138 | 0.97382 | -0.18398 | 0.00055268 | 0.00013851
139 | 0.9738 | -0.18415 | 0.002127 | 0.00053307
140 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.024211 | 0.0060681 | -0.024207 | -0.0060666 | 3.9457e-06 | 1.4598e-06 | 0.036949 | 0.036949 | 0.036949 | 0.97502 | -0.17545 | 0.97486 | -0.17663 | 13.685
1 | -0.025251 | -0.0063288 | 0.025259 | 0.0063315 | 7.1474e-06 | 2.6528e-06 | 0.038537 | 0.038537 | 0.038537 | 0.97502 | -0.17545 | 0.97531 | -0.1734 | 14.273
2 | 0.023728 | 0.0059465 | -0.023722 | -0.0059443 | 6.0836e-06 | 2.2472e-06 | 0.036218 | 0.036218 | 0.036218 | 0.97486 | -0.17663 | 0.9746 | -0.17848 | 13.4142
3 | -0.026047 | -0.006529 | 0.026055 | 0.006532 | 8.113e-06 | 3.0176e-06 | 0.03974 | 0.03974 | 0.03974 | 0.97531 | -0.1734 | 0.97562 | -0.17116 | 14.7184
4 | 0.023722 | 0.0059443 | -0.023716 | -0.0059422 | 5.7361e-06 | 2.1189e-06 | 0.036218 | 0.036218 | 0.036218 | 0.9746 | -0.17848 | 0.97436 | -0.18023 | 13.4142
5 | -0.027178 | -0.0068136 | 0.027206 | 0.006823 | 2.7931e-05 | 9.44e-06 | 0.041453 | 0.041453 | 0.041453 | 0.97562 | -0.17116 | 0.97666 | -0.16374 | 7.6765
6 | -0.00088772 | -0.00022248 | 0.00088775 | 0.00022221 | 2.3442e-08 | -2.7343e-07 | 0.001321 | 0.0013209 | 0.001321 | 0.99997 | -0.00019098 | 1 | 0 | 0.48925
7 | 0.17483 | 0.044236 | -0.17459 | -0.044142 | 0.00024549 | 9.3736e-05 | 0.2603 | 0.2603 | 0.2603 | 1 | 0 | 0.99855 | -0.0099647 | 32.1361
8 | 0.022542 | 0.0056478 | -0.022528 | -0.0056426 | 1.4155e-05 | 5.206e-06 | 0.034425 | 0.034425 | 0.034425 | 0.97436 | -0.18023 | 0.97373 | -0.18477 | 12.7499
9 | -0.00076454 | -0.00019161 | 0.00076456 | 0.00019125 | 2.2981e-08 | -3.5668e-07 | 0.0011437 | 0.0011436 | 0.0011437 | 0.9947 | -0.037042 | 0.99473 | -0.036824 | 0.42359
10 | -0.00076456 | -0.00019125 | 0.00076456 | 0.00019116 | 6.3451e-09 | -9.8499e-08 | 0.0011436 | 0.0011435 | 0.0011436 | 0.99473 | -0.036824 | 0.99474 | -0.036764 | 0.42355
11 | -0.027419 | -0.0068763 | 0.027424 | 0.0068777 | 4.8457e-06 | 1.3625e-06 | 0.041777 | 0.041777 | 0.041777 | 0.97666 | -0.16374 | 0.97683 | -0.16247 | 5.1576
12 | 0.020746 | 0.0051962 | -0.020734 | -0.0051917 | 1.2312e-05 | 4.4915e-06 | 0.031703 | 0.031703 | 0.031703 | 0.97373 | -0.18477 | 0.97313 | -0.18906 | 11.7417
13 | -0.00046375 | -0.00011623 | 0.00046376 | 0.00011599 | 6.0847e-09 | -2.3799e-07 | 0.00070958 | 0.00070949 | 0.00070958 | 0.9725 | -0.19359 | 0.97252 | -0.1935 | 0.26281
14 | -0.0010386 | -0.00026005 | 0.0010386 | 0.00025992 | 1.6556e-08 | -1.2403e-07 | 0.001589 | 0.0015889 | 0.001589 | 0.97252 | -0.1935 | 0.97253 | -0.19338 | 0.58851
15 | -0.027742 | -0.0069575 | 0.027747 | 0.0069589 | 4.9645e-06 | 1.4074e-06 | 0.042262 | 0.042261 | 0.042262 | 0.97683 | -0.16247 | 0.97701 | -0.16118 | 5.2175
16 | -0.0015363 | -0.00038447 | 0.0015363 | 0.0003843 | 5.3664e-08 | -1.7116e-07 | 0.0023546 | 0.0023545 | 0.0023546 | 0.97078 | -0.20594 | 0.97082 | -0.20569 | 0.87208
17 | 0.00050444 | 0.00012587 | -0.00050443 | -0.00012612 | 7.7009e-09 | -2.5236e-07 | 0.00077301 | 0.0007731 | 0.0007731 | 0.97078 | -0.20594 | 0.97077 | -0.20605 | 0.28633
18 | -0.0022547 | -0.00056433 | 0.0022548 | 0.00056412 | 1.672e-07 | -2.1318e-07 | 0.0034556 | 0.0034555 | 0.0034556 | 0.97082 | -0.20569 | 0.97089 | -0.20515 | 1.2798
19 | 0.00050443 | 0.00012612 | -0.00050443 | -0.00012642 | 9.0566e-09 | -2.9669e-07 | 0.0007731 | 0.00077321 | 0.00077321 | 0.97077 | -0.20605 | 0.97075 | -0.20618 | 0.28637
20 | -0.0028976 | -0.00072522 | 0.0028977 | 0.00072516 | 9.8563e-08 | -6.1155e-08 | 0.0044406 | 0.0044406 | 0.0044406 | 0.97089 | -0.20515 | 0.97093 | -0.2049 | 1.6447
21 | -0.0035402 | -0.00088618 | 0.0035406 | 0.00088607 | 3.933e-07 | -1.1361e-07 | 0.0054252 | 0.0054252 | 0.0054252 | 0.97093 | -0.2049 | 0.97104 | -0.2041 | 2.0094
22 | -0.0046362 | -0.001159 | 0.0046371 | 0.001159 | 8.9237e-07 | -7.4538e-09 | 0.0071034 | 0.0071033 | 0.0071034 | 0.97104 | -0.2041 | 0.97123 | -0.2027 | 2.6309
23 | 0.0010956 | 0.00027294 | -0.0010953 | -0.00027452 | 2.3635e-07 | -1.5717e-06 | 0.0016783 | 0.0016789 | 0.0016789 | 0.97104 | -0.2041 | 0.97082 | -0.20567 | 0.6218
24 | -0.015102 | -0.0037826 | 0.015103 | 0.0037831 | 1.8843e-06 | 4.4322e-07 | 0.02309 | 0.02309 | 0.02309 | 0.97316 | -0.1888 | 0.97328 | -0.1879 | 4.276
25 | 0.015102 | 0.0037826 | -0.015099 | -0.0037817 | 2.5321e-06 | 8.7933e-07 | 0.02309 | 0.023091 | 0.023091 | 0.97316 | -0.1888 | 0.97299 | -0.19002 | 8.552
26 | -0.015983 | -0.0040034 | 0.015983 | 0.0040035 | 6.9546e-07 | 5.8685e-08 | 0.024435 | 0.024434 | 0.024435 | 0.97328 | -0.1879 | 0.97332 | -0.18759 | 3.0166
27 | 0.014246 | 0.0035679 | -0.014242 | -0.0035667 | 3.5271e-06 | 1.2087e-06 | 0.021786 | 0.021786 | 0.021786 | 0.97299 | -0.19002 | 0.97274 | -0.19181 | 8.0688
28 | -0.0010212 | -0.00025595 | 0.0010212 | 0.00025591 | 3.8177e-09 | -3.2359e-08 | 0.00153 | 0.0015299 | 0.00153 | 0.99324 | -0.046682 | 0.99324 | -0.046655 | 0.56665
29 | -0.0016345 | -0.00040961 | 0.0016346 | 0.00040929 | 1.0389e-07 | -3.1945e-07 | 0.0024487 | 0.0024485 | 0.0024487 | 0.99324 | -0.046655 | 0.99331 | -0.046196 | 0.90692
30 | 0.14397 | 0.036364 | -0.14391 | -0.036343 | 5.7378e-05 | 2.1839e-05 | 0.21577 | 0.21577 | 0.21577 | 0.99331 | -0.046196 | 0.9929 | -0.049031 | 26.6388
31 | -0.14561 | -0.036774 | 0.14575 | 0.036828 | 0.00014281 | 5.4367e-05 | 0.21822 | 0.21822 | 0.21822 | 0.99331 | -0.046196 | 0.99431 | -0.039227 | 26.9411
32 | -0.005806 | -0.0014542 | 0.0058074 | 0.0014544 | 1.4203e-06 | 1.8053e-07 | 0.0088358 | 0.0088357 | 0.0088358 | 0.97773 | -0.15604 | 0.97798 | -0.15427 | 3.2725
33 | 0.0052052 | 0.0013036 | -0.0052047 | -0.0013036 | 4.798e-07 | 3.0874e-08 | 0.0079215 | 0.0079215 | 0.0079215 | 0.97773 | -0.15604 | 0.97764 | -0.15671 | 2.9339
34 | -0.0067105 | -0.0016807 | 0.0067136 | 0.0016813 | 3.1201e-06 | 5.9783e-07 | 0.01021 | 0.010209 | 0.01021 | 0.97798 | -0.15427 | 0.97845 | -0.15091 | 3.7814
35 | 0.0033036 | 0.0008271 | -0.0033035 | -0.00082712 | 6.3708e-08 | -2.6138e-08 | 0.0050279 | 0.0050279 | 0.0050279 | 0.97764 | -0.15671 | 0.97762 | -0.15685 | 1.8622
36 | 0.0016725 | 0.00041892 | -0.0016724 | -0.00041914 | 8.137e-08 | -2.2187e-07 | 0.0025434 | 0.0025435 | 0.0025435 | 0.97845 | -0.15091 | 0.9784 | -0.15126 | 0.94203
37 | -0.008386 | -0.0021002 | 0.0083866 | 0.0021003 | 5.978e-07 | 1.5593e-07 | 0.012753 | 0.012753 | 0.012753 | 0.97845 | -0.15091 | 0.97852 | -0.15039 | 4.7233
38 | 0.0033035 | 0.00082712 | -0.0033033 | -0.00082722 | 2.4625e-07 | -1.0101e-07 | 0.0050279 | 0.005028 | 0.005028 | 0.97762 | -0.15685 | 0.97755 | -0.15739 | 1.8622
39 | -0.010586 | -0.0026516 | 0.01059 | 0.0026528 | 4.1765e-06 | 1.2817e-06 | 0.016097 | 0.016097 | 0.016097 | 0.97852 | -0.15039 | 0.97892 | -0.14754 | 5.962
40 | 0.0022755 | 0.00056963 | -0.0022754 | -0.0005697 | 4.8626e-08 | -6.2737e-08 | 0.0034635 | 0.0034635 | 0.0034635 | 0.97755 | -0.15739 | 0.97753 | -0.15754 | 1.2828
41 | -0.030901 | -0.0077502 | 0.03091 | 0.0077528 | 8.4658e-06 | 2.563e-06 | 0.047022 | 0.047021 | 0.047022 | 0.97792 | -0.1547 | 0.9782 | -0.15273 | 5.8051
42 | 0.029081 | 0.007294 | -0.02908 | -0.0072938 | 7.4501e-07 | 2.177e-07 | 0.044252 | 0.044252 | 0.044252 | 0.97792 | -0.1547 | 0.97789 | -0.15489 | 5.4632
43 | -0.032278 | -0.0080957 | 0.032283 | 0.0080974 | 5.7224e-06 | 1.7711e-06 | 0.049102 | 0.049102 | 0.049102 | 0.9782 | -0.15273 | 0.97837 | -0.15145 | 6.062
44 | 0.028054 | 0.0070366 | -0.028029 | -0.0070296 | 2.4461e-05 | 6.9817e-06 | 0.04269 | 0.042691 | 0.042691 | 0.97789 | -0.15489 | 0.97701 | -0.16118 | 5.2705
45 | -0.03348 | -0.0083973 | 0.033482 | 0.0083979 | 1.9147e-06 | 6.0267e-07 | 0.050922 | 0.050922 | 0.050922 | 0.97837 | -0.15145 | 0.97843 | -0.15103 | 6.2867
46 | -0.034705 | -0.0087045 | 0.034722 | 0.0087098 | 1.6809e-05 | 5.3716e-06 | 0.052782 | 0.052782 | 0.052782 | 0.97843 | -0.15103 | 0.97892 | -0.14754 | 6.5163
47 | -0.057183 | -0.014344 | 0.057262 | 0.014372 | 7.8187e-05 | 2.8182e-05 | 0.086798 | 0.086797 | 0.086798 | 0.98037 | -0.13719 | 0.98175 | -0.12734 | 10.7158
48 | 0.054188 | 0.013594 | -0.054184 | -0.013592 | 4.0534e-06 | 1.4501e-06 | 0.082252 | 0.082252 | 0.082252 | 0.98037 | -0.13719 | 0.9803 | -0.13773 | 10.1546
49 | -0.057262 | -0.014372 | 0.057413 | 0.014427 | 0.00015161 | 5.4633e-05 | 0.086797 | 0.086796 | 0.086797 | 0.98175 | -0.12734 | 0.98444 | -0.10832 | 10.7157
50 | 0.0025313 | 0.00063343 | -0.002531 | -0.00063372 | 2.9464e-07 | -2.8991e-07 | 0.003842 | 0.0038421 | 0.0038421 | 0.9803 | -0.13773 | 0.98018 | -0.13857 | 1.423
51 | 0.051653 | 0.012959 | -0.051626 | -0.012949 | 2.6621e-05 | 9.452e-06 | 0.07841 | 0.07841 | 0.07841 | 0.9803 | -0.13773 | 0.97978 | -0.14144 | 9.6803
52 | 0.002531 | 0.00063372 | -0.0025305 | -0.0006342 | 4.9153e-07 | -4.8336e-07 | 0.0038421 | 0.0038423 | 0.0038423 | 0.98018 | -0.13857 | 0.97998 | -0.13997 | 1.4231
53 | 0.049811 | 0.012494 | -0.049792 | -0.012488 | 1.922e-05 | 6.7824e-06 | 0.075654 | 0.075654 | 0.075654 | 0.97978 | -0.14144 | 0.97939 | -0.14423 | 9.34
54 | 0.047686 | 0.01196 | -0.047676 | -0.011956 | 1.0226e-05 | 3.5797e-06 | 0.072455 | 0.072455 | 0.072455 | 0.97939 | -0.14423 | 0.97917 | -0.14577 | 8.9451
55 | -0.045312 | -0.011363 | 0.045323 | 0.011367 | 1.1112e-05 | 3.849e-06 | 0.068879 | 0.068879 | 0.068879 | 0.97892 | -0.14754 | 0.97917 | -0.14577 | 8.5036
56 | 0.0022754 | 0.0005697 | -0.0022754 | -0.00056975 | 3.7664e-08 | -4.859e-08 | 0.0034635 | 0.0034635 | 0.0034635 | 0.97753 | -0.15754 | 0.97751 | -0.15766 | 1.2828
57 | 0.0017557 | 0.0004395 | -0.0017555 | -0.00043997 | 1.9368e-07 | -4.702e-07 | 0.0026724 | 0.0026726 | 0.0026726 | 0.97751 | -0.15766 | 0.9774 | -0.15846 | 0.98986
58 | 0.1434 | 0.036213 | -0.14311 | -0.036104 | 0.00028605 | 0.00010887 | 0.215 | 0.215 | 0.215 | 0.9929 | -0.049031 | 0.99086 | -0.063251 | 26.5433
59 | -0.14613 | -0.036924 | 0.14632 | 0.036996 | 0.00018732 | 7.1312e-05 | 0.2188 | 0.2188 | 0.2188 | 0.99431 | -0.039227 | 0.99563 | -0.03013 | 27.012
60 | 0.14186 | 0.03579 | -0.14149 | -0.035649 | 0.00036999 | 0.00014079 | 0.21312 | 0.21312 | 0.21312 | 0.99086 | -0.063251 | 0.98819 | -0.08189 | 26.311
61 | -0.14811 | -0.037443 | 0.14818 | 0.037473 | 7.7228e-05 | 2.9408e-05 | 0.22147 | 0.22147 | 0.22147 | 0.99563 | -0.03013 | 0.99616 | -0.026431 | 27.3415
62 | -0.0068955 | -0.001725 | 0.0068967 | 0.0017253 | 1.247e-06 | 2.5795e-07 | 0.010563 | 0.010563 | 0.010563 | 0.97123 | -0.2027 | 0.97141 | -0.20139 | 3.9124
63 | -0.0032398 | -0.00081151 | 0.0032402 | 0.00081129 | 4.3768e-07 | -2.1942e-07 | 0.0048462 | 0.0048461 | 0.0048462 | 0.99474 | -0.036764 | 0.99488 | -0.035787 | 1.7949
64 | -0.0032402 | -0.00081129 | 0.0032408 | 0.00081103 | 5.1187e-07 | -2.5678e-07 | 0.0048461 | 0.0048459 | 0.0048461 | 0.99488 | -0.035787 | 0.99504 | -0.034643 | 1.7948
65 | -0.006351 | -0.0015905 | 0.0063516 | 0.0015906 | 5.578e-07 | 8.5792e-08 | 0.0094972 | 0.0094971 | 0.0094972 | 0.99504 | -0.034643 | 0.99513 | -0.034008 | 3.5175
66 | -0.00071807 | -0.00017996 | 0.00071807 | 0.00017984 | 7.4878e-09 | -1.2019e-07 | 0.0010993 | 0.0010993 | 0.0010993 | 0.97196 | -0.19752 | 0.97197 | -0.19745 | 0.40715
67 | -0.00071807 | -0.00017984 | 0.0007181 | 0.00017945 | 2.4744e-08 | -3.9726e-07 | 0.0010993 | 0.0010991 | 0.0010993 | 0.97197 | -0.19745 | 0.97201 | -0.1972 | 0.40714
68 | 0.00066139 | 0.00016548 | -0.00066137 | -0.00016576 | 1.4282e-08 | -2.7127e-07 | 0.0010124 | 0.0010125 | 0.0010125 | 0.97201 | -0.1972 | 0.97198 | -0.19735 | 0.375
69 | -0.0013795 | -0.00034493 | 0.0013796 | 0.00034429 | 1.58e-07 | -6.4333e-07 | 0.0021115 | 0.0021113 | 0.0021115 | 0.97201 | -0.1972 | 0.97212 | -0.19636 | 0.78205
70 | -0.0033884 | -0.00084739 | 0.003389 | 0.00084719 | 5.7322e-07 | -2.0309e-07 | 0.005186 | 0.0051858 | 0.005186 | 0.97212 | -0.19636 | 0.97229 | -0.19514 | 1.9207
71 | 0.0011198 | 0.0002803 | -0.0011198 | -0.00028049 | 2.9521e-08 | -1.8831e-07 | 0.0017139 | 0.001714 | 0.001714 | 0.97212 | -0.19636 | 0.97209 | -0.19656 | 0.63481
72 | 0.0076862 | 0.0019232 | -0.0076851 | -0.001923 | 1.0092e-06 | 2.4269e-07 | 0.011752 | 0.011752 | 0.011752 | 0.97313 | -0.18906 | 0.973 | -0.19001 | 4.3525
73 | 0.013048 | 0.0032685 | -0.013041 | -0.0032663 | 6.563e-06 | 2.1961e-06 | 0.019951 | 0.019951 | 0.019951 | 0.97313 | -0.18906 | 0.97263 | -0.1927 | 7.3892
74 | 0.006708 | 0.0016781 | -0.0067057 | -0.0016776 | 2.2151e-06 | 4.3307e-07 | 0.010257 | 0.010258 | 0.010258 | 0.973 | -0.19001 | 0.97267 | -0.19241 | 3.7991
75 | 0.011612 | 0.002908 | -0.01161 | -0.0029074 | 2.0701e-06 | 6.6575e-07 | 0.017764 | 0.017764 | 0.017764 | 0.97263 | -0.1927 | 0.97245 | -0.19399 | 6.5794
76 | 0.00082339 | 0.00020622 | -0.00082338 | -0.00020632 | 8.5019e-09 | -1.0306e-07 | 0.0012603 | 0.0012604 | 0.0012604 | 0.97209 | -0.19656 | 0.97208 | -0.19663 | 0.46681
77 | 0.00037934 | 9.5031e-05 | -0.00037934 | -9.5072e-05 | 6.9824e-10 | -4.0872e-08 | 0.00058066 | 0.00058068 | 0.00058068 | 0.97208 | -0.19663 | 0.97208 | -0.19664 | 0.21506
78 | -0.0037584 | -0.00093977 | 0.0037589 | 0.00093967 | 4.7807e-07 | -1.0344e-07 | 0.0057512 | 0.0057511 | 0.0057512 | 0.97229 | -0.19514 | 0.97242 | -0.19421 | 2.1301
79 | -0.0037589 | -0.00093967 | 0.003759 | 0.00093964 | 1.2262e-07 | -2.6547e-08 | 0.0057511 | 0.005751 | 0.0057511 | 0.97242 | -0.19421 | 0.97245 | -0.19398 | 2.13
80 | 0.006063 | 0.0015165 | -0.0060622 | -0.0015164 | 8.1529e-07 | 1.2506e-07 | 0.0092743 | 0.0092743 | 0.0092743 | 0.97267 | -0.19241 | 0.97253 | -0.19338 | 3.4349
81 | -0.0050232 | -0.0012565 | 0.0050236 | 0.0012565 | 4.1161e-07 | 1.9749e-08 | 0.0076855 | 0.0076854 | 0.0076855 | 0.97245 | -0.19398 | 0.97253 | -0.19338 | 2.8465
82 | 0.011574 | 0.0028975 | -0.011572 | -0.0028968 | 2.294e-06 | 7.3705e-07 | 0.017714 | 0.017714 | 0.017714 | 0.97223 | -0.1955 | 0.97203 | -0.19694 | 6.5607
83 | -0.012588 | -0.0031516 | 0.012593 | 0.0031532 | 4.6991e-06 | 1.5556e-06 | 0.019265 | 0.019265 | 0.019265 | 0.97223 | -0.1955 | 0.9726 | -0.1928 | 7.1353
84 | 0.01084 | 0.0027134 | -0.010836 | -0.0027121 | 4.157e-06 | 1.299e-06 | 0.016593 | 0.016594 | 0.016594 | 0.97203 | -0.19694 | 0.97164 | -0.19972 | 6.1457
85 | -0.013445 | -0.0033668 | 0.013447 | 0.0033674 | 1.8493e-06 | 6.2433e-07 | 0.020569 | 0.020569 | 0.020569 | 0.9726 | -0.1928 | 0.97274 | -0.19181 | 7.6182
86 | 0.010128 | 0.0025345 | -0.010127 | -0.0025344 | 2.4433e-07 | 7.381e-08 | 0.015508 | 0.015508 | 0.015508 | 0.97164 | -0.19972 | 0.97162 | -0.19989 | 5.7438
87 | 0.0086983 | 0.0021763 | -0.0086965 | -0.0021758 | 1.799e-06 | 4.9071e-07 | 0.01332 | 0.01332 | 0.01332 | 0.97162 | -0.19989 | 0.97141 | -0.20139 | 4.9334
88 | 0.0017998 | 0.00045051 | -0.0017998 | -0.00045064 | 5.7999e-08 | -1.2909e-07 | 0.0027568 | 0.0027569 | 0.0027569 | 0.97141 | -0.20139 | 0.97138 | -0.20162 | 1.0211
89 | 0.02179 | 0.0054668 | -0.021737 | -0.0054474 | 5.2949e-05 | 1.9404e-05 | 0.033204 | 0.033204 | 0.033204 | 0.9766 | -0.16406 | 0.97415 | -0.18162 | 12.2977
90 | -0.0258 | -0.0064717 | 0.025812 | 0.0064763 | 1.2507e-05 | 4.6479e-06 | 0.039312 | 0.039312 | 0.039312 | 0.9766 | -0.16406 | 0.97709 | -0.16057 | 14.5602
91 | 0.00089823 | 0.00022463 | -0.00089822 | -0.00022468 | 5.2654e-09 | -5.3793e-08 | 0.0013719 | 0.0013719 | 0.0013719 | 0.97415 | -0.18162 | 0.97414 | -0.18166 | 0.50811
92 | -0.074735 | -0.018742 | 0.074802 | 0.018767 | 6.6494e-05 | 2.4646e-05 | 0.11382 | 0.11382 | 0.11382 | 0.97709 | -0.16057 | 0.97798 | -0.15415 | 14.0517
93 | 0.048923 | 0.012266 | -0.048899 | -0.012257 | 2.3539e-05 | 8.2878e-06 | 0.074507 | 0.074507 | 0.074507 | 0.97709 | -0.16057 | 0.9766 | -0.16404 | 9.1984
94 | 0.00053339 | 0.00013324 | -0.00053338 | -0.00013368 | 1.4571e-08 | -4.324e-07 | 0.00081461 | 0.00081476 | 0.00081476 | 0.97414 | -0.18166 | 0.97412 | -0.18186 | 0.30176
95 | -0.075355 | -0.018905 | 0.07539 | 0.018918 | 3.4747e-05 | 1.2886e-05 | 0.11466 | 0.11466 | 0.11466 | 0.97798 | -0.15415 | 0.97845 | -0.15083 | 14.1558
96 | 0.047865 | 0.011998 | -0.047852 | -0.011994 | 1.2168e-05 | 4.2673e-06 | 0.072931 | 0.072931 | 0.072931 | 0.9766 | -0.16404 | 0.97634 | -0.16588 | 9.0038
97 | -0.081476 | -0.020444 | 0.081514 | 0.020458 | 3.812e-05 | 1.4212e-05 | 0.12392 | 0.12392 | 0.12392 | 0.97845 | -0.15083 | 0.97892 | -0.14746 | 15.2983
98 | 0.047224 | 0.011836 | -0.047215 | -0.011833 | 9.1503e-06 | 3.2008e-06 | 0.071973 | 0.071973 | 0.071973 | 0.97634 | -0.16588 | 0.97615 | -0.16728 | 8.8855
99 | -0.082707 | -0.020757 | 0.082963 | 0.020852 | 0.0002567 | 9.5778e-05 | 0.12573 | 0.12573 | 0.12573 | 0.97892 | -0.14746 | 0.98205 | -0.12517 | 15.5221
100 | 0.045875 | 0.011497 | -0.045857 | -0.011491 | 1.8873e-05 | 6.5632e-06 | 0.069931 | 0.069932 | 0.069932 | 0.97615 | -0.16728 | 0.97573 | -0.17025 | 8.6335
101 | 0.036063 | 0.0090373 | -0.036051 | -0.0090333 | 1.2334e-05 | 4.0094e-06 | 0.054996 | 0.054997 | 0.054997 | 0.97573 | -0.17025 | 0.97539 | -0.17272 | 6.7897
102 | 0.0097937 | 0.0024536 | -0.0097925 | -0.0024533 | 1.1973e-06 | 3.5307e-07 | 0.014935 | 0.014935 | 0.014935 | 0.97573 | -0.17025 | 0.97561 | -0.17113 | 5.5316
103 | 0.034146 | 0.0085559 | -0.034135 | -0.0085523 | 1.1319e-05 | 3.6028e-06 | 0.052091 | 0.052091 | 0.052091 | 0.97539 | -0.17272 | 0.97506 | -0.17512 | 6.431
104 | 0.0058579 | 0.0014672 | -0.0058567 | -0.001467 | 1.1915e-06 | 1.5962e-07 | 0.0089342 | 0.0089343 | 0.0089343 | 0.97561 | -0.17113 | 0.97541 | -0.17261 | 3.309
105 | 0.03187 | 0.0079848 | -0.031856 | -0.0079803 | 1.4509e-05 | 4.4775e-06 | 0.048636 | 0.048636 | 0.048636 | 0.97506 | -0.17512 | 0.9746 | -0.17841 | 6.0044
106 | 0.00048829 | 0.0001219 | -0.00048828 | -0.00012237 | 1.3293e-08 | -4.7418e-07 | 0.00074474 | 0.00074491 | 0.00074491 | 0.97541 | -0.17261 | 0.97538 | -0.1728 | 0.27589
107 | 0.0053684 | 0.0013451 | -0.0053682 | -0.0013451 | 2.1114e-07 | 1.8238e-08 | 0.0081895 | 0.0081896 | 0.0081896 | 0.97541 | -0.17261 | 0.97537 | -0.17289 | 3.0332
108 | 0.028256 | 0.0070782 | -0.028256 | -0.0070781 | 5.4752e-07 | 1.5771e-07 | 0.04314 | 0.04314 | 0.04314 | 0.9746 | -0.17841 | 0.97458 | -0.17855 | 5.326
109 | 0.0053682 | 0.0013451 | -0.0053676 | -0.001345 | 5.8677e-07 | 5.0713e-08 | 0.0081896 | 0.0081896 | 0.0081896 | 0.97537 | -0.17289 | 0.97526 | -0.17368 | 3.0332
110 | 0.0033783 | 0.00084647 | -0.003378 | -0.0008466 | 3.5312e-07 | -1.2993e-07 | 0.0051544 | 0.0051545 | 0.0051545 | 0.97526 | -0.17368 | 0.97515 | -0.17443 | 1.9091
111 | 0.020623 | 0.0051699 | -0.020623 | -0.0051699 | 2.2438e-07 | 8.1353e-08 | 0.030785 | 0.030785 | 0.030785 | 0.99685 | -0.021894 | 0.99684 | -0.021973 | 11.4018
112 | -0.023547 | -0.0059029 | 0.023586 | 0.0059172 | 3.8968e-05 | 1.4328e-05 | 0.03515 | 0.03515 | 0.03515 | 0.99685 | -0.021894 | 0.99855 | -0.0099647 | 13.0186
113 | 0.018595 | 0.0046616 | -0.018584 | -0.0046576 | 1.1191e-05 | 4.0011e-06 | 0.027758 | 0.027758 | 0.027758 | 0.99684 | -0.021973 | 0.99622 | -0.02632 | 10.2806
114 | 0.151 | 0.038225 | -0.15065 | -0.038091 | 0.0003504 | 0.00013347 | 0.22515 | 0.22515 | 0.22515 | 0.99855 | -0.0099647 | 0.99616 | -0.026431 | 27.7967
115 | 0.016102 | 0.0040355 | -0.016092 | -0.0040323 | 9.2299e-06 | 3.2172e-06 | 0.02405 | 0.02405 | 0.02405 | 0.99622 | -0.02632 | 0.99563 | -0.030463 | 8.9075
116 | 0.012733 | 0.0031905 | -0.012732 | -0.0031901 | 1.3371e-06 | 4.3735e-07 | 0.01903 | 0.01903 | 0.01903 | 0.99563 | -0.030463 | 0.99552 | -0.031222 | 7.0483
117 | 0.012214 | 0.0030601 | -0.012209 | -0.0030586 | 4.7064e-06 | 1.516e-06 | 0.018255 | 0.018256 | 0.018256 | 0.99552 | -0.031222 | 0.99513 | -0.034008 | 6.7613
118 | 0.010707 | 0.0026812 | -0.0107 | -0.0026788 | 7.6195e-06 | 2.3666e-06 | 0.016383 | 0.016383 | 0.016383 | 0.97245 | -0.19399 | 0.97173 | -0.19914 | 6.0679
119 | 0.0072554 | 0.0018162 | -0.0072544 | -0.001816 | 9.7916e-07 | 2.1912e-07 | 0.011109 | 0.01111 | 0.01111 | 0.97173 | -0.19914 | 0.9716 | -0.20012 | 4.1146
120 | 0.0034442 | 0.00086258 | -0.0034431 | -0.00086293 | 1.0706e-06 | -3.5209e-07 | 0.0052739 | 0.0052742 | 0.0052742 | 0.97173 | -0.19914 | 0.97142 | -0.20139 | 1.9534
121 | 0.0045935 | 0.0011497 | -0.0045934 | -0.0011497 | 6.7177e-08 | -1.1064e-09 | 0.0070344 | 0.0070344 | 0.0070344 | 0.9716 | -0.20012 | 0.97158 | -0.20023 | 2.6053
122 | 0.002661 | 0.00066631 | -0.0026607 | -0.00066649 | 2.209e-07 | -1.7902e-07 | 0.0040751 | 0.0040752 | 0.0040752 | 0.9716 | -0.20012 | 0.97151 | -0.20072 | 1.5093
123 | 0.0021754 | 0.00054369 | -0.0021752 | -0.00054392 | 1.6649e-07 | -2.337e-07 | 0.0033312 | 0.0033313 | 0.0033313 | 0.97158 | -0.20023 | 0.97151 | -0.20078 | 1.2338
124 | 0.0012007 | 0.00030058 | -0.0012007 | -0.00030092 | 6.2941e-08 | -3.4506e-07 | 0.001839 | 0.0018391 | 0.0018391 | 0.97151 | -0.20072 | 0.97146 | -0.2011 | 0.68116
125 | 0.001101 | 0.00027469 | -0.0011009 | -0.00027523 | 8.2061e-08 | -5.4122e-07 | 0.0016859 | 0.0016861 | 0.0016861 | 0.97151 | -0.20078 | 0.97143 | -0.20132 | 0.62449
126 | 0.0011009 | 0.00027523 | -0.0011009 | -0.00027532 | 1.2988e-08 | -8.564e-08 | 0.0016861 | 0.0016862 | 0.0016862 | 0.97143 | -0.20132 | 0.97142 | -0.20141 | 0.6245
127 | 0.0011009 | 0.00027532 | -0.0011008 | -0.00027589 | 8.7518e-08 | -5.7692e-07 | 0.0016862 | 0.0016864 | 0.0016864 | 0.97142 | -0.20141 | 0.97134 | -0.20198 | 0.62459
128 | -0.00089211 | -0.00022358 | 0.00089215 | 0.00022317 | 4.0567e-08 | -4.1532e-07 | 0.0013666 | 0.0013665 | 0.0013666 | 0.97133 | -0.20195 | 0.97138 | -0.20162 | 0.50617
129 | 0.14109 | 0.03555 | -0.14057 | -0.035352 | 0.00051979 | 0.0001978 | 0.21252 | 0.21252 | 0.21252 | 0.98819 | -0.08189 | 0.98444 | -0.10832 | 26.2374
130 | 0.025865 | 0.0064788 | -0.025859 | -0.0064773 | 5.6284e-06 | 1.5162e-06 | 0.03949 | 0.03949 | 0.03949 | 0.97458 | -0.17855 | 0.97436 | -0.18012 | 4.8753
131 | 0.023278 | 0.0058305 | -0.023275 | -0.0058298 | 3.0366e-06 | 7.3632e-07 | 0.035549 | 0.035549 | 0.035549 | 0.97436 | -0.18012 | 0.97423 | -0.18107 | 4.3888
132 | 0.023014 | 0.0057643 | -0.023014 | -0.0057643 | 9.93e-08 | 2.3758e-08 | 0.03515 | 0.03515 | 0.03515 | 0.97423 | -0.18107 | 0.97423 | -0.1811 | 4.3395
133 | 0.022752 | 0.0056987 | -0.022747 | -0.0056974 | 5.2102e-06 | 1.2292e-06 | 0.03475 | 0.03475 | 0.03475 | 0.97423 | -0.1811 | 0.974 | -0.18275 | 4.2902
134 | 0.020798 | 0.005209 | -0.020795 | -0.0052083 | 3.5232e-06 | 7.2872e-07 | 0.031773 | 0.031773 | 0.031773 | 0.974 | -0.18275 | 0.97382 | -0.18398 | 3.9226
135 | 0.083158 | 0.020925 | -0.082963 | -0.020852 | 0.00019513 | 7.2793e-05 | 0.12573 | 0.12573 | 0.12573 | 0.98444 | -0.10832 | 0.98205 | -0.12517 | 15.522
136 | -0.016853 | -0.0042215 | 0.016857 | 0.0042219 | 3.862e-06 | 4.4218e-07 | 0.025764 | 0.025764 | 0.025764 | 0.97332 | -0.18759 | 0.97355 | -0.18593 | 3.1808
137 | -0.01811 | -0.004536 | 0.018115 | 0.0045366 | 4.4413e-06 | 6.6824e-07 | 0.027679 | 0.027679 | 0.027679 | 0.97355 | -0.18593 | 0.9738 | -0.18415 | 3.4172
138 | 0.020242 | 0.0050698 | -0.020242 | -0.0050697 | 4.8873e-07 | 9.6297e-08 | 0.030929 | 0.030929 | 0.030929 | 0.97382 | -0.18398 | 0.9738 | -0.18415 | 3.8184

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.17718 | 0.044622

## res_load
| p_mw | q_mvar
0 | 0.0010404 | 0.00026076
1 | 0.000479 | 0.00012005
2 | 0.00078825 | 0.00019755
3 | 0.0011234 | 0.00028154
4 | 0.00088772 | 0.00022248
5 | 0.00065431 | 0.00016398
6 | 0.0011745 | 0.00029436
7 | 0.00076454 | 0.00019161
8 | 0.00021278 | 5.3328e-05
9 | 0.0017814 | 0.00044645
10 | 0.00046375 | 0.00011623
11 | 0.0005748 | 0.00014406
12 | 0.00031836 | 7.9788e-05
13 | 0.0010318 | 0.0002586
14 | 0.00071833 | 0.00018003
15 | 0.00064278 | 0.0001611
16 | 0.00050443 | 0.00012642
17 | 0.0006425 | 0.00016103
18 | 0.00087916 | 0.00022034
19 | 0.00085325 | 0.00021385
20 | 0.0010212 | 0.00025595
21 | 0.00061324 | 0.00015369
22 | 0.00060078 | 0.00015057
23 | 0.00090305 | 0.00022633
24 | 0.0019011 | 0.00047647
25 | 0.0016724 | 0.00041914
26 | 0.0021994 | 0.00055121
27 | 0.0010278 | 0.00025759
28 | 0.0018204 | 0.00045624
29 | 0.001368 | 0.00034286
30 | 0.001026 | 0.00025715
31 | 0.0011966 | 0.00029991
32 | 0.00028226 | 7.0741e-05
33 | 0.001223 | 0.00030652
34 | 0.0029951 | 0.00075064
35 | 0.0018152 | 0.00045494
36 | 0.0025305 | 0.0006342
37 | 0.0021056 | 0.0005277
38 | 0.00051969 | 0.00013025
39 | 0.0017555 | 0.00043997
40 | 0.0023532 | 0.00058976
41 | 0.00051665 | 0.00012949
42 | 0.00038361 | 9.6142e-05
43 | 0.001253 | 0.00031404
44 | 0.0017861 | 0.00044764
45 | 0.0010953 | 0.00027452
46 | 0.0022584 | 0.00056601
47 | 0.0024752 | 0.00062035
48 | 0.0031103 | 0.00077951
49 | 0.00071807 | 0.00017996
50 | 0.00066137 | 0.00016576
51 | 0.00088899 | 0.0002228
52 | 0.00097719 | 0.00024491
53 | 0.0014293 | 0.00035822
54 | 0.00029636 | 7.4275e-05
55 | 0.00044404 | 0.00011129
56 | 0.00036941 | 9.2582e-05
57 | 0.00037934 | 9.5072e-05
58 | 0.00064275 | 0.00016109
59 | 0.0012642 | 0.00031683
60 | 0.0010138 | 0.00025407
61 | 0.00073194 | 0.00018344
62 | 0.00085226 | 0.0002136
63 | 0.00070858 | 0.00017759
64 | 0.00079524 | 0.0001993
65 | 0.0014289 | 0.00035812
66 | 0.0040093 | 0.0010048
67 | 0.020839 | 0.0052228
68 | 0.00036483 | 9.1435e-05
69 | 0.00055393 | 0.00013883
70 | 0.0010346 | 0.0002593
71 | 0.00053338 | 0.00013368
72 | 0.0060855 | 0.0015252
73 | 0.00062866 | 0.00015756
74 | 0.0011927 | 0.00029892
75 | 0.0013392 | 0.00033564
76 | 0.0019047 | 0.00047735
77 | 0.0039346 | 0.0009861
78 | 0.0022644 | 0.00056751
79 | 0.0035994 | 0.0009021
80 | 0.00048828 | 0.00012237
81 | 0.0019893 | 0.00049856
82 | 0.003378 | 0.0008466
83 | 0.0029245 | 0.00073295
84 | 0.002028 | 0.00050825
85 | 0.0024821 | 0.00062208
86 | 0.0024685 | 0.00061868
87 | 0.0033589 | 0.00084182
88 | 0.00051843 | 0.00012993
89 | 0.00090261 | 0.00022622
90 | 0.0034431 | 0.00086293
91 | 0.002418 | 0.00060601
92 | 0.00146 | 0.00036591
93 | 0.0010742 | 0.00026923
94 | 0.0011008 | 0.00027589
95 | 0.0012007 | 0.00030092
96 | 0.0058573 | 0.001468
97 | 0.00089211 | 0.00022358
98 | 0.00090763 | 0.00022747
99 | 0.00039639 | 9.9345e-05
100 | 0.0023911 | 0.00059926
101 | 0.0025806 | 0.00064675
102 | 0.00026144 | 6.5524e-05
103 | 0.00026173 | 6.5596e-05
104 | 0.0019487 | 0.0004884
105 | 0.00086981 | 0.00021799
106 | 0.0012531 | 0.00031406
107 | 0.00055268 | 0.00013851
108 | 0.002127 | 0.00053307

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1