## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2428-4_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2428-4_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2428-4_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2428-4_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2428-4_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2428-4_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2428-4_0_3_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2428-4_0_3_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_2428-4_0_3_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_2428-4_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2428-4_0_3_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_2428-4_0_3_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_2428-4_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2428-4_0_3_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_2428-4_0_3_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_2428-4_0_3_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_2428-4_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2428-4_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2428-4_0_3_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_2428-4_0_3_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_2428-4_0_3_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_2428-4_0_3_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_2428-4_0_3_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_2428-4_0_3_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_2428-4_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_2428-4_0_3_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_2428-4_0_3_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_2428-4_0_3_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_2428-4_0_3_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_2428-4_0_3_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_2428-4_0_3_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_2428-4_0_3_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_2428-4_0_3_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_2428-4_0_3_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_2428-4_0_3_node_36 | 0.4 | n |  | TRUE
35 | bus_MV_333_0_node_171 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2428-4_0_3_load_0 | 0 | 0.0013107 | 0.00032849 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2428-4_0_3_load_1 | 1 | 0.011475 | 0.002876 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2428-4_0_3_load_3 | 3 | 0.014509 | 0.0036362 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2428-4_0_3_load_4 | 4 | 0.0023033 | 0.00057725 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2428-4_0_3_load_5 | 5 | 0.00052778 | 0.00013227 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2428-4_0_3_load_7 | 6 | 0.00088328 | 0.00022137 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2428-4_0_3_load_15 | 7 | 0.0037208 | 0.00093253 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2428-4_0_3_load_24 | 11 | 0.0046552 | 0.0011667 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2428-4_0_3_load_14 | 13 | 0.0017198 | 0.00043103 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2428-4_0_3_load_21 | 14 | 0.00026934 | 6.7504e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2428-4_0_3_load_18 | 15 | 0.017226 | 0.0043172 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2428-4_0_3_load_13 | 16 | 0.017422 | 0.0043663 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2428-4_0_3_load_9 | 17 | 0.014821 | 0.0037145 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2428-4_0_3_load_34 | 19 | 0.016761 | 0.0042007 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2428-4_0_3_load_12 | 22 | 0.015877 | 0.0039792 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2428-4_0_3_load_10 | 23 | 0.015439 | 0.0038694 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2428-4_0_3_load_16 | 24 | 0.0038867 | 0.00097409 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2428-4_0_3_load_17 | 25 | 0.0010682 | 0.0002677 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2428-4_0_3_load_27 | 26 | 0.0011023 | 0.00027625 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2428-4_0_3_load_28 | 27 | 0.0091892 | 0.002303 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2428-4_0_3_load_26 | 28 | 0.0071977 | 0.0018039 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2428-4_0_3_load_31 | 30 | 0.0075132 | 0.001883 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2428-4_0_3_load_35 | 33 | 0.0076064 | 0.0019063 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2428-4_0_3_load_36 | 34 | 0.0035863 | 0.0008988 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2428-4_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.024319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2428-4_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0022843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2428-4_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.016146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2428-4_0_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.012521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2428-4_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.0062263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2428-4_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.0079744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2428-4_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.0049515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2428-4_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.01549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2428-4_0_3_line_8 | NAYY 4x150 SE | 6 | 12 | 0.026074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2428-4_0_3_line_9 | NAYY 4x150 SE | 7 | 13 | 0.011934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2428-4_0_3_line_10 | NAYY 4x150 SE | 8 | 14 | 0.0035512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2428-4_0_3_line_11 | NAYY 4x150 SE | 8 | 15 | 0.011374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2428-4_0_3_line_12 | NAYY 4x150 SE | 9 | 10 | 0.010455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2428-4_0_3_line_13 | NAYY 4x150 SE | 9 | 11 | 0.032294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2428-4_0_3_line_14 | NAYY 4x150 SE | 10 | 16 | 0.014727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2428-4_0_3_line_15 | NAYY 4x150 SE | 10 | 17 | 0.018648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2428-4_0_3_line_16 | NAYY 4x150 SE | 11 | 18 | 0.019332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2428-4_0_3_line_17 | NAYY 4x150 SE | 12 | 19 | 0.024056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2428-4_0_3_line_18 | NAYY 4x150 SE | 13 | 24 | 0.010685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2428-4_0_3_line_19 | NAYY 4x150 SE | 16 | 19 | 0.017776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2428-4_0_3_line_20 | NAYY 4x150 SE | 17 | 23 | 0.011949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2428-4_0_3_line_21 | NAYY 4x150 SE | 18 | 28 | 0.031322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2428-4_0_3_line_22 | NAYY 4x150 SE | 20 | 21 | 0.007375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2428-4_0_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.014901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2428-4_0_3_line_24 | NAYY 4x150 SE | 21 | 27 | 0.0091822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2428-4_0_3_line_25 | NAYY 4x150 SE | 22 | 23 | 0.0093524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2428-4_0_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.020196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2428-4_0_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.013077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2428-4_0_3_line_28 | NAYY 4x150 SE | 27 | 29 | 0.01452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2428-4_0_3_line_29 | NAYY 4x150 SE | 29 | 30 | 0.0035107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2428-4_0_3_line_30 | NAYY 4x150 SE | 30 | 31 | 0.021593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2428-4_0_3_line_31 | NAYY 4x150 SE | 31 | 32 | 0.033095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2428-4_0_3_line_32 | NAYY 4x150 SE | 32 | 33 | 0.02208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2428-4_0_3_line_33 | NAYY 4x150 SE | 33 | 34 | 0.018255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2428-4_0_3_trafo_11 | 0.25 MVA 20/0.4 kV | 35 | 10 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2619929.7907 | 1243397.4001 | 2619906.0156 | 1243402.514
1 | 2619903.7823 | 1243402.9944 | 2619906.0156 | 1243402.514
2 | 2619929.7907 | 1243397.4001 | 2619945.4427 | 1243393.4385
3 | 2619929.7907 | 1243397.4001 | 2619927.3247 | 1243385.1247
4 | 2619903.7823 | 1243402.9944 | 2619897.6959 | 1243404.3065
5 | 2619945.4427 | 1243393.4385 | 2619948.042 | 1243392.7806 | 2619953.314 | 1243392.3079
6 | 2619926.3494 | 1243380.2703 | 2619927.3247 | 1243385.1247
7 | 2619882.5536 | 1243407.5708 | 2619897.6959 | 1243404.3065
8 | 2619975.5104 | 1243404.8026 | 2619968.9096 | 1243399.0212 | 2619961.1263 | 1243394.281 | 2619957.3004 | 1243392.5893 | 2619953.7798 | 1243392.2662 | 2619953.314 | 1243392.3079
9 | 2619926.3494 | 1243380.2703 | 2619924.8624 | 1243372.8681 | 2619923.5188 | 1243370.1285 | 2619922.7675 | 1243369.0283
10 | 2619882.5536 | 1243407.5708 | 2619879.085 | 1243408.332
11 | 2619882.5536 | 1243407.5708 | 2619883.9815 | 1243414.4799 | 2619884.0153 | 1243415.6919 | 2619883.6942 | 1243416.7915 | 2619883.0796 | 1243417.5233 | 2619882.2151 | 1243418.0358
12 | 2619925.8737 | 1243431.9089 | 2619916.5847 | 1243436.7586
13 | 2619916.5847 | 1243436.7586 | 2619914.6695 | 1243437.7084 | 2619912.4591 | 1243438.8017 | 2619887.1043 | 1243449.9322
14 | 2619925.8737 | 1243431.9089 | 2619938.8377 | 1243424.921
15 | 2619925.8737 | 1243431.9089 | 2619927.2378 | 1243435.3045 | 2619932.8199 | 1243449.2144
16 | 2619869.4026 | 1243457.703 | 2619887.1043 | 1243449.9322
17 | 2619975.5104 | 1243404.8026 | 2619966.4618 | 1243410.0311 | 2619954.4855 | 1243416.4865
18 | 2619913.4076 | 1243364.8821 | 2619915.7219 | 1243364.9325 | 2619918.5835 | 1243365.7203 | 2619920.6502 | 1243366.9169 | 2619922.2328 | 1243368.2452 | 2619922.7675 | 1243369.0283
19 | 2619938.8377 | 1243424.921 | 2619954.4855 | 1243416.4865
20 | 2619932.8199 | 1243449.2144 | 2619937.2703 | 1243460.3041
21 | 2619869.4026 | 1243457.703 | 2619880.497 | 1243487.0031
22 | 2619947.0686 | 1243489.2162 | 2619948.1813 | 1243481.9264
23 | 2619948.1813 | 1243481.9264 | 2619944.2741 | 1243475.1979 | 2619941.1031 | 1243468.8228
24 | 2619947.0686 | 1243489.2162 | 2619942.4027 | 1243497.1245
25 | 2619941.1031 | 1243468.8228 | 2619940.0254 | 1243466.6561 | 2619939.2517 | 1243465.2415 | 2619937.2703 | 1243460.3041
26 | 2619913.4076 | 1243364.8821 | 2619900.0037 | 1243364.5908 | 2619893.2179 | 1243364.383
27 | 2619893.2179 | 1243364.383 | 2619891.4421 | 1243364.3286 | 2619887.5074 | 1243363.5039 | 2619884.345 | 1243362.2814 | 2619881.0569 | 1243360.2024
28 | 2619935.7462 | 1243510.0248 | 2619941.3075 | 1243498.9808 | 2619942.4027 | 1243497.1245
29 | 2619935.7462 | 1243510.0248 | 2619933.7386 | 1243512.9048
30 | 2619920.4066 | 1243529.8637 | 2619921.6973 | 1243528.1003 | 2619929.8003 | 1243518.5547 | 2619933.7386 | 1243512.9048
31 | 2619920.4066 | 1243529.8637 | 2619899.4856 | 1243555.5545
32 | 2619899.4856 | 1243555.5545 | 2619886.0537 | 1243538.0298
33 | 2619874.9488 | 1243523.5411 | 2619886.0537 | 1243538.0298

## bus_geodata
| x | y | coords
0 | 2619906.0156 | 1243402.514
1 | 2619929.7907 | 1243397.4001
2 | 2619903.7823 | 1243402.9944
3 | 2619945.4427 | 1243393.4385
4 | 2619927.3247 | 1243385.1247
5 | 2619897.6959 | 1243404.3065
6 | 2619953.314 | 1243392.3079
7 | 2619926.3494 | 1243380.2703
8 | 2619882.5536 | 1243407.5708
9 | 2619916.5847 | 1243436.7586
10 | 2619925.8737 | 1243431.9089
11 | 2619887.1043 | 1243449.9322
12 | 2619975.5104 | 1243404.8026
13 | 2619922.7675 | 1243369.0283
14 | 2619879.085 | 1243408.332
15 | 2619882.2151 | 1243418.0358
16 | 2619938.8377 | 1243424.921
17 | 2619932.8199 | 1243449.2144
18 | 2619869.4026 | 1243457.703
19 | 2619954.4855 | 1243416.4865
20 | 2619948.1813 | 1243481.9264
21 | 2619947.0686 | 1243489.2162
22 | 2619941.1031 | 1243468.8228
23 | 2619937.2703 | 1243460.3041
24 | 2619913.4076 | 1243364.8821
25 | 2619893.2179 | 1243364.383
26 | 2619881.0569 | 1243360.2024
27 | 2619942.4027 | 1243497.1245
28 | 2619880.497 | 1243487.0031
29 | 2619935.7462 | 1243510.0248
30 | 2619933.7386 | 1243512.9048
31 | 2619920.4066 | 1243529.8637
32 | 2619899.4856 | 1243555.5545
33 | 2619886.0537 | 1243538.0298
34 | 2619874.9488 | 1243523.5411
35 | 2619916.5847 | 1243436.7586

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98932 | -0.074888 | 0.0013107 | 0.00032849
1 | 0.99 | -0.070096 | 0.011475 | 0.002876
2 | 0.98926 | -0.075308 | 0 | 0
3 | 0.99103 | -0.062767 | 0.014509 | 0.0036362
4 | 0.98975 | -0.071857 | 0.0023033 | 0.00057725
5 | 0.9891 | -0.076453 | 0.00052778 | 0.00013227
6 | 0.99171 | -0.057978 | 0.00088328 | 0.00022137
7 | 0.98967 | -0.072437 | 0.0037208 | 0.00093253
8 | 0.98871 | -0.079219 | 0 | 0
9 | 0.99982 | -0.0012379 | 0 | 0
10 | 1 | 0 | -0.18187 | -0.045507
11 | 0.99928 | -0.0050637 | 0.0046552 | 0.0011667
12 | 0.99397 | -0.042134 | 0 | 0
13 | 0.98953 | -0.073383 | 0.0017198 | 0.00043103
14 | 0.9887 | -0.079229 | 0.00026934 | 6.7504e-05
15 | 0.98842 | -0.08122 | 0.017226 | 0.0043172
16 | 0.99801 | -0.013875 | 0.017422 | 0.0043663
17 | 0.99802 | -0.013808 | 0.014821 | 0.0037145
18 | 0.99908 | -0.0064555 | 0 | 0
19 | 0.99604 | -0.027578 | 0.016761 | 0.0042007
20 | 0.99583 | -0.029204 | 0 | 0
21 | 0.99553 | -0.031276 | 0 | 0
22 | 0.99643 | -0.025021 | 0.015877 | 0.0039792
23 | 0.99701 | -0.020907 | 0.015439 | 0.0038694
24 | 0.98944 | -0.074044 | 0.0038867 | 0.00097409
25 | 0.98938 | -0.074491 | 0.0010682 | 0.0002677
26 | 0.98935 | -0.074638 | 0.0011023 | 0.00027625
27 | 0.99517 | -0.033857 | 0.0091892 | 0.002303
28 | 0.99876 | -0.0087109 | 0.0071977 | 0.0018039
29 | 0.99478 | -0.036597 | 0 | 0
30 | 0.99468 | -0.037259 | 0.0075132 | 0.001883
31 | 0.99434 | -0.0397 | 0 | 0
32 | 0.99381 | -0.043443 | 0 | 0
33 | 0.99345 | -0.045942 | 0.0076064 | 0.0019063
34 | 0.99336 | -0.046604 | 0.0035863 | 0.0008988
35 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.019349 | -0.0048509 | 0.019362 | 0.0048555 | 1.2853e-05 | 4.6309e-06 | 0.029103 | 0.029103 | 0.029103 | 0.98932 | -0.074888 | 0.99 | -0.070096 | 10.7789
1 | 0.018038 | 0.0045224 | -0.018037 | -0.004522 | 1.0493e-06 | 3.7424e-07 | 0.027132 | 0.027132 | 0.027132 | 0.98932 | -0.074888 | 0.98926 | -0.075308 | 10.0487
2 | -0.044644 | -0.011192 | 0.04469 | 0.011209 | 4.5366e-05 | 1.7241e-05 | 0.067104 | 0.067103 | 0.067104 | 0.99 | -0.070096 | 0.99103 | -0.062767 | 24.8532
3 | 0.013807 | 0.0034602 | -0.013804 | -0.0034591 | 3.3648e-06 | 1.1332e-06 | 0.020753 | 0.020753 | 0.020753 | 0.99 | -0.070096 | 0.98975 | -0.071857 | 7.6862
4 | 0.018037 | 0.004522 | -0.018034 | -0.004521 | 2.86e-06 | 1.0201e-06 | 0.027132 | 0.027132 | 0.027132 | 0.98926 | -0.075308 | 0.9891 | -0.076453 | 10.0487
5 | -0.059198 | -0.014845 | 0.059238 | 0.01486 | 3.9316e-05 | 1.5019e-05 | 0.088888 | 0.088888 | 0.088888 | 0.99103 | -0.062767 | 0.99171 | -0.057978 | 32.9215
6 | 0.0115 | 0.0028818 | -0.011499 | -0.0028816 | 9.2364e-07 | 2.9162e-07 | 0.01729 | 0.01729 | 0.01729 | 0.98975 | -0.071857 | 0.98967 | -0.072437 | 6.4037
7 | 0.017507 | 0.0043887 | -0.0175 | -0.0043863 | 6.7049e-06 | 2.3801e-06 | 0.026338 | 0.026338 | 0.026338 | 0.9891 | -0.076453 | 0.98871 | -0.079219 | 9.7547
8 | -0.060121 | -0.015082 | 0.060253 | 0.015132 | 0.00013241 | 5.0591e-05 | 0.090213 | 0.090213 | 0.090213 | 0.99171 | -0.057978 | 0.99397 | -0.042134 | 33.4123
9 | 0.0077786 | 0.001949 | -0.0077776 | -0.0019488 | 1.0186e-06 | 2.3844e-07 | 0.011695 | 0.011695 | 0.011695 | 0.98967 | -0.072437 | 0.98953 | -0.073383 | 4.3317
10 | 0.00026934 | 6.7458e-05 | -0.00026934 | -6.7504e-05 | 3.6409e-10 | -4.5403e-08 | 0.00040535 | 0.00040537 | 0.00040537 | 0.98871 | -0.079219 | 0.9887 | -0.079229 | 0.15014
11 | 0.01723 | 0.0043189 | -0.017226 | -0.0043172 | 4.7728e-06 | 1.6899e-06 | 0.025932 | 0.025932 | 0.025932 | 0.98871 | -0.079219 | 0.98842 | -0.08122 | 9.6046
12 | -0.011863 | -0.0029734 | 0.011865 | 0.002974 | 2.0336e-06 | 6.4501e-07 | 0.017655 | 0.017655 | 0.017655 | 0.99982 | -0.0012379 | 1 | 0 | 6.539
13 | 0.011863 | 0.0029734 | -0.011857 | -0.0029714 | 6.2815e-06 | 1.9927e-06 | 0.017655 | 0.017656 | 0.017656 | 0.99982 | -0.0012379 | 0.99928 | -0.0050637 | 6.5391
14 | 0.094889 | 0.023873 | -0.094706 | -0.023802 | 0.0001833 | 7.0306e-05 | 0.14123 | 0.14123 | 0.14123 | 1 | 0 | 0.99801 | -0.013875 | 52.3068
15 | 0.074315 | 0.01866 | -0.074172 | -0.018606 | 0.00014232 | 5.4495e-05 | 0.11059 | 0.11059 | 0.11059 | 1 | 0 | 0.99802 | -0.013808 | 40.9608
16 | 0.0072014 | 0.0018047 | -0.0072 | -0.0018044 | 1.3872e-06 | 2.8033e-07 | 0.010723 | 0.010724 | 0.010724 | 0.99928 | -0.0050637 | 0.99908 | -0.0064555 | 3.9717
17 | -0.060253 | -0.015132 | 0.060375 | 0.015179 | 0.00012216 | 4.6674e-05 | 0.090213 | 0.090213 | 0.090213 | 0.99397 | -0.042134 | 0.99604 | -0.027578 | 33.4123
18 | 0.0060578 | 0.0015178 | -0.0060572 | -0.0015177 | 5.5329e-07 | 7.5549e-08 | 0.0091093 | 0.0091093 | 0.0091093 | 0.98953 | -0.073383 | 0.98944 | -0.074044 | 3.3738
19 | 0.077284 | 0.019436 | -0.077137 | -0.01938 | 0.00014734 | 5.6438e-05 | 0.11525 | 0.11525 | 0.11525 | 0.99801 | -0.013875 | 0.99604 | -0.027578 | 42.6863
20 | 0.059351 | 0.014892 | -0.059293 | -0.014869 | 5.8396e-05 | 2.2304e-05 | 0.088497 | 0.088497 | 0.088497 | 0.99802 | -0.013808 | 0.99701 | -0.020907 | 32.7765
21 | 0.0072 | 0.0018044 | -0.0071977 | -0.0018039 | 2.2476e-06 | 4.5442e-07 | 0.010724 | 0.010724 | 0.010724 | 0.99908 | -0.0064555 | 0.99876 | -0.0087109 | 3.9717
22 | 0.027936 | 0.0070051 | -0.027928 | -0.0070021 | 8.0193e-06 | 2.9884e-06 | 0.041744 | 0.041744 | 0.041744 | 0.99583 | -0.029204 | 0.99553 | -0.031276 | 15.4608
23 | -0.027936 | -0.0070051 | 0.027952 | 0.0070111 | 1.6203e-05 | 6.0378e-06 | 0.041744 | 0.041744 | 0.041744 | 0.99583 | -0.029204 | 0.99643 | -0.025021 | 15.4608
24 | 0.027928 | 0.0070021 | -0.027918 | -0.0069984 | 9.9844e-06 | 3.7208e-06 | 0.041744 | 0.041744 | 0.041744 | 0.99553 | -0.031276 | 0.99517 | -0.033857 | 15.4608
25 | -0.043829 | -0.01099 | 0.043854 | 0.011 | 2.5003e-05 | 9.4945e-06 | 0.065454 | 0.065454 | 0.065454 | 0.99643 | -0.025021 | 0.99701 | -0.020907 | 24.2424
26 | 0.0021706 | 0.00054359 | -0.0021704 | -0.0005438 | 1.3428e-07 | -2.0773e-07 | 0.0032642 | 0.0032643 | 0.0032643 | 0.98944 | -0.074044 | 0.98938 | -0.074491 | 1.209
27 | 0.0011023 | 0.00027609 | -0.0011023 | -0.00027625 | 2.2427e-08 | -1.5931e-07 | 0.0016578 | 0.0016578 | 0.0016578 | 0.98938 | -0.074491 | 0.98935 | -0.074638 | 0.61401
28 | 0.018728 | 0.0046954 | -0.018721 | -0.0046928 | 7.1057e-06 | 2.5444e-06 | 0.028004 | 0.028004 | 0.028004 | 0.99517 | -0.033857 | 0.99478 | -0.036597 | 10.3719
29 | 0.018721 | 0.0046928 | -0.01872 | -0.0046922 | 1.718e-06 | 6.152e-07 | 0.028004 | 0.028004 | 0.028004 | 0.99478 | -0.036597 | 0.99468 | -0.037259 | 10.3719
30 | 0.011206 | 0.0028092 | -0.011203 | -0.002808 | 3.787e-06 | 1.1764e-06 | 0.016765 | 0.016765 | 0.016765 | 0.99468 | -0.037259 | 0.99434 | -0.0397 | 6.2092
31 | 0.011203 | 0.002808 | -0.011197 | -0.0028062 | 5.8043e-06 | 1.8034e-06 | 0.016765 | 0.016765 | 0.016765 | 0.99434 | -0.0397 | 0.99381 | -0.043443 | 6.2092
32 | 0.011197 | 0.0028062 | -0.011193 | -0.002805 | 3.8725e-06 | 1.2034e-06 | 0.016765 | 0.016765 | 0.016765 | 0.99381 | -0.043443 | 0.99345 | -0.045942 | 6.2093
33 | 0.0035866 | 0.00089869 | -0.0035863 | -0.0008988 | 3.2873e-07 | -1.0991e-07 | 0.005372 | 0.0053721 | 0.0053721 | 0.99345 | -0.045942 | 0.99336 | -0.046604 | 1.9897

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18187 | 0.045507

## res_load
| p_mw | q_mvar
0 | 0.0013107 | 0.00032849
1 | 0.011475 | 0.002876
2 | 0.014509 | 0.0036362
3 | 0.0023033 | 0.00057725
4 | 0.00052778 | 0.00013227
5 | 0.00088328 | 0.00022137
6 | 0.0037208 | 0.00093253
7 | 0.0046552 | 0.0011667
8 | 0.0017198 | 0.00043103
9 | 0.00026934 | 6.7504e-05
10 | 0.017226 | 0.0043172
11 | 0.017422 | 0.0043663
12 | 0.014821 | 0.0037145
13 | 0.016761 | 0.0042007
14 | 0.015877 | 0.0039792
15 | 0.015439 | 0.0038694
16 | 0.0038867 | 0.00097409
17 | 0.0010682 | 0.0002677
18 | 0.0011023 | 0.00027625
19 | 0.0091892 | 0.002303
20 | 0.0071977 | 0.0018039
21 | 0.0075132 | 0.001883
22 | 0.0076064 | 0.0019063
23 | 0.0035863 | 0.0008988

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1