## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2430-2_1_2_node_19 | 0.4 | n |  | TRUE
1 | bus_LV_2430-2_1_2_node_132 | 0.4 | n |  | TRUE
2 | bus_LV_2430-2_1_2_node_11 | 0.4 | n |  | TRUE
3 | bus_LV_2430-2_1_2_node_17 | 0.4 | n |  | TRUE
4 | bus_LV_2430-2_1_2_node_138 | 0.4 | n |  | TRUE
5 | bus_LV_2430-2_1_2_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_2430-2_1_2_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_2430-2_1_2_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_2430-2_1_2_node_57 | 0.4 | n |  | TRUE
9 | bus_LV_2430-2_1_2_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_2430-2_1_2_node_112 | 0.4 | n |  | TRUE
11 | bus_LV_2430-2_1_2_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_2430-2_1_2_node_131 | 0.4 | n |  | TRUE
13 | bus_LV_2430-2_1_2_node_152 | 0.4 | n |  | TRUE
14 | bus_LV_2430-2_1_2_node_61 | 0.4 | n |  | TRUE
15 | bus_LV_2430-2_1_2_node_58 | 0.4 | n |  | TRUE
16 | bus_LV_2430-2_1_2_node_91 | 0.4 | n |  | TRUE
17 | bus_LV_2430-2_1_2_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_2430-2_1_2_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_2430-2_1_2_node_110 | 0.4 | n |  | TRUE
20 | bus_LV_2430-2_1_2_node_64 | 0.4 | n |  | TRUE
21 | bus_LV_2430-2_1_2_node_59 | 0.4 | n |  | TRUE
22 | bus_LV_2430-2_1_2_node_65 | 0.4 | n |  | TRUE
23 | bus_LV_2430-2_1_2_node_66 | 0.4 | n |  | TRUE
24 | bus_LV_2430-2_1_2_node_90 | 0.4 | n |  | TRUE
25 | bus_LV_2430-2_1_2_node_98 | 0.4 | n |  | TRUE
26 | bus_LV_2430-2_1_2_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_2430-2_1_2_node_33 | 0.4 | n |  | TRUE
28 | bus_LV_2430-2_1_2_node_133 | 0.4 | n |  | TRUE
29 | bus_LV_2430-2_1_2_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_2430-2_1_2_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_2430-2_1_2_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_2430-2_1_2_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_2430-2_1_2_node_87 | 0.4 | n |  | TRUE
34 | bus_LV_2430-2_1_2_node_34 | 0.4 | n |  | TRUE
35 | bus_LV_2430-2_1_2_node_55 | 0.4 | n |  | TRUE
36 | bus_LV_2430-2_1_2_node_94 | 0.4 | n |  | TRUE
37 | bus_LV_2430-2_1_2_node_47 | 0.4 | n |  | TRUE
38 | bus_LV_2430-2_1_2_node_53 | 0.4 | n |  | TRUE
39 | bus_LV_2430-2_1_2_node_95 | 0.4 | n |  | TRUE
40 | bus_LV_2430-2_1_2_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_2430-2_1_2_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_2430-2_1_2_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_2430-2_1_2_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_2430-2_1_2_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_2430-2_1_2_node_51 | 0.4 | n |  | TRUE
46 | bus_LV_2430-2_1_2_node_92 | 0.4 | n |  | TRUE
47 | bus_LV_2430-2_1_2_node_49 | 0.4 | n |  | TRUE
48 | bus_LV_2430-2_1_2_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_2430-2_1_2_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_2430-2_1_2_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_2430-2_1_2_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_2430-2_1_2_node_121 | 0.4 | n |  | TRUE
53 | bus_LV_2430-2_1_2_node_139 | 0.4 | n |  | TRUE
54 | bus_LV_2430-2_1_2_node_96 | 0.4 | n |  | TRUE
55 | bus_LV_2430-2_1_2_node_123 | 0.4 | n |  | TRUE
56 | bus_LV_2430-2_1_2_node_119 | 0.4 | n |  | TRUE
57 | bus_LV_2430-2_1_2_node_140 | 0.4 | n |  | TRUE
58 | bus_LV_2430-2_1_2_node_97 | 0.4 | n |  | TRUE
59 | bus_LV_2430-2_1_2_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_2430-2_1_2_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_2430-2_1_2_node_46 | 0.4 | n |  | TRUE
62 | bus_LV_2430-2_1_2_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_2430-2_1_2_node_107 | 0.4 | n |  | TRUE
64 | bus_LV_2430-2_1_2_node_106 | 0.4 | n |  | TRUE
65 | bus_LV_2430-2_1_2_node_50 | 0.4 | n |  | TRUE
66 | bus_LV_2430-2_1_2_node_52 | 0.4 | n |  | TRUE
67 | bus_LV_2430-2_1_2_node_82 | 0.4 | n |  | TRUE
68 | bus_LV_2430-2_1_2_node_56 | 0.4 | n |  | TRUE
69 | bus_LV_2430-2_1_2_node_54 | 0.4 | n |  | TRUE
70 | bus_LV_2430-2_1_2_node_111 | 0.4 | n |  | TRUE
71 | bus_LV_2430-2_1_2_node_109 | 0.4 | n |  | TRUE
72 | bus_LV_2430-2_1_2_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_2430-2_1_2_node_68 | 0.4 | n |  | TRUE
74 | bus_LV_2430-2_1_2_node_69 | 0.4 | n |  | TRUE
75 | bus_LV_2430-2_1_2_node_70 | 0.4 | n |  | TRUE
76 | bus_LV_2430-2_1_2_node_71 | 0.4 | n |  | TRUE
77 | bus_LV_2430-2_1_2_node_80 | 0.4 | n |  | TRUE
78 | bus_LV_2430-2_1_2_node_88 | 0.4 | n |  | TRUE
79 | bus_LV_2430-2_1_2_node_78 | 0.4 | n |  | TRUE
80 | bus_LV_2430-2_1_2_node_89 | 0.4 | n |  | TRUE
81 | bus_LV_2430-2_1_2_node_72 | 0.4 | n |  | TRUE
82 | bus_LV_2430-2_1_2_node_73 | 0.4 | n |  | TRUE
83 | bus_LV_2430-2_1_2_node_74 | 0.4 | n |  | TRUE
84 | bus_LV_2430-2_1_2_node_75 | 0.4 | n |  | TRUE
85 | bus_LV_2430-2_1_2_node_76 | 0.4 | n |  | TRUE
86 | bus_LV_2430-2_1_2_node_108 | 0.4 | n |  | TRUE
87 | bus_LV_2430-2_1_2_node_116 | 0.4 | n |  | TRUE
88 | bus_LV_2430-2_1_2_node_134 | 0.4 | n |  | TRUE
89 | bus_LV_2430-2_1_2_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_2430-2_1_2_node_117 | 0.4 | n |  | TRUE
91 | bus_LV_2430-2_1_2_node_77 | 0.4 | n |  | TRUE
92 | bus_LV_2430-2_1_2_node_79 | 0.4 | n |  | TRUE
93 | bus_LV_2430-2_1_2_node_129 | 0.4 | n |  | TRUE
94 | bus_LV_2430-2_1_2_node_130 | 0.4 | n |  | TRUE
95 | bus_LV_2430-2_1_2_node_93 | 0.4 | n |  | TRUE
96 | bus_LV_2430-2_1_2_node_150 | 0.4 | n |  | TRUE
97 | bus_LV_2430-2_1_2_node_151 | 0.4 | n |  | TRUE
98 | bus_LV_2430-2_1_2_node_135 | 0.4 | n |  | TRUE
99 | bus_LV_2430-2_1_2_node_118 | 0.4 | n |  | TRUE
100 | bus_LV_2430-2_1_2_node_137 | 0.4 | n |  | TRUE
101 | bus_LV_2430-2_1_2_node_120 | 0.4 | n |  | TRUE
102 | bus_LV_2430-2_1_2_node_127 | 0.4 | n |  | TRUE
103 | bus_LV_2430-2_1_2_node_128 | 0.4 | n |  | TRUE
104 | bus_LV_2430-2_1_2_node_125 | 0.4 | n |  | TRUE
105 | bus_LV_2430-2_1_2_node_153 | 0.4 | n |  | TRUE
106 | bus_LV_2430-2_1_2_node_141 | 0.4 | n |  | TRUE
107 | bus_LV_2430-2_1_2_node_136 | 0.4 | n |  | TRUE
108 | bus_MV_292_0_node_8 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2430-2_1_2_load_132 | 1 | 0.0010739 | 0.00026914 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2430-2_1_2_load_138 | 4 | 0.00060878 | 0.00015257 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2430-2_1_2_load_9 | 5 | 0.0009157 | 0.00022949 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2430-2_1_2_load_10 | 6 | 0.0010537 | 0.00026407 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2430-2_1_2_load_12 | 7 | 0.00047385 | 0.00011876 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2430-2_1_2_load_131 | 12 | 0.0026726 | 0.00066983 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2430-2_1_2_load_152 | 13 | 0.0029722 | 0.00074492 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2430-2_1_2_load_91 | 16 | 0.00014702 | 3.6846e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2430-2_1_2_load_25 | 17 | 8.6128e-05 | 2.1586e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2430-2_1_2_load_110 | 19 | 0.0010576 | 0.00026507 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2430-2_1_2_load_64 | 20 | 0.00046028 | 0.00011536 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2430-2_1_2_load_59 | 21 | 0.0060114 | 0.0015066 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2430-2_1_2_load_90 | 24 | 0.00017484 | 4.3819e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2430-2_1_2_load_98 | 25 | 0.0014491 | 0.00036317 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2430-2_1_2_load_32 | 26 | 0.00030836 | 7.7281e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2430-2_1_2_load_33 | 27 | 0.00099922 | 0.00025043 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2430-2_1_2_load_133 | 28 | 0.00027049 | 6.7791e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2430-2_1_2_load_20 | 29 | 0.0007254 | 0.0001818 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2430-2_1_2_load_21 | 30 | 0.00068914 | 0.00017272 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2430-2_1_2_load_23 | 32 | 0.0010297 | 0.00025806 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2430-2_1_2_load_87 | 33 | 0.00038818 | 9.7288e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2430-2_1_2_load_94 | 36 | 0.00031971 | 8.0126e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2430-2_1_2_load_47 | 37 | 0.0014597 | 0.00036583 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2430-2_1_2_load_53 | 38 | 0.0038195 | 0.00095727 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2430-2_1_2_load_95 | 39 | 0.0014866 | 0.00037257 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2430-2_1_2_load_35 | 40 | 0.00091413 | 0.0002291 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2430-2_1_2_load_36 | 41 | 0.0002924 | 7.3283e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2430-2_1_2_load_37 | 42 | 0.0011001 | 0.0002757 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2430-2_1_2_load_38 | 43 | 0.0053112 | 0.0013311 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2430-2_1_2_load_39 | 44 | 0.00016364 | 4.1013e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2430-2_1_2_load_51 | 45 | 0.0029768 | 0.00074606 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2430-2_1_2_load_92 | 46 | 0.00098736 | 0.00024745 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2430-2_1_2_load_49 | 47 | 0.0051993 | 0.0013031 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2430-2_1_2_load_40 | 48 | 0.0019979 | 0.00050073 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2430-2_1_2_load_43 | 51 | 0.0018602 | 0.00046622 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2430-2_1_2_load_121 | 52 | 0.0012585 | 0.00031542 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2430-2_1_2_load_139 | 53 | 0.002027 | 0.000508 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2430-2_1_2_load_96 | 54 | 0.0014247 | 0.00035706 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2430-2_1_2_load_123 | 55 | 0.002058 | 0.00051578 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2430-2_1_2_load_119 | 56 | 0.0015028 | 0.00037665 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2430-2_1_2_load_97 | 58 | 0.0012783 | 0.00032036 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2430-2_1_2_load_44 | 59 | 0.00048969 | 0.00012273 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2430-2_1_2_load_45 | 60 | 0.00045277 | 0.00011347 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2430-2_1_2_load_46 | 61 | 0.0027443 | 0.00068778 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2430-2_1_2_load_48 | 62 | 0.00051303 | 0.00012858 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2430-2_1_2_load_107 | 63 | 0.00047557 | 0.00011919 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2430-2_1_2_load_106 | 64 | 0.00046007 | 0.0001153 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2430-2_1_2_load_50 | 65 | 0.0035858 | 0.00089869 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2430-2_1_2_load_52 | 66 | 0.0011489 | 0.00028793 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2430-2_1_2_load_82 | 67 | 0.003184 | 0.00079799 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2430-2_1_2_load_56 | 68 | 0.0019792 | 0.00049603 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2430-2_1_2_load_54 | 69 | 0.0052159 | 0.0013072 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2430-2_1_2_load_111 | 70 | 0.001776 | 0.00044511 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2430-2_1_2_load_109 | 71 | 0.00087564 | 0.00021946 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2430-2_1_2_load_67 | 72 | 0.00087845 | 0.00022016 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2430-2_1_2_load_68 | 73 | 0.00083654 | 0.00020966 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2430-2_1_2_load_69 | 74 | 0.00062189 | 0.00015586 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2430-2_1_2_load_70 | 75 | 0.0011329 | 0.00028393 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2430-2_1_2_load_71 | 76 | 0.00097902 | 0.00024537 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2430-2_1_2_load_80 | 77 | 0.0011591 | 0.0002905 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2430-2_1_2_load_88 | 78 | 0.0016416 | 0.00041142 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2430-2_1_2_load_78 | 79 | 0.0016416 | 0.00041143 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2430-2_1_2_load_89 | 80 | 0.00080884 | 0.00020272 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2430-2_1_2_load_72 | 81 | 0.00051301 | 0.00012857 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2430-2_1_2_load_73 | 82 | 0.00121 | 0.00030324 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2430-2_1_2_load_74 | 83 | 0.0026883 | 0.00067374 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2430-2_1_2_load_75 | 84 | 0.00040741 | 0.00010211 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2430-2_1_2_load_116 | 87 | 0.00038924 | 9.7554e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2430-2_1_2_load_134 | 88 | 0.00068725 | 0.00017224 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2430-2_1_2_load_77 | 91 | 0.0015876 | 0.0003979 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2430-2_1_2_load_79 | 92 | 0.00056709 | 0.00014213 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2430-2_1_2_load_129 | 93 | 0.0010391 | 0.00026041 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2430-2_1_2_load_130 | 94 | 0.001459 | 0.00036565 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2430-2_1_2_load_93 | 95 | 0.0010274 | 0.00025749 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2430-2_1_2_load_150 | 96 | 0.0018018 | 0.00045158 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2430-2_1_2_load_151 | 97 | 0.0010936 | 0.00027409 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2430-2_1_2_load_135 | 98 | 0.002215 | 0.00055512 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2430-2_1_2_load_118 | 99 | 0.0018126 | 0.00045429 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2430-2_1_2_load_137 | 100 | 0.00063448 | 0.00015901 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2430-2_1_2_load_120 | 101 | 0.0016752 | 0.00041984 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2430-2_1_2_load_125 | 104 | 0.0008776 | 0.00021995 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2430-2_1_2_load_153 | 105 | 0.001713 | 0.00042932 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2430-2_1_2_load_141 | 106 | 0.0021553 | 0.00054017 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2430-2_1_2_load_136 | 107 | 0.0031856 | 0.00079839 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 95 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2430-2_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.024979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2430-2_1_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2430-2_1_2_line_2 | NAYY 4x150 SE | 0 | 3 | 0.1484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2430-2_1_2_line_3 | NAYY 4x150 SE | 1 | 28 | 0.0082471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2430-2_1_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.036778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2430-2_1_2_line_5 | NAYY 4x150 SE | 3 | 4 | 0.017356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2430-2_1_2_line_6 | NAYY 4x150 SE | 5 | 6 | 0.028148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2430-2_1_2_line_7 | NAYY 4x150 SE | 6 | 7 | 0.033362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2430-2_1_2_line_8 | NAYY 4x150 SE | 7 | 8 | 0.016966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2430-2_1_2_line_9 | NAYY 4x150 SE | 8 | 15 | 0.43348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2430-2_1_2_line_10 | NAYY 4x150 SE | 9 | 10 | 0.032854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2430-2_1_2_line_11 | NAYY 4x150 SE | 9 | 11 | 0.37892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2430-2_1_2_line_12 | NAYY 4x150 SE | 9 | 12 | 0.0043656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2430-2_1_2_line_13 | NAYY 4x150 SE | 10 | 18 | 0.02571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2430-2_1_2_line_14 | NAYY 4x150 SE | 10 | 19 | 0.0030368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2430-2_1_2_line_15 | NAYY 4x150 SE | 11 | 13 | 0.17343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2430-2_1_2_line_16 | NAYY 4x150 SE | 11 | 14 | 0.30086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_2430-2_1_2_line_17 | NAYY 4x150 SE | 14 | 20 | 0.16128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_2430-2_1_2_line_18 | NAYY 4x150 SE | 14 | 21 | 0.021459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2430-2_1_2_line_19 | NAYY 4x150 SE | 15 | 39 | 0.03251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2430-2_1_2_line_20 | NAYY 4x150 SE | 15 | 36 | 0.0078591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2430-2_1_2_line_21 | NAYY 4x150 SE | 16 | 17 | 0.0082959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2430-2_1_2_line_22 | NAYY 4x150 SE | 17 | 31 | 0.0039749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2430-2_1_2_line_23 | NAYY 4x150 SE | 18 | 31 | 0.067398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2430-2_1_2_line_24 | NAYY 4x150 SE | 19 | 71 | 0.0091202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2430-2_1_2_line_25 | NAYY 4x150 SE | 20 | 24 | 0.00050378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_2430-2_1_2_line_26 | NAYY 4x150 SE | 22 | 23 | 0.44464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_2430-2_1_2_line_27 | NAYY 4x150 SE | 22 | 24 | 0.10998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_2430-2_1_2_line_28 | NAYY 4x150 SE | 23 | 25 | 0.08918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_2430-2_1_2_line_29 | NAYY 4x150 SE | 25 | 58 | 0.012243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_2430-2_1_2_line_30 | NAYY 4x150 SE | 26 | 27 | 0.008005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2430-2_1_2_line_31 | NAYY 4x150 SE | 27 | 34 | 0.020104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2430-2_1_2_line_32 | NAYY 4x150 SE | 29 | 30 | 0.005232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2430-2_1_2_line_33 | NAYY 4x150 SE | 29 | 31 | 0.026284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2430-2_1_2_line_34 | NAYY 4x150 SE | 30 | 32 | 0.017542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2430-2_1_2_line_35 | NAYY 4x150 SE | 32 | 33 | 0.045336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2430-2_1_2_line_36 | NAYY 4x150 SE | 34 | 35 | 0.25419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2430-2_1_2_line_37 | NAYY 4x150 SE | 34 | 36 | 0.035885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2430-2_1_2_line_38 | NAYY 4x150 SE | 35 | 37 | 0.017236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2430-2_1_2_line_39 | NAYY 4x150 SE | 35 | 38 | 0.019961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2430-2_1_2_line_40 | NAYY 4x150 SE | 37 | 60 | 0.019844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2430-2_1_2_line_41 | NAYY 4x150 SE | 38 | 69 | 0.0072937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2430-2_1_2_line_42 | NAYY 4x150 SE | 40 | 41 | 0.021512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2430-2_1_2_line_43 | NAYY 4x150 SE | 40 | 42 | 0.0019051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2430-2_1_2_line_44 | NAYY 4x150 SE | 41 | 43 | 0.010525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2430-2_1_2_line_45 | NAYY 4x150 SE | 42 | 44 | 0.00032191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2430-2_1_2_line_46 | NAYY 4x150 SE | 43 | 45 | 0.015873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2430-2_1_2_line_47 | NAYY 4x150 SE | 44 | 46 | 0.018053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2430-2_1_2_line_48 | NAYY 4x150 SE | 45 | 47 | 0.01871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2430-2_1_2_line_49 | NAYY 4x150 SE | 47 | 65 | 0.00020895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2430-2_1_2_line_50 | NAYY 4x150 SE | 48 | 49 | 0.010416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2430-2_1_2_line_51 | NAYY 4x150 SE | 49 | 50 | 0.011572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
52 | LV_2430-2_1_2_line_52 | NAYY 4x150 SE | 49 | 51 | 0.022243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_2430-2_1_2_line_53 | NAYY 4x150 SE | 50 | 52 | 0.029458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2430-2_1_2_line_54 | NAYY 4x150 SE | 50 | 53 | 0.012184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_2430-2_1_2_line_55 | NAYY 4x150 SE | 51 | 54 | 0.020308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_2430-2_1_2_line_56 | NAYY 4x150 SE | 52 | 55 | 0.039492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2430-2_1_2_line_57 | NAYY 4x150 SE | 52 | 56 | 0.014589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2430-2_1_2_line_58 | NAYY 4x150 SE | 53 | 57 | 0.016779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
59 | LV_2430-2_1_2_line_59 | NAYY 4x150 SE | 54 | 58 | 0.014699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
60 | LV_2430-2_1_2_line_60 | NAYY 4x150 SE | 55 | 102 | 0.0037608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2430-2_1_2_line_61 | NAYY 4x150 SE | 56 | 101 | 0.026726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2430-2_1_2_line_62 | NAYY 4x150 SE | 57 | 106 | 0.015509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
63 | LV_2430-2_1_2_line_63 | NAYY 4x150 SE | 57 | 94 | 0.017337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
64 | LV_2430-2_1_2_line_64 | NAYY 4x150 SE | 59 | 60 | 0.019262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2430-2_1_2_line_65 | NAYY 4x150 SE | 59 | 61 | 0.00098793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2430-2_1_2_line_66 | NAYY 4x150 SE | 61 | 62 | 0.016494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
67 | LV_2430-2_1_2_line_67 | NAYY 4x150 SE | 62 | 63 | 0.0025383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
68 | LV_2430-2_1_2_line_68 | NAYY 4x150 SE | 63 | 64 | 0.01848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
69 | LV_2430-2_1_2_line_69 | NAYY 4x150 SE | 64 | 89 | 0.012074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
70 | LV_2430-2_1_2_line_70 | NAYY 4x150 SE | 65 | 66 | 0.0041136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2430-2_1_2_line_71 | NAYY 4x150 SE | 66 | 67 | 0.00065922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2430-2_1_2_line_72 | NAYY 4x150 SE | 67 | 68 | 0.021753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2430-2_1_2_line_73 | NAYY 4x150 SE | 68 | 69 | 0.018013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2430-2_1_2_line_74 | NAYY 4x150 SE | 70 | 71 | 0.046337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2430-2_1_2_line_75 | NAYY 4x150 SE | 72 | 73 | 0.0004013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
76 | LV_2430-2_1_2_line_76 | NAYY 4x150 SE | 72 | 74 | 0.018466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
77 | LV_2430-2_1_2_line_77 | NAYY 4x150 SE | 73 | 75 | 0.00076887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
78 | LV_2430-2_1_2_line_78 | NAYY 4x150 SE | 74 | 76 | 0.016019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
79 | LV_2430-2_1_2_line_79 | NAYY 4x150 SE | 75 | 77 | 0.011597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
80 | LV_2430-2_1_2_line_80 | NAYY 4x150 SE | 76 | 78 | 0.012705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
81 | LV_2430-2_1_2_line_81 | NAYY 4x150 SE | 77 | 79 | 0.019525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
82 | LV_2430-2_1_2_line_82 | NAYY 4x150 SE | 78 | 80 | 0.010685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
83 | LV_2430-2_1_2_line_83 | NAYY 4x150 SE | 79 | 91 | 0.00052537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
84 | LV_2430-2_1_2_line_84 | NAYY 4x150 SE | 80 | 93 | 0.011292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
85 | LV_2430-2_1_2_line_85 | NAYY 4x150 SE | 81 | 82 | 0.0082396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2430-2_1_2_line_86 | NAYY 4x150 SE | 81 | 83 | 0.012565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2430-2_1_2_line_87 | NAYY 4x150 SE | 82 | 84 | 0.00036632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2430-2_1_2_line_88 | NAYY 4x150 SE | 83 | 85 | 0.034708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2430-2_1_2_line_89 | NAYY 4x150 SE | 85 | 86 | 0.022138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2430-2_1_2_line_90 | NAYY 4x150 SE | 85 | 87 | 0.0057668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2430-2_1_2_line_91 | NAYY 4x150 SE | 86 | 88 | 0.015558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2430-2_1_2_line_92 | NAYY 4x150 SE | 86 | 89 | 0.018814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2430-2_1_2_line_93 | NAYY 4x150 SE | 87 | 90 | 0.029925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2430-2_1_2_line_94 | NAYY 4x150 SE | 88 | 98 | 0.015825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2430-2_1_2_line_95 | NAYY 4x150 SE | 89 | 92 | 0.042935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
96 | LV_2430-2_1_2_line_96 | NAYY 4x150 SE | 90 | 99 | 0.014441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2430-2_1_2_line_97 | NAYY 4x150 SE | 91 | 92 | 0.016004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
98 | LV_2430-2_1_2_line_98 | NAYY 4x150 SE | 93 | 94 | 0.020259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
99 | LV_2430-2_1_2_line_99 | NAYY 4x150 SE | 95 | 96 | 0.012259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
100 | LV_2430-2_1_2_line_100 | NAYY 4x150 SE | 96 | 97 | 0.014801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
101 | LV_2430-2_1_2_line_101 | NAYY 4x150 SE | 97 | 106 | 0.027295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
102 | LV_2430-2_1_2_line_102 | NAYY 4x150 SE | 98 | 107 | 0.042382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2430-2_1_2_line_103 | NAYY 4x150 SE | 99 | 100 | 0.02994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2430-2_1_2_line_104 | NAYY 4x150 SE | 102 | 103 | 0.035299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2430-2_1_2_line_105 | NAYY 4x150 SE | 102 | 104 | 0.019456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2430-2_1_2_line_106 | NAYY 4x150 SE | 103 | 105 | 0.00536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2430-2_1_2_trafo_93 | 0.25 MVA 20/0.4 kV | 108 | 95 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33
0 | 2605495.6207 | 1235923.7921 | 2605475.3312 | 1235909.2218
1 | 2605495.6207 | 1235923.7921 | 2605483.0658 | 1235950.3635 | 2605481.4439 | 1235953.2527 | 2605476.1007 | 1235962.7758 | 2605468.5462 | 1235974.3204 | 2605453.8846 | 1235987.971 | 2605451.0724 | 1235993.394 | 2605445.7 | 1236001.8721 | 2605439.8388 | 1236006.9032 | 2605430.9905 | 1236010.1193 | 2605415.2193 | 1236021.034 | 2605403.5228 | 1236036.0437 | 2605391.4038 | 1236058.3798 | 2605389.1313 | 1236061.1239 | 2605386.9126 | 1236063.0564 | 2605384.8305 | 1236064.4443 | 2605391.0217 | 1236079.4034 | 2605394.3893 | 1236087.3224 | 2605399.4354 | 1236096.6659 | 2605416.7574 | 1236127.8449 | 2605420.8201 | 1236136.843 | 2605423.9301 | 1236145.0397 | 2605441.0972 | 1236205.0028 | 2605452.6235 | 1236243.8703 | 2605457.8728 | 1236254.0591 | 2605468.4924 | 1236266.3318 | 2605482.9782 | 1236278.797 | 2605499.8124 | 1236288.0291 | 2605517.1705 | 1236295.2049 | 2605533.4949 | 1236299.2557 | 2605556.6093 | 1236308.1714 | 2605585.0058 | 1236316.1025 | 2605589.091 | 1236316.6622 | 2605595.0525 | 1236317.4905
2 | 2605540.4014 | 1235791.8973 | 2605528.8109 | 1235814.278 | 2605491.5946 | 1235882.9969 | 2605490.1072 | 1235887.7206 | 2605491.3735 | 1235893.114 | 2605500.8699 | 1235909.566 | 2605500.6526 | 1235915.4694 | 2605495.6207 | 1235923.7921
3 | 2605468.6324 | 1235904.4112 | 2605475.3312 | 1235909.2218
4 | 2605595.0525 | 1236317.4905 | 2605605.2203 | 1236318.8897 | 2605619.5534 | 1236324.1952 | 2605622.0392 | 1236327.922 | 2605623.6468 | 1236334.4788
5 | 2605540.4014 | 1235791.8973 | 2605525.8974 | 1235782.3644
6 | 2605623.6468 | 1236334.4788 | 2605624.504 | 1236337.9749 | 2605631.8592 | 1236345.1862 | 2605645.6691 | 1236348.689
7 | 2605678.1662 | 1236356.0591 | 2605670.2649 | 1236353.7831 | 2605656.9807 | 1236351.5581 | 2605645.6691 | 1236348.689
8 | 2605694.6909 | 1236359.4541 | 2605688.7745 | 1236359.1149 | 2605678.1662 | 1236356.0591
9 | 2605694.6909 | 1236359.4541 | 2605701.2227 | 1236357.1922 | 2605710.2943 | 1236349.5628 | 2605722.6384 | 1236337.9564 | 2605731.5727 | 1236331.4943 | 2605742.9417 | 1236326.8467 | 2605783.8542 | 1236317.2134 | 2605826.7687 | 1236303.124 | 2605860.8261 | 1236286.1357 | 2605869.2838 | 1236279.8179 | 2605879.0758 | 1236270.8775 | 2605890.9695 | 1236263.7737 | 2605920.8458 | 1236244.0466 | 2605939.8363 | 1236229.8345 | 2605949.3072 | 1236224.485 | 2605962.4925 | 1236219.8508 | 2605968.1839 | 1236218.3444 | 2605974.5022 | 1236217.9727 | 2605980.8415 | 1236219.3354 | 2605991.2636 | 1236223.7818 | 2606008.3239 | 1236233.2713 | 2606041.7914 | 1236186.821 | 2606043.8594 | 1236176.9059 | 2606036.8453 | 1236169.461
10 | 2605379.6757 | 1236785.4687 | 2605366.0354 | 1236793.2724 | 2605353.9346 | 1236805.4914
11 | 2605379.6757 | 1236785.4687 | 2605398.3926 | 1236777.7141 | 2605411.9421 | 1236770.0772 | 2605428.7913 | 1236752.9152 | 2605440.0011 | 1236739.0168 | 2605447.1563 | 1236732.8751 | 2605470.1807 | 1236722.6342 | 2605518.5978 | 1236710.2486 | 2605537.8358 | 1236703.9402 | 2605554.55 | 1236694.2719 | 2605557.8118 | 1236693.3077 | 2605561.9439 | 1236692.0774 | 2605567.4431 | 1236693.2277 | 2605593.2127 | 1236709.0501 | 2605655.1122 | 1236745.1634 | 2605671.9167 | 1236752.1169 | 2605683.8151 | 1236754.763 | 2605697.7658 | 1236755.2543 | 2605715.1759 | 1236753.7811
12 | 2605379.6757 | 1236785.4687 | 2605375.3118 | 1236785.5863
13 | 2605341.229 | 1236783.1219 | 2605353.9346 | 1236805.4914
14 | 2605353.9346 | 1236805.4914 | 2605352.3 | 1236808.0508
15 | 2605715.1759 | 1236753.7811 | 2605715.8312 | 1236764.7773 | 2605715.4024 | 1236770.2469 | 2605713.8989 | 1236775.9823 | 2605711.8663 | 1236781.1836 | 2605709.3885 | 1236785.2615 | 2605708.2215 | 1236787.1949 | 2605697.6299 | 1236802.8611 | 2605694.0343 | 1236812.8638 | 2605692.8516 | 1236823.3802 | 2605691.5225 | 1236836.7649 | 2605689.4515 | 1236842.711 | 2605685.0055 | 1236847.9878 | 2605675.2321 | 1236854.5604 | 2605663.8364 | 1236864.6002 | 2605656.7326 | 1236872.2649 | 2605651.1115 | 1236880.2534 | 2605647.5105 | 1236888.0881 | 2605646.2386 | 1236897.0146 | 2605649.4028 | 1236903.1436
16 | 2605715.1759 | 1236753.7811 | 2605729.2656 | 1236751.3263 | 2605742.1155 | 1236747.9476 | 2605752.8101 | 1236743.5107 | 2605769.1936 | 1236739.7352 | 2605782.0793 | 1236738.3912 | 2605794.2836 | 1236737.6025 | 2605815.6317 | 1236740.1135 | 2605824.86 | 1236742.1348 | 2605832.2186 | 1236745.077 | 2605832.158 | 1236752.8929 | 2605828.7984 | 1236761.1725 | 2605816.2333 | 1236775.2133 | 2605814.043 | 1236779.1469 | 2605812.2533 | 1236783.459 | 2605810.8326 | 1236789.5613 | 2605810.1931 | 1236809.3061 | 2605809.2178 | 1236816.4651 | 2605806.0825 | 1236827.5466 | 2605796.7449 | 1236868.407 | 2605792.9344 | 1236881.478 | 2605786.4792 | 1236898.9714 | 2605785.1572 | 1236904.807 | 2605784.6972 | 1236911.0548 | 2605785.033 | 1236915.9248
17 | 2605785.033 | 1236915.9248 | 2605797.551 | 1236911.1451 | 2605810.3195 | 1236905.465 | 2605827.9287 | 1236901.1683 | 2605841.7691 | 1236898.0021 | 2605856.4073 | 1236891.4679 | 2605876.6031 | 1236880.2585 | 2605885.9734 | 1236876.0873 | 2605900.617 | 1236871.7768 | 2605907.9429 | 1236869.3492 | 2605920.2345 | 1236864.1359 | 2605931.2666 | 1236862.6236 | 2605935.9745 | 1236862.1963
18 | 2605785.033 | 1236915.9248 | 2605777.9185 | 1236934.685 | 2605777.357 | 1236935.9626
19 | 2606036.8453 | 1236169.461 | 2606029.7577 | 1236167.208 | 2606013.3154 | 1236152.4715 | 2606011.9506 | 1236149.8079
20 | 2606036.8453 | 1236169.461 | 2606043.2473 | 1236164.9025
21 | 2605303.0506 | 1236733.8025 | 2605301.8377 | 1236725.5957
22 | 2605303.9097 | 1236737.6834 | 2605303.0506 | 1236733.8025
23 | 2605303.9097 | 1236737.6834 | 2605336.9636 | 1236755.7014 | 2605341.249 | 1236760.586 | 2605342.4917 | 1236766.9687 | 2605339.4858 | 1236778.0506 | 2605341.229 | 1236783.1219
24 | 2605347.3912 | 1236815.7372 | 2605352.3 | 1236808.0508
25 | 2605935.9745 | 1236862.1963 | 2605936.4762 | 1236862.1507
26 | 2606043.489 | 1236838.0983 | 2606101.4911 | 1236819.1787 | 2606309.6008 | 1236738.6 | 2606310.954 | 1236732.431 | 2606321.4312 | 1236719.3228 | 2606335.5194 | 1236704.3285 | 2606349.3975 | 1236687.7442 | 2606383.0125 | 1236644.9314 | 2606343.5369 | 1236634.8612
27 | 2606043.489 | 1236838.0983 | 2606001.7978 | 1236850.2528 | 2605960.828 | 1236859.9401 | 2605936.4762 | 1236862.1507
28 | 2606343.5369 | 1236634.8612 | 2606342.1486 | 1236631.302 | 2606324.8768 | 1236615.8855 | 2606279.8669 | 1236572.9439
29 | 2606279.8669 | 1236572.9439 | 2606279.5417 | 1236572.6337 | 2606270.8206 | 1236564.6939
30 | 2606045.6695 | 1236124.7659 | 2606038.8083 | 1236120.6424
31 | 2606062.901 | 1236135.1218 | 2606045.6695 | 1236124.7659
32 | 2605293.2385 | 1236761.5643 | 2605290.5457 | 1236766.0502
33 | 2605303.9097 | 1236737.6834 | 2605298.6536 | 1236752.5434 | 2605293.2385 | 1236761.5643
34 | 2605275.662 | 1236774.2574 | 2605288.8416 | 1236768.8892 | 2605290.5457 | 1236766.0502
35 | 2605241.5001 | 1236798.2435 | 2605241.3201 | 1236796.4089 | 2605241.3219 | 1236794.2965 | 2605241.7928 | 1236792.229 | 2605242.8311 | 1236790.1175 | 2605243.9673 | 1236788.562 | 2605245.0957 | 1236787.2955 | 2605247.223 | 1236785.8409 | 2605275.662 | 1236774.2574
36 | 2606062.901 | 1236135.1218 | 2606168.886 | 1236200.5919 | 2606239.8941 | 1236247.0714 | 2606258.9823 | 1236263.2122 | 2606272.299 | 1236277.8016
37 | 2606062.901 | 1236135.1218 | 2606045.5302 | 1236163.277 | 2606043.2473 | 1236164.9025
38 | 2606272.299 | 1236277.8016 | 2606278.5412 | 1236285.057 | 2606283.5108 | 1236290.8922
39 | 2606272.299 | 1236277.8016 | 2606260.0292 | 1236293.5465
40 | 2606283.5108 | 1236290.8922 | 2606296.3774 | 1236305.9996
41 | 2606260.0292 | 1236293.5465 | 2606255.5458 | 1236299.2996
42 | 2606200.3126 | 1236370.1754 | 2606187.0898 | 1236387.1431
43 | 2606185.9188 | 1236388.6458 | 2606187.0898 | 1236387.1431
44 | 2606206.7825 | 1236361.8732 | 2606200.3126 | 1236370.1754
45 | 2606185.7209 | 1236388.8997 | 2606185.9188 | 1236388.6458
46 | 2606206.7825 | 1236361.8732 | 2606216.5394 | 1236349.3531
47 | 2606175.0845 | 1236403.4828 | 2606182.6026 | 1236392.9011 | 2606185.7209 | 1236388.8997
48 | 2606228.0402 | 1236334.595 | 2606216.5394 | 1236349.3531
49 | 2606228.0402 | 1236334.595 | 2606228.1687 | 1236334.4302
50 | 2606230.6021 | 1236524.4978 | 2606221.7216 | 1236529.9404
51 | 2606230.6021 | 1236524.4978 | 2606241.3353 | 1236520.0951
52 | 2606230.6021 | 1236524.4978 | 2606234.4156 | 1236531.5505 | 2606244.9345 | 1236541.1269
53 | 2606268.6604 | 1236508.8945 | 2606241.3353 | 1236520.0951
54 | 2606241.3353 | 1236520.0951 | 2606233.3084 | 1236510.9294
55 | 2606259.9515 | 1236554.7986 | 2606244.9345 | 1236541.1269
56 | 2606268.6604 | 1236508.8945 | 2606304.2003 | 1236491.6747
57 | 2606268.6604 | 1236508.8945 | 2606277.8624 | 1236520.2156
58 | 2606222.2537 | 1236498.3064 | 2606233.3084 | 1236510.9294
59 | 2606259.9515 | 1236554.7986 | 2606270.8206 | 1236564.6939
60 | 2606307.5848 | 1236490.0348 | 2606304.2003 | 1236491.6747
61 | 2606277.8624 | 1236520.2156 | 2606285.2389 | 1236529.2909 | 2606296.5317 | 1236539.2113
62 | 2606222.2537 | 1236498.3064 | 2606211.2324 | 1236487.3956
63 | 2606222.2537 | 1236498.3064 | 2606232.8626 | 1236484.5937
64 | 2606308.8667 | 1236320.6641 | 2606296.3774 | 1236305.9996
65 | 2606308.8667 | 1236320.6641 | 2606309.5073 | 1236321.4162
66 | 2606309.5073 | 1236321.4162 | 2606320.2018 | 1236333.9733
67 | 2606321.8475 | 1236335.9057 | 2606320.2018 | 1236333.9733
68 | 2606333.8299 | 1236349.9749 | 2606321.8475 | 1236335.9057
69 | 2606341.6568 | 1236359.1686 | 2606339.5938 | 1236356.7427 | 2606333.8299 | 1236349.9749
70 | 2606228.1687 | 1236334.4302 | 2606230.6973 | 1236331.1855
71 | 2606230.6973 | 1236331.1855 | 2606231.1025 | 1236330.6655
72 | 2606244.4737 | 1236313.5075 | 2606231.1025 | 1236330.6655
73 | 2606244.4737 | 1236313.5075 | 2606255.5458 | 1236299.2996
74 | 2605347.3912 | 1236815.7372 | 2605344.9719 | 1236819.5253 | 2605344.3043 | 1236821.6594 | 2605344.1206 | 1236823.9717 | 2605344.8751 | 1236826.2738 | 2605346.0308 | 1236828.365 | 2605357.6139 | 1236845.23 | 2605364.2545 | 1236855.2426
75 | 2606287.1227 | 1236413.5128 | 2606287.3596 | 1236413.1889
76 | 2606287.1227 | 1236413.5128 | 2606281.751 | 1236420.8544 | 2606276.064 | 1236428.3006
77 | 2606287.3596 | 1236413.1889 | 2606287.8136 | 1236412.5684
78 | 2606266.3408 | 1236441.0316 | 2606276.064 | 1236428.3006
79 | 2606287.8136 | 1236412.5684 | 2606294.6614 | 1236403.2093
80 | 2606266.3408 | 1236441.0316 | 2606258.6296 | 1236451.1283
81 | 2606294.6614 | 1236403.2093 | 2606306.1907 | 1236387.4521
82 | 2606252.1442 | 1236459.62 | 2606258.6296 | 1236451.1283
83 | 2606306.1907 | 1236387.4521 | 2606306.5009 | 1236387.0281
84 | 2606252.1442 | 1236459.62 | 2606249.1115 | 1236463.5909 | 2606245.2592 | 1236468.5702
85 | 2606333.5088 | 1236415.8168 | 2606327.4416 | 1236410.2418
86 | 2606333.5088 | 1236415.8168 | 2606333.5088 | 1236415.8168 | 2606336.9648 | 1236417.4326 | 2606341.3456 | 1236417.4372 | 2606345.4933 | 1236416.0629 | 2606345.4933 | 1236416.0629
87 | 2606327.1719 | 1236409.9939 | 2606327.4416 | 1236410.2418
88 | 2606368.5447 | 1236390.116 | 2606345.4933 | 1236416.0629
89 | 2606353.7854 | 1236373.5791 | 2606365.9525 | 1236387.2225 | 2606368.5447 | 1236390.116
90 | 2606368.5447 | 1236390.116 | 2606372.3902 | 1236394.4134
91 | 2606353.7854 | 1236373.5791 | 2606365.073 | 1236362.8723
92 | 2606341.6568 | 1236359.1686 | 2606347.1053 | 1236365.645 | 2606353.7854 | 1236373.5791
93 | 2606393.3041 | 1236415.8024 | 2606377.6964 | 1236400.343 | 2606372.3902 | 1236394.4134
94 | 2606375.9984 | 1236351.4892 | 2606373.4547 | 1236354.9219 | 2606365.073 | 1236362.8723
95 | 2606341.6568 | 1236359.1686 | 2606337.1042 | 1236364.2002 | 2606337.667 | 1236375.7856 | 2606335.6495 | 1236380.4419 | 2606330.964 | 1236382.3492 | 2606317.7823 | 1236376.5096 | 2606317.7823 | 1236376.5096
96 | 2606393.3041 | 1236415.8024 | 2606400.8186 | 1236403.471
97 | 2606306.5009 | 1236387.0281 | 2606312.8017 | 1236378.4166 | 2606317.7823 | 1236376.5096
98 | 2606245.2592 | 1236468.5702 | 2606232.8626 | 1236484.5937
99 | 2606173.0042 | 1236448.7809 | 2606173.0042 | 1236448.7809 | 2606177.735 | 1236454.2336 | 2606181.3165 | 1236457.7792
100 | 2606181.3165 | 1236457.7792 | 2606191.8348 | 1236468.1922
101 | 2606211.2324 | 1236487.3956 | 2606191.8348 | 1236468.1922
102 | 2606375.9984 | 1236351.4892 | 2606391.6398 | 1236330.3818 | 2606401.807 | 1236317.8849
103 | 2606416.3987 | 1236377.9039 | 2606400.8186 | 1236403.471
104 | 2606307.5848 | 1236490.0348 | 2606310.0069 | 1236496.3079 | 2606315.4901 | 1236512.7014 | 2606316.333 | 1236516.9716 | 2606314.5053 | 1236521.0722 | 2606313.2169 | 1236523.161
105 | 2606307.5848 | 1236490.0348 | 2606309.2199 | 1236489.2472 | 2606315.5172 | 1236487.0302 | 2606321.2384 | 1236485.7799 | 2606326.3263 | 1236485.3211
106 | 2606309.5363 | 1236519.2547 | 2606313.2169 | 1236523.161

## bus_geodata
| x | y | coords
0 | 2605495.6207 | 1235923.7921
1 | 2605475.3312 | 1235909.2218
2 | 2605595.0525 | 1236317.4905
3 | 2605540.4014 | 1235791.8973
4 | 2605525.8974 | 1235782.3644
5 | 2605623.6468 | 1236334.4788
6 | 2605645.6691 | 1236348.689
7 | 2605678.1662 | 1236356.0591
8 | 2605694.6909 | 1236359.4541
9 | 2605379.6757 | 1236785.4687
10 | 2605353.9346 | 1236805.4914
11 | 2605715.1759 | 1236753.7811
12 | 2605375.3118 | 1236785.5863
13 | 2605649.4028 | 1236903.1436
14 | 2605785.033 | 1236915.9248
15 | 2606036.8453 | 1236169.461
16 | 2605301.8377 | 1236725.5957
17 | 2605303.0506 | 1236733.8025
18 | 2605341.229 | 1236783.1219
19 | 2605352.3 | 1236808.0508
20 | 2605935.9745 | 1236862.1963
21 | 2605777.357 | 1236935.9626
22 | 2606043.489 | 1236838.0983
23 | 2606343.5369 | 1236634.8612
24 | 2605936.4762 | 1236862.1507
25 | 2606279.8669 | 1236572.9439
26 | 2606038.8083 | 1236120.6424
27 | 2606045.6695 | 1236124.7659
28 | 2605468.6325 | 1235904.4112
29 | 2605293.2385 | 1236761.5643
30 | 2605290.5457 | 1236766.0502
31 | 2605303.9097 | 1236737.6834
32 | 2605275.662 | 1236774.2574
33 | 2605241.5001 | 1236798.2435
34 | 2606062.901 | 1236135.1218
35 | 2606272.299 | 1236277.8016
36 | 2606043.2473 | 1236164.9025
37 | 2606283.5108 | 1236290.8922
38 | 2606260.0292 | 1236293.5465
39 | 2606011.9506 | 1236149.8079
40 | 2606187.0898 | 1236387.1431
41 | 2606200.3126 | 1236370.1754
42 | 2606185.9188 | 1236388.6458
43 | 2606206.7825 | 1236361.8732
44 | 2606185.7209 | 1236388.8997
45 | 2606216.5394 | 1236349.3531
46 | 2606175.0845 | 1236403.4828
47 | 2606228.0402 | 1236334.595
48 | 2606221.7216 | 1236529.9404
49 | 2606230.6021 | 1236524.4978
50 | 2606241.3353 | 1236520.0951
51 | 2606244.9345 | 1236541.1269
52 | 2606268.6604 | 1236508.8945
53 | 2606233.3084 | 1236510.9294
54 | 2606259.9515 | 1236554.7986
55 | 2606304.2003 | 1236491.6747
56 | 2606277.8624 | 1236520.2156
57 | 2606222.2537 | 1236498.3064
58 | 2606270.8206 | 1236564.6939
59 | 2606308.8667 | 1236320.6641
60 | 2606296.3774 | 1236305.9996
61 | 2606309.5073 | 1236321.4162
62 | 2606320.2018 | 1236333.9733
63 | 2606321.8475 | 1236335.9057
64 | 2606333.8299 | 1236349.9749
65 | 2606228.1687 | 1236334.4302
66 | 2606230.6973 | 1236331.1855
67 | 2606231.1025 | 1236330.6655
68 | 2606244.4737 | 1236313.5075
69 | 2606255.5458 | 1236299.2996
70 | 2605364.2545 | 1236855.2426
71 | 2605347.3912 | 1236815.7372
72 | 2606287.1227 | 1236413.5128
73 | 2606287.3596 | 1236413.1889
74 | 2606276.064 | 1236428.3006
75 | 2606287.8136 | 1236412.5684
76 | 2606266.3408 | 1236441.0316
77 | 2606294.6614 | 1236403.2093
78 | 2606258.6296 | 1236451.1283
79 | 2606306.1907 | 1236387.4521
80 | 2606252.1442 | 1236459.62
81 | 2606333.5088 | 1236415.8168
82 | 2606327.4416 | 1236410.2418
83 | 2606345.4933 | 1236416.0629
84 | 2606327.1719 | 1236409.9939
85 | 2606368.5447 | 1236390.1159
86 | 2606353.7854 | 1236373.5791
87 | 2606372.3902 | 1236394.4134
88 | 2606365.073 | 1236362.8723
89 | 2606341.6568 | 1236359.1686
90 | 2606393.3041 | 1236415.8024
91 | 2606306.5009 | 1236387.0281
92 | 2606317.7823 | 1236376.5096
93 | 2606245.2592 | 1236468.5702
94 | 2606232.8626 | 1236484.5937
95 | 2606173.0042 | 1236448.7809
96 | 2606181.3165 | 1236457.7792
97 | 2606191.8348 | 1236468.1922
98 | 2606375.9984 | 1236351.4892
99 | 2606400.8186 | 1236403.471
100 | 2606416.3987 | 1236377.9039
101 | 2606296.5317 | 1236539.2113
102 | 2606307.5848 | 1236490.0348
103 | 2606313.2169 | 1236523.161
104 | 2606326.3263 | 1236485.3211
105 | 2606309.5363 | 1236519.2547
106 | 2606211.2324 | 1236487.3956
107 | 2606401.807 | 1236317.8849
108 | 2606222.2537 | 1236498.3064

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97023 | -0.21167 | 0 | 0
1 | 0.97018 | -0.21203 | 0.0010739 | 0.00026914
2 | 0.97178 | -0.20022 | 0 | 0
3 | 0.9701 | -0.21265 | 0 | 0
4 | 0.97008 | -0.21276 | 0.00060878 | 0.00015257
5 | 0.97189 | -0.19943 | 0.0009157 | 0.00022949
6 | 0.97201 | -0.19856 | 0.0010537 | 0.00026407
7 | 0.9722 | -0.19715 | 0.00047385 | 0.00011876
8 | 0.97231 | -0.19635 | 0 | 0
9 | 0.97268 | -0.19367 | 0 | 0
10 | 0.97236 | -0.19603 | 0 | 0
11 | 0.97793 | -0.15593 | 0 | 0
12 | 0.97267 | -0.1938 | 0.0026726 | 0.00066983
13 | 0.97718 | -0.16133 | 0.0029722 | 0.00074492
14 | 0.98067 | -0.13632 | 0 | 0
15 | 0.9751 | -0.17584 | 0 | 0
16 | 0.97194 | -0.19908 | 0.00014702 | 3.6846e-05
17 | 0.97194 | -0.19907 | 8.6128e-05 | 2.1586e-05
18 | 0.97224 | -0.19687 | 0 | 0
19 | 0.97234 | -0.19615 | 0.0010576 | 0.00026507
20 | 0.98284 | -0.12081 | 0.00046028 | 0.00011536
21 | 0.98048 | -0.13766 | 0.0060114 | 0.0015066
22 | 0.98437 | -0.10984 | 0 | 0
23 | 0.99056 | -0.065929 | 0 | 0
24 | 0.98284 | -0.12076 | 0.00017484 | 4.3819e-05
25 | 0.9918 | -0.057165 | 0.0014491 | 0.00036317
26 | 0.97545 | -0.17326 | 0.00030836 | 7.7281e-05
27 | 0.97546 | -0.17323 | 0.00099922 | 0.00025043
28 | 0.97018 | -0.21205 | 0.00027049 | 6.7791e-05
29 | 0.97183 | -0.19985 | 0.0007254 | 0.0001818
30 | 0.97181 | -0.19996 | 0.00068914 | 0.00017272
31 | 0.97194 | -0.19906 | 0 | 0
32 | 0.97178 | -0.20023 | 0.0010297 | 0.00025806
33 | 0.97175 | -0.20042 | 0.00038818 | 9.7288e-05
34 | 0.9755 | -0.17296 | 0 | 0
35 | 0.97829 | -0.15262 | 0 | 0
36 | 0.97517 | -0.17534 | 0.00031971 | 8.0126e-05
37 | 0.97938 | -0.1448 | 0.0014597 | 0.00036583
38 | 0.97725 | -0.1601 | 0.0038195 | 0.00095727
39 | 0.97503 | -0.17634 | 0.0014866 | 0.00037257
40 | 0.97458 | -0.17922 | 0.00091413 | 0.0002291
41 | 0.97468 | -0.1785 | 0.0002924 | 7.3283e-05
42 | 0.97457 | -0.17927 | 0.0011001 | 0.0002757
43 | 0.97473 | -0.17812 | 0.0053112 | 0.0013311
44 | 0.97457 | -0.17927 | 0.00016364 | 4.1013e-05
45 | 0.97494 | -0.17666 | 0.0029768 | 0.00074606
46 | 0.97455 | -0.17946 | 0.00098736 | 0.00024745
47 | 0.97526 | -0.17435 | 0.0051993 | 0.0013031
48 | 0.99294 | -0.049159 | 0.0019979 | 0.00050073
49 | 0.99297 | -0.048948 | 0 | 0
50 | 0.9932 | -0.047345 | 0 | 0
51 | 0.99256 | -0.051807 | 0.0018602 | 0.00046622
52 | 0.99281 | -0.050058 | 0.0012585 | 0.00031542
53 | 0.99352 | -0.045097 | 0.002027 | 0.000508
54 | 0.99222 | -0.054226 | 0.0014247 | 0.00035706
55 | 0.99255 | -0.051921 | 0.002058 | 0.00051578
56 | 0.99275 | -0.050528 | 0.0015028 | 0.00037665
57 | 0.99398 | -0.041831 | 0 | 0
58 | 0.99199 | -0.055873 | 0.0012783 | 0.00032036
59 | 0.98196 | -0.12644 | 0.00048969 | 0.00012273
60 | 0.98068 | -0.13552 | 0.00045277 | 0.00011347
61 | 0.98203 | -0.12597 | 0.0027443 | 0.00068778
62 | 0.98261 | -0.12181 | 0.00051303 | 0.00012858
63 | 0.9827 | -0.12117 | 0.00047557 | 0.00011919
64 | 0.98337 | -0.11642 | 0.00046007 | 0.0001153
65 | 0.97526 | -0.17431 | 0.0035858 | 0.00089869
66 | 0.97539 | -0.17343 | 0.0011489 | 0.00028793
67 | 0.97541 | -0.17328 | 0.003184 | 0.00079799
68 | 0.9762 | -0.16761 | 0.0019792 | 0.00049603
69 | 0.9769 | -0.16254 | 0.0052159 | 0.0013072
70 | 0.97218 | -0.19728 | 0.001776 | 0.00044511
71 | 0.97231 | -0.19641 | 0.00087564 | 0.00021946
72 | 0.98818 | -0.082419 | 0.00087845 | 0.00022016
73 | 0.98816 | -0.082565 | 0.00083654 | 0.00020966
74 | 0.98914 | -0.075654 | 0.00062189 | 0.00015586
75 | 0.98812 | -0.08284 | 0.0011329 | 0.00028393
76 | 0.98999 | -0.069746 | 0.00097902 | 0.00024537
77 | 0.98754 | -0.086926 | 0.0011591 | 0.0002905
78 | 0.99066 | -0.065003 | 0.0016416 | 0.00041142
79 | 0.98658 | -0.0937 | 0.0016416 | 0.00041143
80 | 0.99124 | -0.060931 | 0.00080884 | 0.00020272
81 | 0.98291 | -0.11973 | 0.00051301 | 0.00012857
82 | 0.98289 | -0.11987 | 0.00121 | 0.00030324
83 | 0.98295 | -0.11945 | 0.0026883 | 0.00067374
84 | 0.98289 | -0.11987 | 0.00040741 | 0.00010211
85 | 0.98319 | -0.11772 | 0 | 0
86 | 0.98344 | -0.11597 | 0 | 0
87 | 0.98317 | -0.11789 | 0.00038924 | 9.7554e-05
88 | 0.9833 | -0.11695 | 0.00068725 | 0.00017224
89 | 0.98381 | -0.1133 | 0 | 0
90 | 0.98306 | -0.11865 | 0 | 0
91 | 0.98656 | -0.093878 | 0.0015876 | 0.0003979
92 | 0.98581 | -0.099176 | 0.00056709 | 0.00014213
93 | 0.99186 | -0.056585 | 0.0010391 | 0.00026041
94 | 0.99299 | -0.048696 | 0.001459 | 0.00036565
95 | 1 | 0 | -0.1243 | -0.031167
96 | 0.99892 | -0.0074652 | 0.0018018 | 0.00045158
97 | 0.99764 | -0.016366 | 0.0010936 | 0.00027409
98 | 0.98317 | -0.11783 | 0.002215 | 0.00055512
99 | 0.98301 | -0.11902 | 0.0018126 | 0.00045429
100 | 0.98298 | -0.11921 | 0.00063448 | 0.00015901
101 | 0.99268 | -0.050982 | 0.0016752 | 0.00041984
102 | 0.99253 | -0.05202 | 0 | 0
103 | 0.99245 | -0.052633 | 0 | 0
104 | 0.99251 | -0.052193 | 0.0008776 | 0.00021995
105 | 0.99243 | -0.052726 | 0.001713 | 0.00042932
106 | 0.99529 | -0.032691 | 0.0021553 | 0.00054017
107 | 0.98298 | -0.11923 | 0.0031856 | 0.00079839
108 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0013444 | 0.00033655 | -0.0013444 | -0.00033683 | 6.6264e-08 | -2.8298e-07 | 0.0020618 | 0.0020619 | 0.0020619 | 0.97023 | -0.21167 | 0.97018 | -0.21203 | 0.76367
1 | -0.0019533 | -0.00048711 | 0.0019563 | 0.00048157 | 3.031e-06 | -5.5385e-06 | 0.0029949 | 0.0029925 | 0.0029949 | 0.97023 | -0.21167 | 0.97178 | -0.20022 | 1.1092
2 | 0.00060887 | 0.00015056 | -0.00060879 | -0.00015236 | 8.0678e-08 | -1.8014e-06 | 0.00093307 | 0.00093373 | 0.00093373 | 0.97023 | -0.21167 | 0.9701 | -0.21265 | 0.34583
3 | 0.00027049 | 6.769e-05 | -0.00027049 | -6.7791e-05 | 8.8565e-10 | -1.015e-07 | 0.00041483 | 0.00041487 | 0.00041487 | 0.97018 | -0.21203 | 0.97018 | -0.21205 | 0.15365
4 | -0.0019563 | -0.00048157 | 0.0019566 | 0.0004812 | 2.055e-07 | -3.7667e-07 | 0.0029925 | 0.0029923 | 0.0029925 | 0.97178 | -0.20022 | 0.97189 | -0.19943 | 1.1083
5 | 0.00060879 | 0.00015236 | -0.00060878 | -0.00015257 | 9.4432e-09 | -2.1065e-07 | 0.00093373 | 0.00093381 | 0.00093381 | 0.9701 | -0.21265 | 0.97008 | -0.21276 | 0.34585
6 | -0.0028722 | -0.00071069 | 0.0028726 | 0.00071047 | 3.3915e-07 | -2.1841e-07 | 0.0043943 | 0.0043942 | 0.0043943 | 0.97189 | -0.19943 | 0.97201 | -0.19856 | 1.6275
7 | -0.0039263 | -0.00097455 | 0.003927 | 0.00097442 | 7.5121e-07 | -1.2468e-07 | 0.0060072 | 0.006007 | 0.0060072 | 0.97201 | -0.19856 | 0.9722 | -0.19715 | 2.2249
8 | -0.0044009 | -0.0010932 | 0.0044013 | 0.0010932 | 4.7982e-07 | -2.5853e-08 | 0.0067323 | 0.0067322 | 0.0067323 | 0.9722 | -0.19715 | 0.97231 | -0.19635 | 2.4934
9 | -0.0044013 | -0.0010932 | 0.0044136 | 0.0010925 | 1.2256e-05 | -6.7803e-07 | 0.0067322 | 0.0067303 | 0.0067322 | 0.97231 | -0.19635 | 0.9751 | -0.17584 | 2.4934
10 | 0.0067791 | 0.001696 | -0.0067769 | -0.0016955 | 2.2045e-06 | 4.4022e-07 | 0.01037 | 0.01037 | 0.01037 | 0.97268 | -0.19367 | 0.97236 | -0.19603 | 3.8407
11 | -0.0094518 | -0.0023658 | 0.0095012 | 0.00238 | 4.9421e-05 | 1.428e-05 | 0.014458 | 0.014457 | 0.014458 | 0.97268 | -0.19367 | 0.97793 | -0.15593 | 5.3549
12 | 0.0026727 | 0.00066979 | -0.0026726 | -0.00066983 | 4.554e-08 | -3.6671e-08 | 0.0040887 | 0.0040887 | 0.0040887 | 0.97268 | -0.19367 | 0.97267 | -0.1938 | 1.5143
13 | 0.0030672 | 0.00076647 | -0.0030669 | -0.00076665 | 3.5335e-07 | -1.8297e-07 | 0.004693 | 0.0046931 | 0.0046931 | 0.97236 | -0.19603 | 0.97224 | -0.19687 | 1.7382
14 | 0.0037097 | 0.00092906 | -0.0037096 | -0.00092907 | 6.1066e-08 | -1.4181e-08 | 0.0056767 | 0.0056768 | 0.0056768 | 0.97236 | -0.19603 | 0.97234 | -0.19615 | 2.1025
15 | 0.0029745 | 0.00074359 | -0.0029722 | -0.00074492 | 2.2165e-06 | -1.3218e-06 | 0.0045253 | 0.004526 | 0.004526 | 0.97793 | -0.15593 | 0.97718 | -0.16133 | 1.6763
16 | -0.012476 | -0.0031236 | 0.012509 | 0.0031291 | 3.3817e-05 | 5.4359e-06 | 0.018982 | 0.018979 | 0.018982 | 0.97793 | -0.15593 | 0.98067 | -0.13632 | 3.5152
17 | -0.018522 | -0.0046358 | 0.018562 | 0.004647 | 3.9737e-05 | 1.1205e-05 | 0.028102 | 0.028101 | 0.028102 | 0.98067 | -0.13632 | 0.98284 | -0.12081 | 5.2041
18 | 0.0060125 | 0.0015068 | -0.0060114 | -0.0015066 | 1.1145e-06 | 1.5796e-07 | 0.0091231 | 0.0091232 | 0.0091232 | 0.98067 | -0.13632 | 0.98048 | -0.13766 | 3.3789
19 | 0.0014867 | 0.00037221 | -0.0014866 | -0.00037257 | 1.0441e-07 | -3.6534e-07 | 0.0022686 | 0.0022687 | 0.0022687 | 0.9751 | -0.17584 | 0.97503 | -0.17634 | 0.84026
20 | -0.0059003 | -0.0014647 | 0.0059007 | 0.0014647 | 3.9713e-07 | 5.4698e-08 | 0.0089988 | 0.0089988 | 0.0089988 | 0.9751 | -0.17584 | 0.97517 | -0.17534 | 3.3329
21 | -0.00014702 | -3.6846e-05 | 0.00014702 | 3.6743e-05 | 2.6223e-10 | -1.0271e-07 | 0.00022508 | 0.00022504 | 0.00022508 | 0.97194 | -0.19908 | 0.97194 | -0.19907 | 0.083363
22 | -0.00023314 | -5.8329e-05 | 0.00023314 | 5.828e-05 | 3.1588e-10 | -4.914e-08 | 0.0003569 | 0.00035688 | 0.0003569 | 0.97194 | -0.19907 | 0.97194 | -0.19906 | 0.13219
23 | 0.0030669 | 0.00076665 | -0.0030659 | -0.00076713 | 9.2637e-07 | -4.7925e-07 | 0.0046931 | 0.0046934 | 0.0046934 | 0.97224 | -0.19687 | 0.97194 | -0.19906 | 1.7383
24 | 0.002652 | 0.000664 | -0.0026519 | -0.00066408 | 9.3726e-08 | -7.707e-08 | 0.0040582 | 0.0040582 | 0.0040582 | 0.97234 | -0.19615 | 0.97231 | -0.19641 | 1.5031
25 | -0.019022 | -0.0047624 | 0.019022 | 0.0047624 | 1.3035e-07 | 3.7366e-08 | 0.028798 | 0.028798 | 0.028798 | 0.98284 | -0.12081 | 0.98284 | -0.12076 | 5.3329
26 | -0.019226 | -0.0048146 | 0.019343 | 0.0048483 | 0.00011715 | 3.3681e-05 | 0.029061 | 0.029057 | 0.029061 | 0.98437 | -0.10984 | 0.99056 | -0.065929 | 5.3817
27 | 0.019226 | 0.0048146 | -0.019197 | -0.0048062 | 2.8981e-05 | 8.3545e-06 | 0.029061 | 0.029062 | 0.029062 | 0.98437 | -0.10984 | 0.98284 | -0.12076 | 5.3819
28 | -0.019343 | -0.0048483 | 0.019367 | 0.004855 | 2.3492e-05 | 6.7365e-06 | 0.029057 | 0.029056 | 0.029057 | 0.99056 | -0.065929 | 0.9918 | -0.057165 | 5.381
29 | -0.020816 | -0.0052182 | 0.020819 | 0.0052193 | 3.7258e-06 | 1.1169e-06 | 0.03123 | 0.03123 | 0.03123 | 0.9918 | -0.057165 | 0.99199 | -0.055873 | 5.7834
30 | -0.00030836 | -7.7281e-05 | 0.00030836 | 7.7182e-05 | 1.1051e-09 | -9.9503e-08 | 0.00047039 | 0.00047035 | 0.00047039 | 0.97545 | -0.17326 | 0.97546 | -0.17323 | 0.17422
31 | -0.0013076 | -0.00032761 | 0.0013076 | 0.00032738 | 4.9907e-08 | -2.3178e-07 | 0.0019946 | 0.0019945 | 0.0019946 | 0.97546 | -0.17323 | 0.9755 | -0.17296 | 0.73874
32 | 0.0021071 | 0.00052725 | -0.0021071 | -0.00052731 | 3.3976e-08 | -5.1758e-08 | 0.003226 | 0.003226 | 0.003226 | 0.97183 | -0.19985 | 0.97181 | -0.19996 | 1.1948
33 | -0.0028325 | -0.00070906 | 0.0028328 | 0.00070885 | 3.0844e-07 | -2.0707e-07 | 0.0043367 | 0.0043365 | 0.0043367 | 0.97183 | -0.19985 | 0.97194 | -0.19906 | 1.6062
34 | 0.0014179 | 0.00035459 | -0.0014179 | -0.00035479 | 5.1584e-08 | -1.975e-07 | 0.0021708 | 0.0021709 | 0.0021709 | 0.97181 | -0.19996 | 0.97178 | -0.20023 | 0.80402
35 | 0.00038819 | 9.673e-05 | -0.00038818 | -9.7288e-05 | 9.9923e-09 | -5.5782e-07 | 0.00059421 | 0.00059442 | 0.00059442 | 0.97178 | -0.20023 | 0.97175 | -0.20042 | 0.22015
36 | -0.00753 | -0.0018726 | 0.0075509 | 0.0018774 | 2.0906e-05 | 4.8582e-06 | 0.011481 | 0.01148 | 0.011481 | 0.9755 | -0.17296 | 0.97829 | -0.15262 | 4.2522
37 | 0.0062224 | 0.0015452 | -0.0062204 | -0.0015449 | 2.0152e-06 | 3.2723e-07 | 0.0094865 | 0.0094866 | 0.0094866 | 0.9755 | -0.17296 | 0.97517 | -0.17534 | 3.5136
38 | -0.043525 | -0.010904 | 0.043572 | 0.010922 | 4.7136e-05 | 1.7912e-05 | 0.066202 | 0.066201 | 0.066202 | 0.97829 | -0.15262 | 0.97938 | -0.1448 | 24.5191
39 | 0.035974 | 0.0090268 | -0.035937 | -0.0090127 | 3.7298e-05 | 1.4095e-05 | 0.054722 | 0.054722 | 0.054722 | 0.97829 | -0.15262 | 0.97725 | -0.1601 | 20.2673
40 | -0.045032 | -0.011288 | 0.04509 | 0.01131 | 5.7965e-05 | 2.2044e-05 | 0.068419 | 0.068419 | 0.068419 | 0.97938 | -0.1448 | 0.98068 | -0.13552 | 25.3404
41 | 0.032117 | 0.0080554 | -0.032106 | -0.0080513 | 1.0886e-05 | 4.0955e-06 | 0.048906 | 0.048906 | 0.048906 | 0.97725 | -0.1601 | 0.9769 | -0.16254 | 18.1133
42 | -0.0031652 | -0.00079304 | 0.0031655 | 0.00079289 | 3.1349e-07 | -1.475e-07 | 0.0048327 | 0.0048326 | 0.0048327 | 0.97458 | -0.17922 | 0.97468 | -0.1785 | 1.7899
43 | 0.0022511 | 0.00056393 | -0.0022511 | -0.00056395 | 1.4043e-08 | -1.8338e-08 | 0.003437 | 0.003437 | 0.003437 | 0.97458 | -0.17922 | 0.97457 | -0.17927 | 1.273
44 | -0.003458 | -0.00086617 | 0.0034581 | 0.00086611 | 1.8303e-07 | -6.0793e-08 | 0.005279 | 0.0052789 | 0.005279 | 0.97468 | -0.1785 | 0.97473 | -0.17812 | 1.9552
45 | 0.001151 | 0.00028825 | -0.001151 | -0.00028825 | 6.2044e-10 | -3.7727e-09 | 0.0017573 | 0.0017574 | 0.0017574 | 0.97457 | -0.17927 | 0.97457 | -0.17927 | 0.65087
46 | -0.0087694 | -0.0021972 | 0.0087712 | 0.0021977 | 1.7751e-06 | 4.8482e-07 | 0.013387 | 0.013387 | 0.013387 | 0.97473 | -0.17812 | 0.97494 | -0.17666 | 4.9582
47 | 0.00098738 | 0.00024724 | -0.00098736 | -0.00024745 | 2.5602e-08 | -2.151e-07 | 0.0015075 | 0.0015076 | 0.0015076 | 0.97457 | -0.17927 | 0.97455 | -0.17946 | 0.55836
48 | -0.011748 | -0.0029438 | 0.011752 | 0.002945 | 3.7535e-06 | 1.2103e-06 | 0.01793 | 0.01793 | 0.01793 | 0.97494 | -0.17666 | 0.97526 | -0.17435 | 6.6409
49 | -0.016951 | -0.0042481 | 0.016951 | 0.0042481 | 8.7216e-08 | 3.0937e-08 | 0.025863 | 0.025863 | 0.025863 | 0.97526 | -0.17435 | 0.97526 | -0.17431 | 9.579
50 | -0.0019979 | -0.00050073 | 0.001998 | 0.00050061 | 5.8262e-08 | -1.1232e-07 | 0.0029941 | 0.002994 | 0.0029941 | 0.99294 | -0.049159 | 0.99297 | -0.048948 | 1.1089
51 | -0.027404 | -0.0068709 | 0.02741 | 0.006873 | 6.0889e-06 | 2.0425e-06 | 0.041067 | 0.041067 | 0.041067 | 0.99297 | -0.048948 | 0.9932 | -0.047345 | 7.6049
52 | 0.025406 | 0.0063703 | -0.025396 | -0.006367 | 1.0059e-05 | 3.2938e-06 | 0.038073 | 0.038073 | 0.038073 | 0.99297 | -0.048948 | 0.99256 | -0.051807 | 7.0505
53 | 0.0090903 | 0.0022767 | -0.0090869 | -0.0022757 | 3.4092e-06 | 9.3016e-07 | 0.013619 | 0.013619 | 0.013619 | 0.9932 | -0.047345 | 0.99281 | -0.050058 | 5.044
54 | -0.0365 | -0.0091496 | 0.036511 | 0.0091537 | 1.1368e-05 | 4.0567e-06 | 0.054685 | 0.054685 | 0.054685 | 0.9932 | -0.047345 | 0.99352 | -0.045097 | 10.1269
55 | 0.023535 | 0.0059008 | -0.023527 | -0.0058983 | 7.8884e-06 | 2.5092e-06 | 0.035284 | 0.035284 | 0.035284 | 0.99256 | -0.051807 | 0.99222 | -0.054226 | 6.5341
56 | 0.00465 | 0.0011643 | -0.0046488 | -0.0011643 | 1.1969e-06 | -5.022e-08 | 0.006969 | 0.0069691 | 0.0069691 | 0.99281 | -0.050058 | 0.99255 | -0.051921 | 2.5812
57 | 0.0031783 | 0.00079607 | -0.0031781 | -0.00079618 | 2.0657e-07 | -1.092e-07 | 0.0047635 | 0.0047635 | 0.0047635 | 0.99281 | -0.050058 | 0.99275 | -0.050528 | 1.7643
58 | -0.038538 | -0.0096617 | 0.038556 | 0.009668 | 1.7442e-05 | 6.2737e-06 | 0.057721 | 0.057721 | 0.057721 | 0.99352 | -0.045097 | 0.99398 | -0.041831 | 10.6891
59 | 0.022103 | 0.0055412 | -0.022098 | -0.0055397 | 5.039e-06 | 1.5585e-06 | 0.033148 | 0.033148 | 0.033148 | 0.99222 | -0.054226 | 0.99199 | -0.055873 | 6.1385
60 | 0.0025908 | 0.00064853 | -0.0025908 | -0.00064856 | 3.5399e-08 | -3.4991e-08 | 0.0038839 | 0.0038839 | 0.0038839 | 0.99255 | -0.051921 | 0.99253 | -0.05202 | 1.4385
61 | 0.0016753 | 0.00041953 | -0.0016752 | -0.00041984 | 1.0515e-07 | -3.051e-07 | 0.0025109 | 0.0025111 | 0.0025111 | 0.99275 | -0.050528 | 0.99268 | -0.050982 | 0.93002
62 | -0.11775 | -0.029631 | 0.1179 | 0.029689 | 0.00015042 | 5.745e-05 | 0.17631 | 0.17631 | 0.17631 | 0.99398 | -0.041831 | 0.99529 | -0.032691 | 32.6506
63 | 0.079191 | 0.019963 | -0.079115 | -0.019935 | 7.6078e-05 | 2.8812e-05 | 0.11859 | 0.11859 | 0.11859 | 0.99398 | -0.041831 | 0.99299 | -0.048696 | 21.9616
64 | 0.0456 | 0.011445 | -0.045542 | -0.011423 | 5.7401e-05 | 2.1834e-05 | 0.069106 | 0.069106 | 0.069106 | 0.98196 | -0.12644 | 0.98068 | -0.13552 | 25.5948
65 | -0.04609 | -0.011568 | 0.046093 | 0.011569 | 3.0076e-06 | 1.1443e-06 | 0.069848 | 0.069848 | 0.069848 | 0.98196 | -0.12644 | 0.98203 | -0.12597 | 25.8696
66 | -0.048837 | -0.012257 | 0.048865 | 0.012267 | 2.8185e-05 | 1.0423e-05 | 0.074006 | 0.074006 | 0.074006 | 0.98203 | -0.12597 | 0.98261 | -0.12181 | 13.7049
67 | -0.049378 | -0.012396 | 0.049383 | 0.012398 | 4.429e-06 | 1.6391e-06 | 0.074783 | 0.074783 | 0.074783 | 0.98261 | -0.12181 | 0.9827 | -0.12117 | 13.8487
68 | -0.049858 | -0.012517 | 0.049891 | 0.012529 | 3.2869e-05 | 1.2173e-05 | 0.075503 | 0.075503 | 0.075503 | 0.9827 | -0.12117 | 0.98337 | -0.11642 | 13.9821
69 | -0.050351 | -0.012644 | 0.050373 | 0.012652 | 2.1873e-05 | 8.1062e-06 | 0.076199 | 0.076199 | 0.076199 | 0.98337 | -0.11642 | 0.98381 | -0.1133 | 14.111
70 | -0.020537 | -0.0051468 | 0.020539 | 0.0051477 | 2.5203e-06 | 9.1801e-07 | 0.031334 | 0.031334 | 0.031334 | 0.97526 | -0.17431 | 0.97539 | -0.17343 | 11.6053
71 | -0.021688 | -0.0054356 | 0.021689 | 0.0054358 | 4.5033e-07 | 1.6497e-07 | 0.033087 | 0.033087 | 0.033087 | 0.97539 | -0.17343 | 0.97541 | -0.17328 | 12.2545
72 | -0.024873 | -0.0062338 | 0.024892 | 0.006241 | 1.9543e-05 | 7.2449e-06 | 0.037944 | 0.037944 | 0.037944 | 0.97541 | -0.17328 | 0.9762 | -0.16761 | 14.0535
73 | -0.026872 | -0.0067371 | 0.02689 | 0.0067441 | 1.8858e-05 | 7.0279e-06 | 0.040961 | 0.040961 | 0.040961 | 0.9762 | -0.16761 | 0.9769 | -0.16254 | 15.1708
74 | -0.001776 | -0.00044511 | 0.0017762 | 0.00044462 | 2.1364e-07 | -4.9245e-07 | 0.0027184 | 0.0027182 | 0.0027184 | 0.97218 | -0.19728 | 0.97231 | -0.19641 | 1.0068
75 | 0.071335 | 0.01794 | -0.071333 | -0.017939 | 1.4453e-06 | 5.4559e-07 | 0.10744 | 0.10744 | 0.10744 | 0.98818 | -0.082419 | 0.98816 | -0.082565 | 19.8961
76 | -0.072213 | -0.01816 | 0.072281 | 0.018186 | 6.8153e-05 | 2.5739e-05 | 0.10876 | 0.10876 | 0.10876 | 0.98818 | -0.082419 | 0.98914 | -0.075654 | 20.141
77 | 0.070497 | 0.01773 | -0.070494 | -0.017729 | 2.7045e-06 | 1.0205e-06 | 0.10618 | 0.10618 | 0.10618 | 0.98816 | -0.082565 | 0.98812 | -0.08284 | 19.6628
78 | -0.072903 | -0.018342 | 0.072963 | 0.018364 | 6.0143e-05 | 2.272e-05 | 0.1097 | 0.1097 | 0.1097 | 0.98914 | -0.075654 | 0.98999 | -0.069746 | 20.3142
79 | 0.069361 | 0.017445 | -0.069322 | -0.01743 | 3.9491e-05 | 1.4892e-05 | 0.10447 | 0.10447 | 0.10447 | 0.98812 | -0.08284 | 0.98754 | -0.086926 | 19.3469
80 | -0.073942 | -0.01861 | 0.073991 | 0.018628 | 4.8987e-05 | 1.8514e-05 | 0.11117 | 0.11117 | 0.11117 | 0.98999 | -0.069746 | 0.99066 | -0.065003 | 20.5867
81 | 0.068163 | 0.017139 | -0.068098 | -0.017115 | 6.4284e-05 | 2.4226e-05 | 0.10273 | 0.10273 | 0.10273 | 0.98754 | -0.086926 | 0.98658 | -0.0937 | 19.0235
82 | -0.075633 | -0.01904 | 0.075676 | 0.019056 | 4.3047e-05 | 1.6281e-05 | 0.11363 | 0.11363 | 0.11363 | 0.99066 | -0.065003 | 0.99124 | -0.060931 | 21.0433
83 | 0.066457 | 0.016704 | -0.066455 | -0.016703 | 1.6474e-06 | 6.2019e-07 | 0.10025 | 0.10025 | 0.10025 | 0.98658 | -0.0937 | 0.98656 | -0.093878 | 18.565
84 | -0.076485 | -0.019259 | 0.076531 | 0.019276 | 4.647e-05 | 1.7582e-05 | 0.11485 | 0.11485 | 0.11485 | 0.99124 | -0.060931 | 0.99186 | -0.056585 | 21.2682
85 | 0.0016174 | 0.00040525 | -0.0016174 | -0.00040535 | 3.0825e-08 | -9.2576e-08 | 0.0024485 | 0.0024486 | 0.0024486 | 0.98291 | -0.11973 | 0.98289 | -0.11987 | 0.90688
86 | -0.0021304 | -0.00053383 | 0.0021305 | 0.0005337 | 8.1556e-08 | -1.279e-07 | 0.0032252 | 0.0032251 | 0.0032252 | 0.98291 | -0.11973 | 0.98295 | -0.11945 | 1.1945
87 | 0.00040741 | 0.0001021 | -0.00040741 | -0.00010211 | 8.7079e-11 | -4.6092e-09 | 0.00061679 | 0.00061679 | 0.00061679 | 0.98289 | -0.11987 | 0.98289 | -0.11987 | 0.22844
88 | -0.0048188 | -0.0012074 | 0.0048199 | 0.0012074 | 1.1524e-06 | 3.1901e-09 | 0.0072947 | 0.0072945 | 0.0072947 | 0.98295 | -0.11945 | 0.98319 | -0.11772 | 2.7017
89 | -0.0076567 | -0.0019175 | 0.0076586 | 0.0019179 | 1.8548e-06 | 4.3257e-07 | 0.011588 | 0.011587 | 0.011588 | 0.98319 | -0.11772 | 0.98344 | -0.11597 | 4.2917
90 | 0.0028368 | 0.00071002 | -0.0028367 | -0.00071006 | 6.6321e-08 | -4.7624e-08 | 0.004293 | 0.0042931 | 0.0042931 | 0.98319 | -0.11772 | 0.98317 | -0.11789 | 1.59
91 | 0.0060899 | 0.0015256 | -0.0060891 | -0.0015255 | 8.2426e-07 | 1.1965e-07 | 0.0092143 | 0.0092144 | 0.0092144 | 0.98344 | -0.11597 | 0.9833 | -0.11695 | 3.4127
92 | -0.013749 | -0.0034435 | 0.013754 | 0.0034452 | 5.08e-06 | 1.715e-06 | 0.020802 | 0.020802 | 0.020802 | 0.98344 | -0.11597 | 0.98381 | -0.1133 | 7.7044
93 | 0.0024475 | 0.00061251 | -0.0024472 | -0.00061279 | 2.5619e-07 | -2.8091e-07 | 0.0037039 | 0.0037041 | 0.0037041 | 0.98317 | -0.11789 | 0.98306 | -0.11865 | 1.3719
94 | 0.0054019 | 0.0013533 | -0.0054012 | -0.0013532 | 6.5984e-07 | 5.3076e-08 | 0.0081744 | 0.0081744 | 0.0081744 | 0.9833 | -0.11695 | 0.98317 | -0.11783 | 3.0276
95 | -0.064126 | -0.016098 | 0.064253 | 0.016145 | 0.00012604 | 4.7385e-05 | 0.097001 | 0.097 | 0.097001 | 0.98381 | -0.1133 | 0.98581 | -0.099176 | 17.9631
96 | 0.0024472 | 0.00061279 | -0.0024471 | -0.00061293 | 1.2363e-07 | -1.3553e-07 | 0.0037041 | 0.0037041 | 0.0037041 | 0.98306 | -0.11865 | 0.98301 | -0.11902 | 1.3719
97 | 0.064867 | 0.016305 | -0.06482 | -0.016287 | 4.7813e-05 | 1.7981e-05 | 0.097856 | 0.097856 | 0.097856 | 0.98656 | -0.093878 | 0.98581 | -0.099176 | 18.1215
98 | -0.07757 | -0.019537 | 0.077656 | 0.019569 | 8.565e-05 | 3.2419e-05 | 0.11641 | 0.11641 | 0.11641 | 0.99186 | -0.056585 | 0.99299 | -0.048696 | 21.5568
99 | 0.1235 | 0.031167 | -0.12337 | -0.031117 | 0.00012928 | 4.9401e-05 | 0.18385 | 0.18385 | 0.18385 | 1 | 0 | 0.99892 | -0.0074652 | 34.0464
100 | 0.12157 | 0.030666 | -0.12142 | -0.030608 | 0.00015156 | 5.7907e-05 | 0.18117 | 0.18117 | 0.18117 | 0.99892 | -0.0074652 | 0.99764 | -0.016366 | 33.5494
101 | 0.12033 | 0.030334 | -0.12005 | -0.030229 | 0.0002745 | 0.00010487 | 0.17954 | 0.17954 | 0.17954 | 0.99764 | -0.016366 | 0.99529 | -0.032691 | 33.2473
102 | 0.0031862 | 0.00079809 | -0.0031856 | -0.00079839 | 6.1498e-07 | -3.0083e-07 | 0.0048221 | 0.0048223 | 0.0048223 | 0.98317 | -0.11783 | 0.98298 | -0.11923 | 1.786
103 | 0.00063449 | 0.00015864 | -0.00063448 | -0.00015901 | 1.7232e-08 | -3.7292e-07 | 0.00096032 | 0.00096046 | 0.00096046 | 0.98301 | -0.11902 | 0.98298 | -0.11921 | 0.35573
104 | 0.0017132 | 0.00042886 | -0.001713 | -0.00042926 | 1.4529e-07 | -4.0029e-07 | 0.0025682 | 0.0025684 | 0.0025684 | 0.99253 | -0.05202 | 0.99245 | -0.052633 | 0.95125
105 | 0.00087763 | 0.00021971 | -0.0008776 | -0.00021995 | 2.1016e-08 | -2.4336e-07 | 0.0013157 | 0.0013157 | 0.0013157 | 0.99253 | -0.05202 | 0.99251 | -0.052193 | 0.48731
106 | 0.001713 | 0.00042926 | -0.001713 | -0.00042932 | 2.2063e-08 | -6.0774e-08 | 0.0025684 | 0.0025684 | 0.0025684 | 0.99245 | -0.052633 | 0.99243 | -0.052726 | 0.95126

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.12533 | 0.031424

## res_load
| p_mw | q_mvar
0 | 0.0010739 | 0.00026914
1 | 0.00060878 | 0.00015257
2 | 0.0009157 | 0.00022949
3 | 0.0010537 | 0.00026407
4 | 0.00047385 | 0.00011876
5 | 0.0026726 | 0.00066983
6 | 0.0029722 | 0.00074492
7 | 0.00014702 | 3.6846e-05
8 | 8.6128e-05 | 2.1586e-05
9 | 0.0010576 | 0.00026507
10 | 0.00046028 | 0.00011536
11 | 0.0060114 | 0.0015066
12 | 0.00017484 | 4.3819e-05
13 | 0.0014491 | 0.00036317
14 | 0.00030836 | 7.7281e-05
15 | 0.00099922 | 0.00025043
16 | 0.00027049 | 6.7791e-05
17 | 0.0007254 | 0.0001818
18 | 0.00068914 | 0.00017272
19 | 0.0010297 | 0.00025806
20 | 0.00038818 | 9.7288e-05
21 | 0.00031971 | 8.0126e-05
22 | 0.0014597 | 0.00036583
23 | 0.0038195 | 0.00095727
24 | 0.0014866 | 0.00037257
25 | 0.00091413 | 0.0002291
26 | 0.0002924 | 7.3283e-05
27 | 0.0011001 | 0.0002757
28 | 0.0053112 | 0.0013311
29 | 0.00016364 | 4.1013e-05
30 | 0.0029768 | 0.00074606
31 | 0.00098736 | 0.00024745
32 | 0.0051993 | 0.0013031
33 | 0.0019979 | 0.00050073
34 | 0.0018602 | 0.00046622
35 | 0.0012585 | 0.00031542
36 | 0.002027 | 0.000508
37 | 0.0014247 | 0.00035706
38 | 0.002058 | 0.00051578
39 | 0.0015028 | 0.00037665
40 | 0.0012783 | 0.00032036
41 | 0.00048969 | 0.00012273
42 | 0.00045277 | 0.00011347
43 | 0.0027443 | 0.00068778
44 | 0.00051303 | 0.00012858
45 | 0.00047557 | 0.00011919
46 | 0.00046007 | 0.0001153
47 | 0.0035858 | 0.00089869
48 | 0.0011489 | 0.00028793
49 | 0.003184 | 0.00079799
50 | 0.0019792 | 0.00049603
51 | 0.0052159 | 0.0013072
52 | 0.001776 | 0.00044511
53 | 0.00087564 | 0.00021946
54 | 0.00087845 | 0.00022016
55 | 0.00083654 | 0.00020966
56 | 0.00062189 | 0.00015586
57 | 0.0011329 | 0.00028393
58 | 0.00097902 | 0.00024537
59 | 0.0011591 | 0.0002905
60 | 0.0016416 | 0.00041142
61 | 0.0016416 | 0.00041143
62 | 0.00080884 | 0.00020272
63 | 0.00051301 | 0.00012857
64 | 0.00121 | 0.00030324
65 | 0.0026883 | 0.00067374
66 | 0.00040741 | 0.00010211
67 | 0.00038924 | 9.7554e-05
68 | 0.00068725 | 0.00017224
69 | 0.0015876 | 0.0003979
70 | 0.00056709 | 0.00014213
71 | 0.0010391 | 0.00026041
72 | 0.001459 | 0.00036565
73 | 0.0010274 | 0.00025749
74 | 0.0018018 | 0.00045158
75 | 0.0010936 | 0.00027409
76 | 0.002215 | 0.00055512
77 | 0.0018126 | 0.00045429
78 | 0.00063448 | 0.00015901
79 | 0.0016752 | 0.00041984
80 | 0.0008776 | 0.00021995
81 | 0.001713 | 0.00042932
82 | 0.0021553 | 0.00054017
83 | 0.0031856 | 0.00079839

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1