## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2430-4_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2430-4_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2430-4_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2430-4_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2430-4_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2430-4_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_2430-4_0_3_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2430-4_0_3_node_54 | 0.4 | n |  | TRUE
8 | bus_LV_2430-4_0_3_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_2430-4_0_3_node_65 | 0.4 | n |  | TRUE
10 | bus_LV_2430-4_0_3_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_2430-4_0_3_node_100 | 0.4 | n |  | TRUE
12 | bus_LV_2430-4_0_3_node_83 | 0.4 | n |  | TRUE
13 | bus_LV_2430-4_0_3_node_53 | 0.4 | n |  | TRUE
14 | bus_LV_2430-4_0_3_node_63 | 0.4 | n |  | TRUE
15 | bus_LV_2430-4_0_3_node_84 | 0.4 | n |  | TRUE
16 | bus_LV_2430-4_0_3_node_111 | 0.4 | n |  | TRUE
17 | bus_LV_2430-4_0_3_node_126 | 0.4 | n |  | TRUE
18 | bus_LV_2430-4_0_3_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_2430-4_0_3_node_99 | 0.4 | n |  | TRUE
20 | bus_LV_2430-4_0_3_node_8 | 0.4 | n |  | TRUE
21 | bus_LV_2430-4_0_3_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_2430-4_0_3_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_2430-4_0_3_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_2430-4_0_3_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_2430-4_0_3_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2430-4_0_3_node_120 | 0.4 | n |  | TRUE
27 | bus_LV_2430-4_0_3_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_2430-4_0_3_node_121 | 0.4 | n |  | TRUE
29 | bus_LV_2430-4_0_3_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_2430-4_0_3_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_2430-4_0_3_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_2430-4_0_3_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_2430-4_0_3_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_2430-4_0_3_node_35 | 0.4 | n |  | TRUE
35 | bus_LV_2430-4_0_3_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_2430-4_0_3_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_2430-4_0_3_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_2430-4_0_3_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_2430-4_0_3_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_2430-4_0_3_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_2430-4_0_3_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_2430-4_0_3_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_2430-4_0_3_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_2430-4_0_3_node_119 | 0.4 | n |  | TRUE
45 | bus_LV_2430-4_0_3_node_116 | 0.4 | n |  | TRUE
46 | bus_LV_2430-4_0_3_node_66 | 0.4 | n |  | TRUE
47 | bus_LV_2430-4_0_3_node_71 | 0.4 | n |  | TRUE
48 | bus_LV_2430-4_0_3_node_49 | 0.4 | n |  | TRUE
49 | bus_LV_2430-4_0_3_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_2430-4_0_3_node_28 | 0.4 | n |  | TRUE
51 | bus_LV_2430-4_0_3_node_29 | 0.4 | n |  | TRUE
52 | bus_LV_2430-4_0_3_node_38 | 0.4 | n |  | TRUE
53 | bus_LV_2430-4_0_3_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_2430-4_0_3_node_33 | 0.4 | n |  | TRUE
55 | bus_LV_2430-4_0_3_node_112 | 0.4 | n |  | TRUE
56 | bus_LV_2430-4_0_3_node_118 | 0.4 | n |  | TRUE
57 | bus_LV_2430-4_0_3_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_2430-4_0_3_node_43 | 0.4 | n |  | TRUE
59 | bus_LV_2430-4_0_3_node_74 | 0.4 | n |  | TRUE
60 | bus_LV_2430-4_0_3_node_117 | 0.4 | n |  | TRUE
61 | bus_LV_2430-4_0_3_node_133 | 0.4 | n |  | TRUE
62 | bus_LV_2430-4_0_3_node_50 | 0.4 | n |  | TRUE
63 | bus_LV_2430-4_0_3_node_98 | 0.4 | n |  | TRUE
64 | bus_LV_2430-4_0_3_node_96 | 0.4 | n |  | TRUE
65 | bus_LV_2430-4_0_3_node_108 | 0.4 | n |  | TRUE
66 | bus_LV_2430-4_0_3_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_2430-4_0_3_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_2430-4_0_3_node_64 | 0.4 | n |  | TRUE
69 | bus_LV_2430-4_0_3_node_40 | 0.4 | n |  | TRUE
70 | bus_LV_2430-4_0_3_node_41 | 0.4 | n |  | TRUE
71 | bus_LV_2430-4_0_3_node_42 | 0.4 | n |  | TRUE
72 | bus_LV_2430-4_0_3_node_44 | 0.4 | n |  | TRUE
73 | bus_LV_2430-4_0_3_node_55 | 0.4 | n |  | TRUE
74 | bus_LV_2430-4_0_3_node_56 | 0.4 | n |  | TRUE
75 | bus_LV_2430-4_0_3_node_132 | 0.4 | n |  | TRUE
76 | bus_LV_2430-4_0_3_node_102 | 0.4 | n |  | TRUE
77 | bus_LV_2430-4_0_3_node_48 | 0.4 | n |  | TRUE
78 | bus_LV_2430-4_0_3_node_113 | 0.4 | n |  | TRUE
79 | bus_LV_2430-4_0_3_node_114 | 0.4 | n |  | TRUE
80 | bus_LV_2430-4_0_3_node_115 | 0.4 | n |  | TRUE
81 | bus_LV_2430-4_0_3_node_127 | 0.4 | n |  | TRUE
82 | bus_LV_2430-4_0_3_node_97 | 0.4 | n |  | TRUE
83 | bus_LV_2430-4_0_3_node_95 | 0.4 | n |  | TRUE
84 | bus_LV_2430-4_0_3_node_107 | 0.4 | n |  | TRUE
85 | bus_LV_2430-4_0_3_node_131 | 0.4 | n |  | TRUE
86 | bus_LV_2430-4_0_3_node_101 | 0.4 | n |  | TRUE
87 | bus_LV_2430-4_0_3_node_93 | 0.4 | n |  | TRUE
88 | bus_LV_2430-4_0_3_node_57 | 0.4 | n |  | TRUE
89 | bus_LV_2430-4_0_3_node_58 | 0.4 | n |  | TRUE
90 | bus_LV_2430-4_0_3_node_59 | 0.4 | n |  | TRUE
91 | bus_LV_2430-4_0_3_node_60 | 0.4 | n |  | TRUE
92 | bus_LV_2430-4_0_3_node_62 | 0.4 | n |  | TRUE
93 | bus_LV_2430-4_0_3_node_123 | 0.4 | n |  | TRUE
94 | bus_LV_2430-4_0_3_node_70 | 0.4 | n |  | TRUE
95 | bus_LV_2430-4_0_3_node_76 | 0.4 | n |  | TRUE
96 | bus_LV_2430-4_0_3_node_68 | 0.4 | n |  | TRUE
97 | bus_LV_2430-4_0_3_node_124 | 0.4 | n |  | TRUE
98 | bus_LV_2430-4_0_3_node_122 | 0.4 | n |  | TRUE
99 | bus_LV_2430-4_0_3_node_67 | 0.4 | n |  | TRUE
100 | bus_LV_2430-4_0_3_node_69 | 0.4 | n |  | TRUE
101 | bus_LV_2430-4_0_3_node_75 | 0.4 | n |  | TRUE
102 | bus_LV_2430-4_0_3_node_72 | 0.4 | n |  | TRUE
103 | bus_LV_2430-4_0_3_node_73 | 0.4 | n |  | TRUE
104 | bus_LV_2430-4_0_3_node_77 | 0.4 | n |  | TRUE
105 | bus_LV_2430-4_0_3_node_78 | 0.4 | n |  | TRUE
106 | bus_LV_2430-4_0_3_node_79 | 0.4 | n |  | TRUE
107 | bus_LV_2430-4_0_3_node_80 | 0.4 | n |  | TRUE
108 | bus_LV_2430-4_0_3_node_81 | 0.4 | n |  | TRUE
109 | bus_LV_2430-4_0_3_node_103 | 0.4 | n |  | TRUE
110 | bus_LV_2430-4_0_3_node_105 | 0.4 | n |  | TRUE
111 | bus_LV_2430-4_0_3_node_85 | 0.4 | n |  | TRUE
112 | bus_LV_2430-4_0_3_node_86 | 0.4 | n |  | TRUE
113 | bus_LV_2430-4_0_3_node_87 | 0.4 | n |  | TRUE
114 | bus_LV_2430-4_0_3_node_88 | 0.4 | n |  | TRUE
115 | bus_LV_2430-4_0_3_node_89 | 0.4 | n |  | TRUE
116 | bus_LV_2430-4_0_3_node_90 | 0.4 | n |  | TRUE
117 | bus_LV_2430-4_0_3_node_125 | 0.4 | n |  | TRUE
118 | bus_LV_2430-4_0_3_node_91 | 0.4 | n |  | TRUE
119 | bus_LV_2430-4_0_3_node_92 | 0.4 | n |  | TRUE
120 | bus_LV_2430-4_0_3_node_94 | 0.4 | n |  | TRUE
121 | bus_LV_2430-4_0_3_node_130 | 0.4 | n |  | TRUE
122 | bus_LV_2430-4_0_3_node_128 | 0.4 | n |  | TRUE
123 | bus_LV_2430-4_0_3_node_109 | 0.4 | n |  | TRUE
124 | bus_LV_2430-4_0_3_node_110 | 0.4 | n |  | TRUE
125 | bus_MV_292_0_node_17 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2430-4_0_3_load_0 | 0 | 0.0041206 | 0.0010327 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2430-4_0_3_load_2 | 2 | 0.0024025 | 0.00060212 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2430-4_0_3_load_3 | 3 | 0.0019143 | 0.00047977 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2430-4_0_3_load_6 | 5 | 0.002307 | 0.00057819 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2430-4_0_3_load_7 | 6 | 0.00094988 | 0.00023806 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2430-4_0_3_load_54 | 7 | 0.0018434 | 0.00046199 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2430-4_0_3_load_4 | 8 | 0.0011457 | 0.00028715 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2430-4_0_3_load_65 | 9 | 0.0013884 | 0.00034797 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2430-4_0_3_load_27 | 10 | 0.0023789 | 0.00059622 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2430-4_0_3_load_100 | 11 | 0.0021199 | 0.00053128 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2430-4_0_3_load_83 | 12 | 0.0026815 | 0.00067204 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2430-4_0_3_load_53 | 13 | 0.0023095 | 0.00057881 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2430-4_0_3_load_63 | 14 | 0.0023377 | 0.00058587 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2430-4_0_3_load_111 | 16 | 0.0017827 | 0.0004468 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2430-4_0_3_load_126 | 17 | 0.0020822 | 0.00052184 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2430-4_0_3_load_26 | 18 | 0.001368 | 0.00034286 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2430-4_0_3_load_99 | 19 | 0.0017912 | 0.00044893 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2430-4_0_3_load_8 | 20 | 0.0017147 | 0.00042974 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2430-4_0_3_load_9 | 21 | 0.0050981 | 0.0012777 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2430-4_0_3_load_11 | 23 | 0.0011981 | 0.00030028 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2430-4_0_3_load_12 | 24 | 0.00078284 | 0.0001962 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2430-4_0_3_load_13 | 25 | 0.0027525 | 0.00068985 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2430-4_0_3_load_120 | 26 | 0.0013096 | 0.00032821 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2430-4_0_3_load_18 | 27 | 0.0014551 | 0.00036467 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2430-4_0_3_load_121 | 28 | 0.0020945 | 0.00052492 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2430-4_0_3_load_16 | 29 | 0.0019976 | 0.00050064 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2430-4_0_3_load_14 | 30 | 0.00027094 | 6.7903e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2430-4_0_3_load_15 | 31 | 0.0054684 | 0.0013705 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2430-4_0_3_load_17 | 32 | 0.00026839 | 6.7264e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2430-4_0_3_load_34 | 35 | 0.0091158 | 0.0022846 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2430-4_0_3_load_19 | 36 | 0.0011028 | 0.00027638 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2430-4_0_3_load_20 | 37 | 0.0023353 | 0.00058527 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2430-4_0_3_load_22 | 39 | 0.0037508 | 0.00094003 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2430-4_0_3_load_24 | 41 | 0.00098289 | 0.00024634 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2430-4_0_3_load_37 | 43 | 0.0028684 | 0.0007189 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2430-4_0_3_load_119 | 44 | 0.0030627 | 0.00076758 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2430-4_0_3_load_116 | 45 | 0.0018501 | 0.00046367 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2430-4_0_3_load_66 | 46 | 0.0022087 | 0.00055356 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2430-4_0_3_load_71 | 47 | 0.0023809 | 0.00059671 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2430-4_0_3_load_46 | 49 | 0.0001036 | 2.5966e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2430-4_0_3_load_28 | 50 | 0.00090736 | 0.00022741 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2430-4_0_3_load_29 | 51 | 0.0008263 | 0.00020709 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2430-4_0_3_load_38 | 52 | 0.0010638 | 0.00026662 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2430-4_0_3_load_39 | 53 | 0.0012524 | 0.00031388 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2430-4_0_3_load_112 | 55 | 0.0013677 | 0.00034279 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2430-4_0_3_load_118 | 56 | 0.00096485 | 0.00024181 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2430-4_0_3_load_45 | 57 | 0.0010971 | 0.00027495 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2430-4_0_3_load_43 | 58 | 0.0011904 | 0.00029835 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2430-4_0_3_load_117 | 60 | 0.001 | 0.00025063 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2430-4_0_3_load_133 | 61 | 0.00028756 | 7.2069e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2430-4_0_3_load_108 | 65 | 0.0022983 | 0.00057601 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2430-4_0_3_load_47 | 67 | 7.1354e-05 | 1.7883e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2430-4_0_3_load_64 | 68 | 0.0011867 | 0.00029741 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2430-4_0_3_load_40 | 69 | 0.0012772 | 0.00032011 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2430-4_0_3_load_41 | 70 | 0.0016465 | 0.00041265 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2430-4_0_3_load_42 | 71 | 0.0020087 | 0.00050343 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2430-4_0_3_load_55 | 73 | 0.0017364 | 0.00043518 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2430-4_0_3_load_56 | 74 | 0.0019953 | 0.00050008 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2430-4_0_3_load_132 | 75 | 0.0044873 | 0.0011246 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2430-4_0_3_load_48 | 77 | 0.00069577 | 0.00017438 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2430-4_0_3_load_113 | 78 | 0.0014355 | 0.00035978 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2430-4_0_3_load_115 | 80 | 0.00014254 | 3.5723e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2430-4_0_3_load_127 | 81 | 0.0040955 | 0.0010264 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2430-4_0_3_load_97 | 82 | 0.0020414 | 0.00051163 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2430-4_0_3_load_95 | 83 | 0.0023963 | 0.00060058 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2430-4_0_3_load_107 | 84 | 0.0056075 | 0.0014054 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2430-4_0_3_load_131 | 85 | 0.0022667 | 0.0005681 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2430-4_0_3_load_101 | 86 | 0.0051359 | 0.0012872 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2430-4_0_3_load_93 | 87 | 0.001267 | 0.00031753 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2430-4_0_3_load_57 | 88 | 0.0011898 | 0.00029819 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2430-4_0_3_load_58 | 89 | 0.0014708 | 0.00036862 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2430-4_0_3_load_59 | 90 | 0.0011345 | 0.00028432 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2430-4_0_3_load_60 | 91 | 0.0013939 | 0.00034935 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2430-4_0_3_load_62 | 92 | 0.00096125 | 0.00024091 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2430-4_0_3_load_68 | 96 | 0.0015386 | 0.00038561 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2430-4_0_3_load_124 | 97 | 0.00088673 | 0.00022223 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2430-4_0_3_load_122 | 98 | 0.0013663 | 0.00034242 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2430-4_0_3_load_67 | 99 | 0.0044896 | 0.0011252 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2430-4_0_3_load_69 | 100 | 0.0021144 | 0.00052991 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2430-4_0_3_load_75 | 101 | 0.0058329 | 0.0014619 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2430-4_0_3_load_72 | 102 | 0.0017271 | 0.00043285 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2430-4_0_3_load_73 | 103 | 0.0018575 | 0.00046554 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2430-4_0_3_load_77 | 104 | 0.0014452 | 0.00036221 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2430-4_0_3_load_78 | 105 | 0.0031043 | 0.000778 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2430-4_0_3_load_81 | 108 | 0.0016976 | 0.00042546 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2430-4_0_3_load_105 | 110 | 0.0017883 | 0.00044818 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2430-4_0_3_load_85 | 111 | 0.00081783 | 0.00020497 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2430-4_0_3_load_86 | 112 | 0.0018952 | 0.00047497 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2430-4_0_3_load_88 | 114 | 0.0020347 | 0.00050994 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2430-4_0_3_load_89 | 115 | 0.0021582 | 0.0005409 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2430-4_0_3_load_125 | 117 | 0.002347 | 0.00058821 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2430-4_0_3_load_91 | 118 | 0.012726 | 0.0031893 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2430-4_0_3_load_130 | 121 | 0.0019267 | 0.00048287 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2430-4_0_3_load_128 | 122 | 0.003202 | 0.00080249 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2430-4_0_3_load_109 | 123 | 0.00064523 | 0.00016171 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2430-4_0_3_load_110 | 124 | 0.00011189 | 2.8043e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2430-4_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.017797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2430-4_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.024881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2430-4_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.012156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2430-4_0_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.026089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2430-4_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.024246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2430-4_0_3_line_5 | NAYY 4x150 SE | 2 | 6 | 0.012547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2430-4_0_3_line_6 | NAYY 4x150 SE | 3 | 7 | 0.0076943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2430-4_0_3_line_7 | NAYY 4x150 SE | 4 | 10 | 0.017274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2430-4_0_3_line_8 | NAYY 4x150 SE | 4 | 11 | 0.014319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2430-4_0_3_line_9 | NAYY 4x150 SE | 6 | 12 | 0.0028473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2430-4_0_3_line_10 | NAYY 4x150 SE | 7 | 13 | 0.017094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2430-4_0_3_line_11 | NAYY 4x150 SE | 8 | 9 | 0.013266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2430-4_0_3_line_12 | NAYY 4x150 SE | 9 | 14 | 0.001246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2430-4_0_3_line_13 | NAYY 4x150 SE | 10 | 18 | 0.020044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2430-4_0_3_line_14 | NAYY 4x150 SE | 11 | 19 | 0.014908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_2430-4_0_3_line_15 | NAYY 4x150 SE | 12 | 15 | 0.013646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2430-4_0_3_line_16 | NAYY 4x150 SE | 13 | 72 | 0.018332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2430-4_0_3_line_17 | NAYY 4x150 SE | 14 | 68 | 0.016441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_2430-4_0_3_line_18 | NAYY 4x150 SE | 15 | 16 | 0.052605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2430-4_0_3_line_19 | NAYY 4x150 SE | 15 | 17 | 0.0082074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2430-4_0_3_line_20 | NAYY 4x150 SE | 16 | 59 | 0.0018272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2430-4_0_3_line_21 | NAYY 4x150 SE | 17 | 97 | 0.02144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2430-4_0_3_line_22 | NAYY 4x150 SE | 18 | 50 | 0.0037743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2430-4_0_3_line_23 | NAYY 4x150 SE | 19 | 39 | 0.0040031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_2430-4_0_3_line_24 | NAYY 4x150 SE | 20 | 21 | 0.006252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2430-4_0_3_line_25 | NAYY 4x150 SE | 20 | 22 | 0.033998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2430-4_0_3_line_26 | NAYY 4x150 SE | 21 | 23 | 0.011003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2430-4_0_3_line_27 | NAYY 4x150 SE | 22 | 24 | 0.015956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2430-4_0_3_line_28 | NAYY 4x150 SE | 22 | 25 | 0.019317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2430-4_0_3_line_29 | NAYY 4x150 SE | 24 | 26 | 0.013841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2430-4_0_3_line_30 | NAYY 4x150 SE | 25 | 27 | 0.0050469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2430-4_0_3_line_31 | NAYY 4x150 SE | 26 | 28 | 0.01649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2430-4_0_3_line_32 | NAYY 4x150 SE | 27 | 29 | 0.0089622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2430-4_0_3_line_33 | NAYY 4x150 SE | 29 | 30 | 0.0088864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2430-4_0_3_line_34 | NAYY 4x150 SE | 30 | 31 | 0.0045174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2430-4_0_3_line_35 | NAYY 4x150 SE | 31 | 32 | 0.0094061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2430-4_0_3_line_36 | NAYY 4x150 SE | 32 | 33 | 0.012671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2430-4_0_3_line_37 | NAYY 4x150 SE | 33 | 34 | 0.001584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2430-4_0_3_line_38 | NAYY 4x150 SE | 33 | 35 | 0.014688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2430-4_0_3_line_39 | NAYY 4x150 SE | 34 | 48 | 0.024712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2430-4_0_3_line_40 | NAYY 4x150 SE | 34 | 49 | 0.014261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2430-4_0_3_line_41 | NAYY 4x150 SE | 35 | 40 | 0.025989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2430-4_0_3_line_42 | NAYY 4x150 SE | 36 | 37 | 0.011303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
43 | LV_2430-4_0_3_line_43 | NAYY 4x150 SE | 36 | 38 | 0.020495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
44 | LV_2430-4_0_3_line_44 | NAYY 4x150 SE | 37 | 39 | 0.036414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
45 | LV_2430-4_0_3_line_45 | NAYY 4x150 SE | 38 | 40 | 0.027553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
46 | LV_2430-4_0_3_line_46 | NAYY 4x150 SE | 38 | 41 | 0.034897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2430-4_0_3_line_47 | NAYY 4x150 SE | 40 | 42 | 0.030299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2430-4_0_3_line_48 | NAYY 4x150 SE | 40 | 43 | 0.021685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_2430-4_0_3_line_49 | NAYY 4x150 SE | 41 | 44 | 0.0017952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2430-4_0_3_line_50 | NAYY 4x150 SE | 42 | 45 | 0.0031621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2430-4_0_3_line_51 | NAYY 4x150 SE | 43 | 46 | 0.0072708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
52 | LV_2430-4_0_3_line_52 | NAYY 4x150 SE | 44 | 47 | 0.0071502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2430-4_0_3_line_53 | NAYY 4x150 SE | 45 | 66 | 0.015396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2430-4_0_3_line_54 | NAYY 4x150 SE | 46 | 68 | 0.011813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_2430-4_0_3_line_55 | NAYY 4x150 SE | 47 | 100 | 0.015117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2430-4_0_3_line_56 | NAYY 4x150 SE | 48 | 61 | 0.019561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2430-4_0_3_line_57 | NAYY 4x150 SE | 49 | 67 | 0.012036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2430-4_0_3_line_58 | NAYY 4x150 SE | 50 | 51 | 0.015098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2430-4_0_3_line_59 | NAYY 4x150 SE | 51 | 52 | 0.0040537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2430-4_0_3_line_60 | NAYY 4x150 SE | 52 | 53 | 0.018898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2430-4_0_3_line_61 | NAYY 4x150 SE | 53 | 69 | 0.031633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2430-4_0_3_line_62 | NAYY 4x150 SE | 54 | 55 | 0.032403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2430-4_0_3_line_63 | NAYY 4x150 SE | 54 | 56 | 0.05135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2430-4_0_3_line_64 | NAYY 4x150 SE | 55 | 59 | 0.0097968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2430-4_0_3_line_65 | NAYY 4x150 SE | 56 | 60 | 0.0070758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2430-4_0_3_line_66 | NAYY 4x150 SE | 57 | 58 | 0.012874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2430-4_0_3_line_67 | NAYY 4x150 SE | 58 | 70 | 0.019054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2430-4_0_3_line_68 | NAYY 4x150 SE | 59 | 103 | 0.015079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2430-4_0_3_line_69 | NAYY 4x150 SE | 62 | 63 | 0.029199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2430-4_0_3_line_70 | NAYY 4x150 SE | 62 | 64 | 0.017903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2430-4_0_3_line_71 | NAYY 4x150 SE | 62 | 65 | 0.012323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2430-4_0_3_line_72 | NAYY 4x150 SE | 63 | 81 | 0.020327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2430-4_0_3_line_73 | NAYY 4x150 SE | 63 | 66 | 0.02974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2430-4_0_3_line_74 | NAYY 4x150 SE | 64 | 82 | 0.020995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2430-4_0_3_line_75 | NAYY 4x150 SE | 64 | 83 | 0.016672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2430-4_0_3_line_76 | NAYY 4x150 SE | 65 | 84 | 0.0030293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2430-4_0_3_line_77 | NAYY 4x150 SE | 67 | 77 | 0.040211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2430-4_0_3_line_78 | NAYY 4x150 SE | 70 | 71 | 0.0099216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2430-4_0_3_line_79 | NAYY 4x150 SE | 71 | 72 | 0.021126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2430-4_0_3_line_80 | NAYY 4x150 SE | 72 | 73 | 0.011943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2430-4_0_3_line_81 | NAYY 4x150 SE | 72 | 74 | 0.033016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2430-4_0_3_line_82 | NAYY 4x150 SE | 73 | 75 | 0.03314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2430-4_0_3_line_83 | NAYY 4x150 SE | 74 | 76 | 0.008298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2430-4_0_3_line_84 | NAYY 4x150 SE | 75 | 85 | 0.0039734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2430-4_0_3_line_85 | NAYY 4x150 SE | 76 | 86 | 0.062616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2430-4_0_3_line_86 | NAYY 4x150 SE | 76 | 87 | 0.026921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2430-4_0_3_line_87 | NAYY 4x150 SE | 78 | 79 | 0.045348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2430-4_0_3_line_88 | NAYY 4x150 SE | 79 | 80 | 0.037175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2430-4_0_3_line_89 | NAYY 4x150 SE | 80 | 124 | 0.067434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2430-4_0_3_line_90 | NAYY 4x150 SE | 81 | 122 | 0.0016332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2430-4_0_3_line_91 | NAYY 4x150 SE | 83 | 116 | 0.019652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2430-4_0_3_line_92 | NAYY 4x150 SE | 84 | 123 | 0.039613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2430-4_0_3_line_93 | NAYY 4x150 SE | 85 | 120 | 0.0097518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2430-4_0_3_line_94 | NAYY 4x150 SE | 86 | 107 | 0.025376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2430-4_0_3_line_95 | NAYY 4x150 SE | 87 | 119 | 0.016993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2430-4_0_3_line_96 | NAYY 4x150 SE | 88 | 89 | 0.010474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2430-4_0_3_line_97 | NAYY 4x150 SE | 88 | 90 | 0.012852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2430-4_0_3_line_98 | NAYY 4x150 SE | 89 | 91 | 0.010848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2430-4_0_3_line_99 | NAYY 4x150 SE | 91 | 92 | 0.021091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2430-4_0_3_line_100 | NAYY 4x150 SE | 92 | 93 | 0.01715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2430-4_0_3_line_101 | NAYY 4x150 SE | 93 | 97 | 0.011093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2430-4_0_3_line_102 | NAYY 4x150 SE | 93 | 98 | 0.067143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2430-4_0_3_line_103 | NAYY 4x150 SE | 94 | 95 | 0.035299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2430-4_0_3_line_104 | NAYY 4x150 SE | 94 | 96 | 0.065466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2430-4_0_3_line_105 | NAYY 4x150 SE | 95 | 101 | 0.020862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2430-4_0_3_line_106 | NAYY 4x150 SE | 96 | 99 | 0.03329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2430-4_0_3_line_107 | NAYY 4x150 SE | 99 | 100 | 0.014499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2430-4_0_3_line_108 | NAYY 4x150 SE | 102 | 103 | 0.015774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2430-4_0_3_line_109 | NAYY 4x150 SE | 104 | 105 | 0.010441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2430-4_0_3_line_110 | NAYY 4x150 SE | 104 | 106 | 0.0092065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2430-4_0_3_line_111 | NAYY 4x150 SE | 105 | 107 | 0.01089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2430-4_0_3_line_112 | NAYY 4x150 SE | 106 | 108 | 0.016963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2430-4_0_3_line_113 | NAYY 4x150 SE | 107 | 109 | 0.010195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2430-4_0_3_line_114 | NAYY 4x150 SE | 109 | 110 | 0.067839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2430-4_0_3_line_115 | NAYY 4x150 SE | 111 | 112 | 0.054545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2430-4_0_3_line_116 | NAYY 4x150 SE | 111 | 113 | 0.0025278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2430-4_0_3_line_117 | NAYY 4x150 SE | 112 | 114 | 0.006079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2430-4_0_3_line_118 | NAYY 4x150 SE | 113 | 115 | 0.059985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2430-4_0_3_line_119 | NAYY 4x150 SE | 113 | 116 | 0.029368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2430-4_0_3_line_120 | NAYY 4x150 SE | 114 | 117 | 0.0061261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2430-4_0_3_line_121 | NAYY 4x150 SE | 118 | 119 | 0.0098567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2430-4_0_3_line_122 | NAYY 4x150 SE | 120 | 121 | 0.010829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_2430-4_0_3_line_123 | NAYY 4x150 SE | 123 | 124 | 0.0073779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2430-4_0_3_trafo_63 | 0.25 MVA 20/0.4 kV | 125 | 14 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2606428.653 | 1236627.8475 | 2606419.4507 | 1236643.0804
1 | 2606405.312 | 1236663.5332 | 2606416.041 | 1236648.7245 | 2606419.4507 | 1236643.0804
2 | 2606428.653 | 1236627.8475 | 2606438.8785 | 1236634.4207
3 | 2606406.045 | 1236614.7153 | 2606428.653 | 1236627.8475
4 | 2606405.312 | 1236663.5332 | 2606390.1971 | 1236682.4916
5 | 2606405.312 | 1236663.5332 | 2606395.6774 | 1236655.4962
6 | 2606438.8785 | 1236634.4207 | 2606445.3508 | 1236638.5814
7 | 2606406.045 | 1236614.7153 | 2606391.3611 | 1236605.6165
8 | 2606406.045 | 1236614.7153 | 2606414.5145 | 1236603.1691
9 | 2606395.6774 | 1236655.4962 | 2606393.491 | 1236653.6723
10 | 2606459.73 | 1236647.8248 | 2606445.3508 | 1236638.5814
11 | 2606462.0398 | 1236589.3393 | 2606453.3497 | 1236599.3624
12 | 2606462.856 | 1236588.3979 | 2606462.0398 | 1236589.3393
13 | 2606374.3228 | 1236595.059 | 2606391.3611 | 1236605.6165
14 | 2606423.3321 | 1236591.1484 | 2606414.5145 | 1236603.1691
15 | 2606383.0125 | 1236644.9314 | 2606393.491 | 1236653.6723
16 | 2606475.151 | 1236657.7379 | 2606459.73 | 1236647.8248
17 | 2606462.856 | 1236588.3979 | 2606469.0521 | 1236581.2513 | 2606473.0445 | 1236575.5224
18 | 2606383.0125 | 1236644.9314 | 2606350.5258 | 1236686.307
19 | 2606383.0125 | 1236644.9314 | 2606375.0598 | 1236642.9027
20 | 2606349.3975 | 1236687.7442 | 2606350.5258 | 1236686.307
21 | 2606354.2854 | 1236637.6032 | 2606375.0598 | 1236642.9027
22 | 2606371.1145 | 1236593.071 | 2606374.3228 | 1236595.059
23 | 2606423.3321 | 1236591.1484 | 2606425.6998 | 1236587.9206
24 | 2606431.7915 | 1236450.2518 | 2606427.0633 | 1236446.1614
25 | 2606457.9798 | 1236471.9281 | 2606437.3651 | 1236455.0735 | 2606431.7915 | 1236450.2518
26 | 2606418.7421 | 1236438.9627 | 2606427.0633 | 1236446.1614
27 | 2606457.9798 | 1236471.9281 | 2606467.0208 | 1236458.7809
28 | 2606457.9798 | 1236471.9281 | 2606471.3987 | 1236481.9932 | 2606473.574 | 1236483.3092
29 | 2606467.0208 | 1236458.7809 | 2606474.8634 | 1236447.3762
30 | 2606473.574 | 1236483.3092 | 2606477.8921 | 1236485.9216
31 | 2606484.2072 | 1236433.7886 | 2606474.8634 | 1236447.3762
32 | 2606485.5669 | 1236490.5489 | 2606485.3717 | 1236490.4467 | 2606477.8921 | 1236485.9216
33 | 2606493.4401 | 1236494.6697 | 2606485.5669 | 1236490.5489
34 | 2606493.4401 | 1236494.6697 | 2606497.4424 | 1236496.7645
35 | 2606497.4424 | 1236496.7645 | 2606505.776 | 1236501.1263
36 | 2606517.0025 | 1236507.0022 | 2606505.776 | 1236501.1263
37 | 2606517.0025 | 1236507.0022 | 2606518.3787 | 1236507.7931
38 | 2606517.0025 | 1236507.0022 | 2606509.3965 | 1236519.5679
39 | 2606539.3175 | 1236504.5583 | 2606526.9457 | 1236512.7276 | 2606518.3787 | 1236507.7931
40 | 2606518.3787 | 1236507.7931 | 2606530.0198 | 1236499.5559
41 | 2606495.9388 | 1236541.8006 | 2606509.3965 | 1236519.5679
42 | 2606453.923 | 1236549.4451 | 2606447.2374 | 1236558.5592
43 | 2606468.9801 | 1236535.7456 | 2606457.0005 | 1236545.2496 | 2606453.923 | 1236549.4451
44 | 2606447.2374 | 1236558.5592 | 2606425.6998 | 1236587.9206
45 | 2606468.9801 | 1236535.7456 | 2606495.9388 | 1236541.8006
46 | 2606468.9801 | 1236535.7456 | 2606436.1534 | 1236523.9052
47 | 2606495.9388 | 1236541.8006 | 2606525.1952 | 1236549.9929
48 | 2606495.9388 | 1236541.8006 | 2606490.8153 | 1236550.0223 | 2606483.9558 | 1236559.8654
49 | 2606436.1534 | 1236523.9052 | 2606434.4647 | 1236523.296
50 | 2606525.1952 | 1236549.9929 | 2606528.2704 | 1236550.7294
51 | 2606483.9558 | 1236559.8654 | 2606479.7986 | 1236565.8306
52 | 2606434.4647 | 1236523.296 | 2606427.7387 | 1236520.87
53 | 2606543.2429 | 1236554.3152 | 2606528.2704 | 1236550.7294
54 | 2606473.0445 | 1236575.5224 | 2606479.7986 | 1236565.8306
55 | 2606414.0775 | 1236514.3968 | 2606427.7387 | 1236520.87 | 2606427.7387 | 1236520.87
56 | 2606539.3175 | 1236504.5583 | 2606545.1959 | 1236498.0163 | 2606554.1169 | 1236491.9896
57 | 2606530.0198 | 1236499.5559 | 2606534.7415 | 1236496.2149 | 2606538.6297 | 1236491.3196
58 | 2606371.1145 | 1236593.071 | 2606358.2804 | 1236585.1185
59 | 2606354.8345 | 1236582.9833 | 2606358.2804 | 1236585.1185
60 | 2606354.8345 | 1236582.9833 | 2606338.7707 | 1236573.0296
61 | 2606338.7707 | 1236573.0296 | 2606335.4635 | 1236570.9803 | 2606320.9023 | 1236560.6253 | 2606313.4862 | 1236554.1059
62 | 2606321.4312 | 1236719.3228 | 2606335.5194 | 1236704.3285 | 2606343.1103 | 1236695.2574
63 | 2606321.4312 | 1236719.3228 | 2606316.2793 | 1236711.8128 | 2606302.7747 | 1236675.4987 | 2606301.2933 | 1236672.3288
64 | 2606349.3975 | 1236687.7442 | 2606343.1103 | 1236695.2574
65 | 2606298.2976 | 1236665.9184 | 2606301.2933 | 1236672.3288
66 | 2606448.6232 | 1236700.1637 | 2606442.3272 | 1236711.3927
67 | 2606457.9417 | 1236683.5442 | 2606448.6232 | 1236700.1637
68 | 2606349.3975 | 1236687.7442 | 2606344.8622 | 1236683.748 | 2606339.847 | 1236676.2335
69 | 2606571.0525 | 1236563.9626 | 2606579.0131 | 1236555.9442 | 2606587.3979 | 1236547.5038 | 2606582.2034 | 1236544.4963
70 | 2606582.2034 | 1236544.4963 | 2606587.3979 | 1236547.5038 | 2606597.7872 | 1236553.3076
71 | 2606582.2034 | 1236544.4963 | 2606587.9615 | 1236533.6016
72 | 2606571.0525 | 1236563.9626 | 2606557.9155 | 1236579.4742
73 | 2606571.0525 | 1236563.9626 | 2606565.1435 | 1236563.9005 | 2606543.2429 | 1236554.3152
74 | 2606597.7872 | 1236553.3076 | 2606609.5444 | 1236535.9135
75 | 2606597.7872 | 1236553.3076 | 2606612.2032 | 1236561.682
76 | 2606589.377 | 1236530.9234 | 2606587.9615 | 1236533.6016
77 | 2606565.4978 | 1236461.4606 | 2606547.72 | 1236479.8746 | 2606538.6297 | 1236491.3196
78 | 2606457.9417 | 1236683.5442 | 2606461.61 | 1236677.0018 | 2606463.0022 | 1236675.0212
79 | 2606475.151 | 1236657.7379 | 2606463.0022 | 1236675.0212
80 | 2606475.151 | 1236657.7379 | 2606482.2479 | 1236648.1319
81 | 2606475.151 | 1236657.7379 | 2606486.2063 | 1236663.1976 | 2606505.8869 | 1236669.5668
82 | 2606504.1831 | 1236623.4696 | 2606492.0172 | 1236634.9088 | 2606482.2479 | 1236648.1319
83 | 2606513.7817 | 1236672.1218 | 2606505.8869 | 1236669.5668
84 | 2606504.1831 | 1236623.4696 | 2606504.5364 | 1236623.1374 | 2606507.0826 | 1236620.7528
85 | 2606513.7817 | 1236672.1218 | 2606573.3556 | 1236691.4008
86 | 2606513.7817 | 1236672.1218 | 2606524.6196 | 1236647.4783
87 | 2606601.5068 | 1236397.8056 | 2606622.2148 | 1236357.4619
88 | 2606601.5068 | 1236397.8056 | 2606627.8802 | 1236424.006
89 | 2606611.3344 | 1236489.3784 | 2606627.8802 | 1236424.006
90 | 2606557.9155 | 1236579.4742 | 2606556.86 | 1236580.7205
91 | 2606629.1962 | 1236571.5534 | 2606612.2032 | 1236561.682
92 | 2606589.377 | 1236530.9234 | 2606607.887 | 1236495.9012
93 | 2606514.2003 | 1236614.0868 | 2606507.0826 | 1236620.7528
94 | 2606596.2844 | 1236702.1303 | 2606579.0365 | 1236693.2393 | 2606573.3556 | 1236691.4008
95 | 2606536.5326 | 1236637.0474 | 2606527.5098 | 1236640.9066 | 2606524.6196 | 1236647.4783
96 | 2606301.2953 | 1236593.3876 | 2606308.8739 | 1236600.618
97 | 2606301.2953 | 1236593.3876 | 2606291.9965 | 1236584.5161
98 | 2606308.8739 | 1236600.618 | 2606316.7231 | 1236608.1065
99 | 2606332.2039 | 1236622.4256 | 2606324.8768 | 1236615.8855 | 2606316.7231 | 1236608.1065
100 | 2606343.5369 | 1236634.8612 | 2606342.1486 | 1236631.302 | 2606332.2039 | 1236622.4256
101 | 2606343.5369 | 1236634.8612 | 2606354.2854 | 1236637.6032
102 | 2606343.5369 | 1236634.8612 | 2606331.9929 | 1236633.4482 | 2606321.9605 | 1236633.5043 | 2606302.2633 | 1236636.4743 | 2606284.6851 | 1236639.0908 | 2606277.0091 | 1236640.4116
103 | 2606307.5848 | 1236490.0348 | 2606310.0069 | 1236496.3079 | 2606315.4901 | 1236512.7014 | 2606316.333 | 1236516.9716 | 2606314.5053 | 1236521.0722 | 2606313.2169 | 1236523.161
104 | 2606307.5848 | 1236490.0348 | 2606309.2199 | 1236489.2472 | 2606315.5172 | 1236487.0302 | 2606321.2384 | 1236485.7799 | 2606328.1847 | 1236485.1535 | 2606336.0765 | 1236484.8506 | 2606343.6344 | 1236485.3589 | 2606351.6377 | 1236486.8794 | 2606359.9726 | 1236489.6788 | 2606367.4904 | 1236492.3217 | 2606370.8916 | 1236493.9333
105 | 2606313.2169 | 1236523.161 | 2606327.8279 | 1236536.5512 | 2606327.1686 | 1236537.3602
106 | 2606400.9753 | 1236508.1883 | 2606370.8916 | 1236493.9333
107 | 2606400.9753 | 1236508.1883 | 2606414.0775 | 1236514.3968
108 | 2606331.0905 | 1236663.1135 | 2606339.847 | 1236676.2335
109 | 2606614.0232 | 1236713.9776 | 2606605.3402 | 1236708.1784
110 | 2606621.6791 | 1236719.0908 | 2606614.0232 | 1236713.9776
111 | 2606596.2844 | 1236702.1303 | 2606605.3402 | 1236708.1784
112 | 2606621.6791 | 1236719.0908 | 2606628.2991 | 1236703.4727
113 | 2606591.0846 | 1236710.9077 | 2606596.2844 | 1236702.1303
114 | 2606591.0846 | 1236710.9077 | 2606580.9012 | 1236717.7007 | 2606527.9978 | 1236734.7978
115 | 2606632.324 | 1236593.8697 | 2606627.2358 | 1236599.6573 | 2606611.4703 | 1236611.6584 | 2606607.7721 | 1236617.0909 | 2606602.145 | 1236636.755
116 | 2606633.9931 | 1236591.9712 | 2606632.324 | 1236593.8697
117 | 2606600.4726 | 1236642.5994 | 2606602.145 | 1236636.755
118 | 2606642.5513 | 1236645.6246 | 2606647.0414 | 1236628.7637 | 2606647.2445 | 1236622.9492 | 2606644.524 | 1236620.0333 | 2606638.3016 | 1236616.1574 | 2606633.9062 | 1236608.9593 | 2606633.9931 | 1236591.9712
119 | 2606629.1962 | 1236571.5534 | 2606641.3244 | 1236578.3599 | 2606633.9931 | 1236591.9712
120 | 2606598.7871 | 1236648.4891 | 2606600.4726 | 1236642.5994
121 | 2606536.5326 | 1236637.0474 | 2606539.3329 | 1236646.4979
122 | 2606514.2003 | 1236614.0868 | 2606518.843 | 1236609.7336 | 2606522.7638 | 1236607.599
123 | 2606611.3344 | 1236489.3784 | 2606607.887 | 1236495.9012

## bus_geodata
| x | y | coords
0 | 2606419.4507 | 1236643.0804
1 | 2606428.653 | 1236627.8475
2 | 2606405.312 | 1236663.5332
3 | 2606438.8785 | 1236634.4207
4 | 2606406.045 | 1236614.7153
5 | 2606390.1971 | 1236682.4916
6 | 2606395.6774 | 1236655.4962
7 | 2606445.3508 | 1236638.5814
8 | 2606453.3497 | 1236599.3624
9 | 2606462.0398 | 1236589.3393
10 | 2606391.3611 | 1236605.6165
11 | 2606414.5145 | 1236603.1691
12 | 2606393.491 | 1236653.6723
13 | 2606459.7301 | 1236647.8248
14 | 2606462.856 | 1236588.3979
15 | 2606383.0125 | 1236644.9314
16 | 2606350.5258 | 1236686.307
17 | 2606375.0598 | 1236642.9027
18 | 2606374.3228 | 1236595.059
19 | 2606423.3321 | 1236591.1484
20 | 2606431.7915 | 1236450.2518
21 | 2606427.0633 | 1236446.1614
22 | 2606457.9798 | 1236471.9281
23 | 2606418.7421 | 1236438.9627
24 | 2606467.0208 | 1236458.7809
25 | 2606473.574 | 1236483.3092
26 | 2606474.8634 | 1236447.3762
27 | 2606477.8921 | 1236485.9216
28 | 2606484.2072 | 1236433.7886
29 | 2606485.5669 | 1236490.5489
30 | 2606493.4401 | 1236494.6697
31 | 2606497.4424 | 1236496.7645
32 | 2606505.776 | 1236501.1263
33 | 2606517.0025 | 1236507.0022
34 | 2606518.3787 | 1236507.7931
35 | 2606509.3965 | 1236519.5679
36 | 2606453.9229 | 1236549.4451
37 | 2606447.2374 | 1236558.5592
38 | 2606468.9801 | 1236535.7456
39 | 2606425.6998 | 1236587.9206
40 | 2606495.9388 | 1236541.8006
41 | 2606436.1534 | 1236523.9052
42 | 2606525.1952 | 1236549.9929
43 | 2606483.9558 | 1236559.8654
44 | 2606434.4647 | 1236523.296
45 | 2606528.2704 | 1236550.7294
46 | 2606479.7986 | 1236565.8306
47 | 2606427.7387 | 1236520.87
48 | 2606539.3175 | 1236504.5583
49 | 2606530.0198 | 1236499.5559
50 | 2606371.1145 | 1236593.071
51 | 2606358.2804 | 1236585.1185
52 | 2606354.8345 | 1236582.9833
53 | 2606338.7707 | 1236573.0296
54 | 2606321.4312 | 1236719.3228
55 | 2606343.1103 | 1236695.2574
56 | 2606301.2933 | 1236672.3288
57 | 2606442.3272 | 1236711.3927
58 | 2606448.6232 | 1236700.1637
59 | 2606349.3975 | 1236687.7442
60 | 2606298.2976 | 1236665.9184
61 | 2606554.1169 | 1236491.9896
62 | 2606582.2034 | 1236544.4963
63 | 2606571.0525 | 1236563.9626
64 | 2606597.7872 | 1236553.3076
65 | 2606587.9615 | 1236533.6016
66 | 2606543.2429 | 1236554.3152
67 | 2606538.6297 | 1236491.3196
68 | 2606473.0445 | 1236575.5224
69 | 2606313.4862 | 1236554.1059
70 | 2606457.9417 | 1236683.5442
71 | 2606463.0022 | 1236675.0212
72 | 2606475.151 | 1236657.7379
73 | 2606482.2479 | 1236648.1319
74 | 2606505.8869 | 1236669.5668
75 | 2606504.1831 | 1236623.4696
76 | 2606513.7817 | 1236672.1218
77 | 2606565.4978 | 1236461.4606
78 | 2606622.2148 | 1236357.4619
79 | 2606601.5068 | 1236397.8056
80 | 2606627.8802 | 1236424.006
81 | 2606557.9155 | 1236579.4742
82 | 2606609.5444 | 1236535.9135
83 | 2606612.2032 | 1236561.682
84 | 2606589.377 | 1236530.9234
85 | 2606507.0826 | 1236620.7528
86 | 2606573.3556 | 1236691.4008
87 | 2606524.6196 | 1236647.4783
88 | 2606301.2953 | 1236593.3876
89 | 2606308.8739 | 1236600.618
90 | 2606291.9965 | 1236584.5161
91 | 2606316.723 | 1236608.1065
92 | 2606332.2039 | 1236622.4255
93 | 2606343.5369 | 1236634.8612
94 | 2606307.5848 | 1236490.0348
95 | 2606313.2169 | 1236523.161
96 | 2606370.8916 | 1236493.9333
97 | 2606354.2855 | 1236637.6032
98 | 2606277.0091 | 1236640.4116
99 | 2606400.9753 | 1236508.1883
100 | 2606414.0775 | 1236514.3968
101 | 2606327.1686 | 1236537.3602
102 | 2606331.0905 | 1236663.1135
103 | 2606339.847 | 1236676.2335
104 | 2606614.0232 | 1236713.9776
105 | 2606605.3402 | 1236708.1784
106 | 2606621.6791 | 1236719.0908
107 | 2606596.2844 | 1236702.1303
108 | 2606628.2991 | 1236703.4727
109 | 2606591.0846 | 1236710.9077
110 | 2606527.9978 | 1236734.7978
111 | 2606632.324 | 1236593.8697
112 | 2606602.145 | 1236636.755
113 | 2606633.9931 | 1236591.9712
114 | 2606600.4726 | 1236642.5994
115 | 2606642.5513 | 1236645.6246
116 | 2606629.1961 | 1236571.5534
117 | 2606598.7871 | 1236648.4891
118 | 2606539.3329 | 1236646.4979
119 | 2606536.5326 | 1236637.0474
120 | 2606514.2003 | 1236614.0868
121 | 2606522.7638 | 1236607.599
122 | 2606556.86 | 1236580.7205
123 | 2606607.887 | 1236495.9012
124 | 2606611.3344 | 1236489.3784
125 | 2606428.653 | 1236627.8475

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97712 | -0.16042 | 0.0041206 | 0.0010327
1 | 0.97794 | -0.15453 | 0 | 0
2 | 0.97611 | -0.1676 | 0.0024025 | 0.00060212
3 | 0.97702 | -0.16109 | 0.0019143 | 0.00047977
4 | 0.98112 | -0.13192 | 0 | 0
5 | 0.97603 | -0.16819 | 0.002307 | 0.00057819
6 | 0.9757 | -0.1706 | 0.00094988 | 0.00023806
7 | 0.97646 | -0.16509 | 0.0018434 | 0.00046199
8 | 0.99997 | -0.00018331 | 0.0011457 | 0.00028715
9 | 1 | -3.153e-05 | 0.0013884 | 0.00034797
10 | 0.98089 | -0.13355 | 0.0023789 | 0.00059622
11 | 0.98305 | -0.11823 | 0.0021199 | 0.00053128
12 | 0.9756 | -0.17126 | 0.0026815 | 0.00067204
13 | 0.97526 | -0.17367 | 0.0023095 | 0.00057881
14 | 1 | 0 | -0.20477 | -0.05157
15 | 0.97522 | -0.17401 | 0 | 0
16 | 0.97455 | -0.17882 | 0.0017827 | 0.0004468
17 | 0.9751 | -0.17491 | 0.0020822 | 0.00052184
18 | 0.9807 | -0.13494 | 0.001368 | 0.00034286
19 | 0.98408 | -0.11096 | 0.0017912 | 0.00044893
20 | 0.98788 | -0.084587 | 0.0017147 | 0.00042974
21 | 0.98782 | -0.08499 | 0.0050981 | 0.0012777
22 | 0.98827 | -0.081802 | 0 | 0
23 | 0.9878 | -0.085125 | 0.0011981 | 0.00030028
24 | 0.98818 | -0.082485 | 0.00078284 | 0.0001962
25 | 0.98861 | -0.079393 | 0.0027525 | 0.00068985
26 | 0.98811 | -0.082967 | 0.0013096 | 0.00032821
27 | 0.98872 | -0.078622 | 0.0014551 | 0.00036467
28 | 0.98806 | -0.08332 | 0.0020945 | 0.00052492
29 | 0.98893 | -0.07712 | 0.0019976 | 0.00050064
30 | 0.98917 | -0.075451 | 0.00027094 | 6.7903e-05
31 | 0.98929 | -0.07459 | 0.0054684 | 0.0013705
32 | 0.98962 | -0.072273 | 0.00026839 | 6.7264e-05
33 | 0.99007 | -0.069121 | 0 | 0
34 | 0.99006 | -0.06914 | 0 | 0
35 | 0.99061 | -0.065295 | 0.0091158 | 0.0022846
36 | 0.98787 | -0.08433 | 0.0011028 | 0.00027638
37 | 0.98702 | -0.090254 | 0.0023353 | 0.00058527
38 | 0.98942 | -0.073497 | 0 | 0
39 | 0.98436 | -0.10897 | 0.0037508 | 0.00094003
40 | 0.99191 | -0.056131 | 0 | 0
41 | 0.98839 | -0.08077 | 0.00098289 | 0.00024634
42 | 0.99046 | -0.06633 | 0 | 0
43 | 0.99492 | -0.0351 | 0.0028684 | 0.0007189
44 | 0.98834 | -0.081127 | 0.0030627 | 0.00076758
45 | 0.99031 | -0.067396 | 0.0018501 | 0.00046367
46 | 0.99595 | -0.027971 | 0.0022087 | 0.00055356
47 | 0.98817 | -0.082323 | 0.0023809 | 0.00059671
48 | 0.99005 | -0.069213 | 0 | 0
49 | 0.99005 | -0.069267 | 0.0001036 | 2.5966e-05
50 | 0.98067 | -0.13515 | 0.00090736 | 0.00022741
51 | 0.98057 | -0.13584 | 0.0008263 | 0.00020709
52 | 0.98055 | -0.136 | 0.0010638 | 0.00026662
53 | 0.98048 | -0.13649 | 0.0012524 | 0.00031388
54 | 0.97439 | -0.17997 | 0 | 0
55 | 0.97449 | -0.1793 | 0.0013677 | 0.00034279
56 | 0.97425 | -0.18103 | 0.00096485 | 0.00024181
57 | 0.97371 | -0.18478 | 0.0010971 | 0.00027495
58 | 0.97373 | -0.18463 | 0.0011904 | 0.00029835
59 | 0.97453 | -0.17896 | 0 | 0
60 | 0.97424 | -0.18111 | 0.001 | 0.00025063
61 | 0.99004 | -0.06927 | 0.00028756 | 7.2069e-05
62 | 0.98726 | -0.088953 | 0 | 0
63 | 0.98827 | -0.081792 | 0 | 0
64 | 0.98691 | -0.091468 | 0 | 0
65 | 0.98708 | -0.090248 | 0.0022983 | 0.00057601
66 | 0.98961 | -0.0723 | 0 | 0
67 | 0.99003 | -0.069361 | 7.1354e-05 | 1.7883e-05
68 | 0.99764 | -0.01629 | 0.0011867 | 0.00029741
69 | 0.98042 | -0.13691 | 0.0012772 | 0.00032011
70 | 0.9738 | -0.18417 | 0.0016465 | 0.00041265
71 | 0.97385 | -0.18376 | 0.0020087 | 0.00050343
72 | 0.97404 | -0.18244 | 0 | 0
73 | 0.97385 | -0.18375 | 0.0017364 | 0.00043518
74 | 0.97262 | -0.19259 | 0.0019953 | 0.00050008
75 | 0.97343 | -0.18678 | 0.0044873 | 0.0011246
76 | 0.97229 | -0.19497 | 0 | 0
77 | 0.98999 | -0.069647 | 0.00069577 | 0.00017438
78 | 0.98657 | -0.093895 | 0.0014355 | 0.00035978
79 | 0.98666 | -0.093226 | 0 | 0
80 | 0.98674 | -0.092677 | 0.00014254 | 3.5723e-05
81 | 0.98806 | -0.083309 | 0.0040955 | 0.0010264
82 | 0.98685 | -0.091907 | 0.0020414 | 0.00051163
83 | 0.98663 | -0.093462 | 0.0023963 | 0.00060058
84 | 0.98704 | -0.090495 | 0.0056075 | 0.0014054
85 | 0.97341 | -0.18696 | 0.0022667 | 0.0005681
86 | 0.97108 | -0.2037 | 0.0051359 | 0.0012872
87 | 0.97174 | -0.19895 | 0.001267 | 0.00031753
88 | 0.9743 | -0.18064 | 0.0011898 | 0.00029819
89 | 0.97434 | -0.18038 | 0.0014708 | 0.00036862
90 | 0.97428 | -0.18079 | 0.0011345 | 0.00028432
91 | 0.9744 | -0.17995 | 0.0013939 | 0.00034935
92 | 0.97456 | -0.1788 | 0.00096125 | 0.00024091
93 | 0.97471 | -0.17769 | 0 | 0
94 | 0.98671 | -0.092682 | 0 | 0
95 | 0.98641 | -0.094794 | 0 | 0
96 | 0.98726 | -0.088764 | 0.0015386 | 0.00038561
97 | 0.97483 | -0.17681 | 0.00088673 | 0.00022223
98 | 0.97458 | -0.17865 | 0.0013663 | 0.00034242
99 | 0.98762 | -0.086247 | 0.0044896 | 0.0011252
100 | 0.98787 | -0.084486 | 0.0021144 | 0.00052991
101 | 0.98624 | -0.096043 | 0.0058329 | 0.0014619
102 | 0.97442 | -0.17981 | 0.0017271 | 0.00043285
103 | 0.97445 | -0.17952 | 0.0018575 | 0.00046554
104 | 0.97064 | -0.20693 | 0.0014452 | 0.00036221
105 | 0.97068 | -0.20659 | 0.0031043 | 0.000778
106 | 0.97061 | -0.2071 | 0 | 0
107 | 0.97078 | -0.20586 | 0 | 0
108 | 0.97057 | -0.2074 | 0.0016976 | 0.00042546
109 | 0.97076 | -0.20606 | 0 | 0
110 | 0.97058 | -0.20735 | 0.0017883 | 0.00044818
111 | 0.98594 | -0.098307 | 0.00081783 | 0.00020497
112 | 0.98545 | -0.10183 | 0.0018952 | 0.00047497
113 | 0.98597 | -0.098122 | 0 | 0
114 | 0.98541 | -0.1021 | 0.0020347 | 0.00050994
115 | 0.98578 | -0.099453 | 0.0021582 | 0.0005409
116 | 0.98636 | -0.09533 | 0 | 0
117 | 0.98539 | -0.10225 | 0.002347 | 0.00058821
118 | 0.97124 | -0.20257 | 0.012726 | 0.0031893
119 | 0.97142 | -0.20124 | 0 | 0
120 | 0.97338 | -0.18715 | 0 | 0
121 | 0.97335 | -0.18737 | 0.0019267 | 0.00048287
122 | 0.98805 | -0.083362 | 0.003202 | 0.00080249
123 | 0.98691 | -0.09145 | 0.00064523 | 0.00016171
124 | 0.98689 | -0.091579 | 0.00011189 | 2.8043e-05
125 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.031707 | -0.007949 | 0.031733 | 0.0079587 | 2.5892e-05 | 9.7355e-06 | 0.048286 | 0.048286 | 0.048286 | 0.97712 | -0.16042 | 0.97794 | -0.15453 | 17.8838
1 | 0.027586 | 0.0069163 | -0.027559 | -0.006906 | 2.7402e-05 | 1.0228e-05 | 0.042011 | 0.042011 | 0.042011 | 0.97712 | -0.16042 | 0.97611 | -0.1676 | 15.5597
2 | 0.051865 | 0.01303 | -0.051818 | -0.013012 | 4.7254e-05 | 1.8022e-05 | 0.078928 | 0.078928 | 0.078928 | 0.97794 | -0.15453 | 0.97702 | -0.16109 | 29.2326
3 | -0.083598 | -0.020988 | 0.083861 | 0.021089 | 0.00026346 | 0.000101 | 0.12721 | 0.12721 | 0.12721 | 0.97794 | -0.15453 | 0.98112 | -0.13192 | 47.1164
4 | 0.0023072 | 0.00057796 | -0.002307 | -0.00057819 | 1.8715e-07 | -2.3107e-07 | 0.003517 | 0.0035172 | 0.0035172 | 0.97611 | -0.1676 | 0.97603 | -0.16819 | 1.3027
5 | 0.022849 | 0.005726 | -0.02284 | -0.0057225 | 9.4987e-06 | 3.4966e-06 | 0.034832 | 0.034832 | 0.034832 | 0.97611 | -0.1676 | 0.9757 | -0.1706 | 12.9007
6 | 0.049903 | 0.012532 | -0.049876 | -0.012521 | 2.7741e-05 | 1.0573e-05 | 0.076013 | 0.076013 | 0.076013 | 0.97702 | -0.16109 | 0.97646 | -0.16509 | 28.1528
7 | 0.0090784 | 0.0022744 | -0.0090763 | -0.0022739 | 2.0434e-06 | 5.6783e-07 | 0.013768 | 0.013768 | 0.013768 | 0.98112 | -0.13192 | 0.98089 | -0.13355 | 5.0994
8 | -0.092939 | -0.023364 | 0.093117 | 0.023432 | 0.0001776 | 6.8126e-05 | 0.14098 | 0.14098 | 0.14098 | 0.98112 | -0.13192 | 0.98305 | -0.11823 | 52.2157
9 | 0.02189 | 0.0054844 | -0.021888 | -0.0054837 | 1.98e-06 | 7.2598e-07 | 0.033383 | 0.033383 | 0.033383 | 0.9757 | -0.1706 | 0.9756 | -0.17126 | 12.3641
10 | 0.048032 | 0.012059 | -0.047975 | -0.012038 | 5.716e-05 | 2.1771e-05 | 0.073204 | 0.073204 | 0.073204 | 0.97646 | -0.16509 | 0.97526 | -0.17367 | 27.1124
11 | -0.0011457 | -0.00028715 | 0.0011458 | 0.00028699 | 2.4061e-08 | -1.6478e-07 | 0.0017049 | 0.0017049 | 0.0017049 | 0.99997 | -0.00018331 | 1 | -3.153e-05 | 0.63146
12 | -0.0025342 | -0.00063496 | 0.0025342 | 0.00063495 | 1.1055e-08 | -1.2094e-08 | 0.0037709 | 0.0037709 | 0.0037709 | 1 | -3.153e-05 | 1 | 0 | 1.3966
13 | 0.0066974 | 0.0016776 | -0.0066961 | -0.0016774 | 1.291e-06 | 2.4358e-07 | 0.01016 | 0.01016 | 0.01016 | 0.98089 | -0.13355 | 0.9807 | -0.13494 | 3.7629
14 | -0.095237 | -0.023963 | 0.095334 | 0.024 | 9.6705e-05 | 3.6816e-05 | 0.14419 | 0.14419 | 0.14419 | 0.98305 | -0.11823 | 0.98408 | -0.11096 | 26.7021
15 | 0.019206 | 0.0048116 | -0.019199 | -0.004809 | 7.3066e-06 | 2.6399e-06 | 0.029293 | 0.029293 | 0.029293 | 0.9756 | -0.17126 | 0.97522 | -0.17401 | 10.8494
16 | 0.045666 | 0.011459 | -0.04561 | -0.011438 | 5.5541e-05 | 2.1134e-05 | 0.06968 | 0.06968 | 0.06968 | 0.97526 | -0.17367 | 0.97404 | -0.18244 | 25.8074
17 | 0.20144 | 0.050935 | -0.20098 | -0.050758 | 0.00046138 | 0.00017702 | 0.2999 | 0.2999 | 0.2999 | 1 | 0 | 0.99764 | -0.01629 | 55.5376
18 | 0.0087069 | 0.0021808 | -0.0087011 | -0.0021792 | 5.7933e-06 | 1.5723e-06 | 0.013285 | 0.013285 | 0.013285 | 0.97522 | -0.17401 | 0.97455 | -0.17882 | 4.9203
19 | 0.010492 | 0.0026282 | -0.010491 | -0.0026278 | 1.3125e-06 | 4.0242e-07 | 0.016009 | 0.016009 | 0.016009 | 0.97522 | -0.17401 | 0.9751 | -0.17491 | 5.9291
20 | 0.0069184 | 0.0017324 | -0.0069182 | -0.0017324 | 1.2721e-07 | 2.6162e-08 | 0.010563 | 0.010563 | 0.010563 | 0.97455 | -0.17882 | 0.97453 | -0.17896 | 3.9122
21 | 0.0084086 | 0.002106 | -0.0084064 | -0.0021054 | 2.2026e-06 | 5.798e-07 | 0.012831 | 0.012831 | 0.012831 | 0.9751 | -0.17491 | 0.97483 | -0.17681 | 4.7523
22 | 0.005328 | 0.0013345 | -0.0053279 | -0.0013345 | 1.5391e-07 | 1.1576e-08 | 0.008084 | 0.008084 | 0.008084 | 0.9807 | -0.13494 | 0.98067 | -0.13515 | 2.9941
23 | -0.097125 | -0.024449 | 0.097152 | 0.024459 | 2.6952e-05 | 1.0264e-05 | 0.1469 | 0.1469 | 0.1469 | 0.98408 | -0.11096 | 0.98436 | -0.10897 | 27.2036
24 | 0.0062965 | 0.0015779 | -0.0062962 | -0.0015778 | 3.5092e-07 | 5.4929e-08 | 0.0094842 | 0.0094843 | 0.0094843 | 0.98788 | -0.084587 | 0.98782 | -0.08499 | 3.5127
25 | -0.0080112 | -0.0020076 | 0.0080143 | 0.0020084 | 3.0891e-06 | 7.5265e-07 | 0.012067 | 0.012067 | 0.012067 | 0.98788 | -0.084587 | 0.98827 | -0.081802 | 4.4693
26 | 0.0011981 | 0.00030014 | -0.0011981 | -0.00030028 | 2.2364e-08 | -1.3225e-07 | 0.0018048 | 0.0018048 | 0.0018048 | 0.98782 | -0.08499 | 0.9878 | -0.085125 | 0.66845
27 | 0.0041876 | 0.001049 | -0.0041872 | -0.0010491 | 3.958e-07 | -5.2198e-08 | 0.006305 | 0.006305 | 0.006305 | 0.98827 | -0.081802 | 0.98818 | -0.082485 | 2.3352
28 | -0.012202 | -0.0030574 | 0.012206 | 0.0030587 | 4.0683e-06 | 1.3171e-06 | 0.018372 | 0.018372 | 0.018372 | 0.98827 | -0.081802 | 0.98861 | -0.079393 | 6.8044
29 | 0.0034044 | 0.00085287 | -0.0034041 | -0.00085296 | 2.2696e-07 | -9.0011e-08 | 0.0051262 | 0.0051263 | 0.0051263 | 0.98818 | -0.082485 | 0.98811 | -0.082967 | 1.8986
30 | -0.014959 | -0.0037486 | 0.01496 | 0.0037491 | 1.5964e-06 | 5.4928e-07 | 0.022515 | 0.022515 | 0.022515 | 0.98861 | -0.079393 | 0.98872 | -0.078622 | 8.3388
31 | 0.0020946 | 0.00052475 | -0.0020945 | -0.00052492 | 1.0238e-07 | -1.7184e-07 | 0.0031542 | 0.0031543 | 0.0031543 | 0.98811 | -0.082967 | 0.98806 | -0.08332 | 1.1682
32 | -0.016415 | -0.0041138 | 0.016419 | 0.004115 | 3.4131e-06 | 1.1978e-06 | 0.024705 | 0.024705 | 0.024705 | 0.98872 | -0.078622 | 0.98893 | -0.07712 | 9.1498
33 | -0.018416 | -0.0046156 | 0.01842 | 0.0046171 | 4.2578e-06 | 1.5236e-06 | 0.02771 | 0.02771 | 0.02771 | 0.98893 | -0.07712 | 0.98917 | -0.075451 | 10.263
34 | -0.018691 | -0.0046851 | 0.018694 | 0.0046858 | 2.2286e-06 | 7.9916e-07 | 0.028118 | 0.028118 | 0.028118 | 0.98917 | -0.075451 | 0.98929 | -0.07459 | 10.414
35 | -0.024162 | -0.0060564 | 0.02417 | 0.0060592 | 7.7523e-06 | 2.8609e-06 | 0.036343 | 0.036343 | 0.036343 | 0.98929 | -0.07459 | 0.98962 | -0.072273 | 13.4603
36 | -0.024438 | -0.0061265 | 0.024449 | 0.0061304 | 1.0677e-05 | 3.9435e-06 | 0.036746 | 0.036746 | 0.036746 | 0.98962 | -0.072273 | 0.99007 | -0.069121 | 13.6098
37 | 0.0011584 | 0.00028887 | -0.0011584 | -0.00028889 | 2.994e-09 | -1.9218e-08 | 0.0017404 | 0.0017404 | 0.0017404 | 0.99007 | -0.069121 | 0.99006 | -0.06914 | 0.64461
38 | -0.025607 | -0.0064193 | 0.025621 | 0.0064243 | 1.3576e-05 | 5.0326e-06 | 0.038487 | 0.038487 | 0.038487 | 0.99007 | -0.069121 | 0.99061 | -0.065295 | 14.2543
39 | 0.00028757 | 7.1502e-05 | -0.00028756 | -7.1819e-05 | 2.8785e-09 | -3.1668e-07 | 0.000432 | 0.00043211 | 0.00043211 | 0.99006 | -0.06914 | 0.99005 | -0.069213 | 0.16004
40 | 0.00087079 | 0.00021739 | -0.00087077 | -0.00021757 | 1.5236e-08 | -1.7753e-07 | 0.0013084 | 0.0013085 | 0.0013085 | 0.99006 | -0.06914 | 0.99005 | -0.069267 | 0.48463
41 | -0.034737 | -0.008709 | 0.034781 | 0.0087256 | 4.4154e-05 | 1.6647e-05 | 0.05218 | 0.05218 | 0.05218 | 0.99061 | -0.065295 | 0.99191 | -0.056131 | 19.3259
42 | 0.10359 | 0.026118 | -0.1035 | -0.026085 | 8.5922e-05 | 3.2758e-05 | 0.15609 | 0.15609 | 0.15609 | 0.98787 | -0.08433 | 0.98702 | -0.090254 | 28.9055
43 | -0.10469 | -0.026395 | 0.10485 | 0.026455 | 0.00015913 | 6.0677e-05 | 0.15775 | 0.15775 | 0.15775 | 0.98787 | -0.08433 | 0.98942 | -0.073497 | 29.2131
44 | 0.10117 | 0.0255 | -0.1009 | -0.025399 | 0.00026446 | 0.00010079 | 0.15257 | 0.15257 | 0.15257 | 0.98702 | -0.090254 | 0.98436 | -0.10897 | 28.2536
45 | -0.12529 | -0.031581 | 0.1256 | 0.031698 | 0.00030544 | 0.00011677 | 0.18849 | 0.18849 | 0.18849 | 0.98942 | -0.073497 | 0.99191 | -0.056131 | 34.9063
46 | 0.020442 | 0.0051256 | -0.020421 | -0.0051181 | 2.0582e-05 | 7.4685e-06 | 0.030744 | 0.030744 | 0.030744 | 0.98942 | -0.073497 | 0.98839 | -0.08077 | 11.3867
47 | 0.03324 | 0.0083448 | -0.033193 | -0.0083271 | 4.7021e-05 | 1.7694e-05 | 0.04987 | 0.04987 | 0.04987 | 0.99191 | -0.056131 | 0.99046 | -0.06633 | 18.4703
48 | -0.19362 | -0.048768 | 0.19419 | 0.048987 | 0.00057113 | 0.0002191 | 0.29054 | 0.29054 | 0.29054 | 0.99191 | -0.056131 | 0.99492 | -0.0351 | 53.8043
49 | 0.019438 | 0.0048718 | -0.019437 | -0.0048715 | 9.5937e-07 | 3.4598e-07 | 0.029264 | 0.029264 | 0.029264 | 0.98839 | -0.08077 | 0.98834 | -0.081127 | 10.8387
50 | 0.033193 | 0.0083271 | -0.033188 | -0.0083253 | 4.9073e-06 | 1.8467e-06 | 0.04987 | 0.04987 | 0.04987 | 0.99046 | -0.06633 | 0.99031 | -0.067396 | 18.4704
51 | -0.19706 | -0.049706 | 0.19725 | 0.049782 | 0.00019719 | 7.5655e-05 | 0.29483 | 0.29483 | 0.29483 | 0.99492 | -0.0351 | 0.99595 | -0.027971 | 54.5988
52 | 0.016375 | 0.0041039 | -0.016372 | -0.0041029 | 2.7118e-06 | 9.5137e-07 | 0.024653 | 0.024653 | 0.024653 | 0.98834 | -0.081127 | 0.98817 | -0.082323 | 9.1308
53 | 0.031338 | 0.0078616 | -0.031316 | -0.0078536 | 2.1304e-05 | 7.9957e-06 | 0.04709 | 0.04709 | 0.04709 | 0.99031 | -0.067396 | 0.98961 | -0.0723 | 17.4408
54 | -0.19946 | -0.050335 | 0.19979 | 0.050461 | 0.0003276 | 0.00012569 | 0.29813 | 0.29813 | 0.29813 | 0.99595 | -0.027971 | 0.99764 | -0.01629 | 55.2099
55 | 0.013991 | 0.0035062 | -0.013987 | -0.0035048 | 4.187e-06 | 1.4168e-06 | 0.021068 | 0.021068 | 0.021068 | 0.98817 | -0.082323 | 0.98787 | -0.084486 | 7.803
56 | 0.00028756 | 7.1819e-05 | -0.00028756 | -7.2069e-05 | 2.2796e-09 | -2.5067e-07 | 0.00043211 | 0.0004322 | 0.0004322 | 0.99005 | -0.069213 | 0.99004 | -0.06927 | 0.16007
57 | 0.00076717 | 0.0001916 | -0.00076716 | -0.00019175 | 9.9812e-09 | -1.5093e-07 | 0.0011528 | 0.0011529 | 0.0011529 | 0.99005 | -0.069267 | 0.99003 | -0.069361 | 0.42698
58 | 0.0044205 | 0.0011071 | -0.0044201 | -0.0011071 | 4.2384e-07 | -2.7459e-08 | 0.0067072 | 0.0067073 | 0.0067073 | 0.98067 | -0.13515 | 0.98057 | -0.13584 | 2.4842
59 | 0.0035938 | 0.00090005 | -0.0035937 | -0.00090007 | 7.5227e-08 | -2.2201e-08 | 0.0054534 | 0.0054534 | 0.0054534 | 0.98057 | -0.13584 | 0.98055 | -0.136 | 2.0198
60 | 0.0025299 | 0.00063345 | -0.0025297 | -0.00063362 | 1.738e-07 | -1.7151e-07 | 0.003839 | 0.0038391 | 0.0038391 | 0.98055 | -0.136 | 0.98048 | -0.13649 | 1.4219
61 | 0.0012773 | 0.00031974 | -0.0012772 | -0.00032011 | 7.417e-08 | -3.704e-07 | 0.0019384 | 0.0019385 | 0.0019385 | 0.98048 | -0.13649 | 0.98042 | -0.13691 | 0.71797
62 | -0.0019652 | -0.00049183 | 0.0019654 | 0.0004915 | 1.8206e-07 | -3.3362e-07 | 0.0030008 | 0.0030007 | 0.0030008 | 0.97439 | -0.17997 | 0.97449 | -0.1793 | 1.1114
63 | 0.0019652 | 0.00049183 | -0.0019649 | -0.00049236 | 2.8856e-07 | -5.2854e-07 | 0.0030008 | 0.003001 | 0.003001 | 0.97439 | -0.17997 | 0.97425 | -0.18103 | 1.1115
64 | -0.0033331 | -0.00083428 | 0.0033332 | 0.00083422 | 1.5833e-07 | -6.1163e-08 | 0.0050892 | 0.0050891 | 0.0050892 | 0.97449 | -0.1793 | 0.97453 | -0.17896 | 1.8849
65 | 0.001 | 0.00025055 | -0.001 | -0.00025063 | 1.0301e-08 | -8.4146e-08 | 0.0015274 | 0.0015274 | 0.0015274 | 0.97425 | -0.18103 | 0.97424 | -0.18111 | 0.56571
66 | -0.0010971 | -0.00027495 | 0.0010971 | 0.0002748 | 2.2579e-08 | -1.5145e-07 | 0.0016765 | 0.0016765 | 0.0016765 | 0.97371 | -0.18478 | 0.97373 | -0.18463 | 0.62094
67 | -0.0022875 | -0.00057315 | 0.0022877 | 0.00057297 | 1.4528e-07 | -1.8115e-07 | 0.0034957 | 0.0034956 | 0.0034957 | 0.97373 | -0.18463 | 0.9738 | -0.18417 | 1.2947
68 | 0.003585 | 0.00089815 | -0.0035847 | -0.00089823 | 2.8193e-07 | -7.9429e-08 | 0.0054738 | 0.0054739 | 0.0054739 | 0.97453 | -0.17896 | 0.97445 | -0.17952 | 2.0274
69 | -0.023952 | -0.0060001 | 0.023976 | 0.0060089 | 2.3745e-05 | 8.7589e-06 | 0.0361 | 0.0361 | 0.0361 | 0.98726 | -0.088953 | 0.98827 | -0.081792 | 13.3705
70 | 0.013709 | 0.0034351 | -0.013704 | -0.0034335 | 4.7691e-06 | 1.6054e-06 | 0.020662 | 0.020662 | 0.020662 | 0.98726 | -0.088953 | 0.98691 | -0.091468 | 7.6525
71 | 0.010244 | 0.002565 | -0.010242 | -0.0025645 | 1.8328e-06 | 5.474e-07 | 0.015439 | 0.015439 | 0.015439 | 0.98726 | -0.088953 | 0.98708 | -0.090248 | 5.7181
72 | 0.007299 | 0.0018292 | -0.0072975 | -0.0018289 | 1.532e-06 | 3.2882e-07 | 0.01099 | 0.01099 | 0.01099 | 0.98827 | -0.081792 | 0.98806 | -0.083309 | 4.0704
73 | -0.031275 | -0.0078381 | 0.031316 | 0.0078536 | 4.1152e-05 | 1.5446e-05 | 0.04709 | 0.04709 | 0.04709 | 0.98827 | -0.081792 | 0.98961 | -0.0723 | 17.4408
74 | 0.0020415 | 0.00051141 | -0.0020414 | -0.00051163 | 1.2413e-07 | -2.2052e-07 | 0.0030781 | 0.0030782 | 0.0030782 | 0.98691 | -0.091468 | 0.98685 | -0.091907 | 1.1401
75 | 0.011662 | 0.0029221 | -0.011659 | -0.0029211 | 3.2165e-06 | 1.0241e-06 | 0.017584 | 0.017584 | 0.017584 | 0.98691 | -0.091468 | 0.98663 | -0.093462 | 6.5125
76 | 0.0079437 | 0.0019885 | -0.0079435 | -0.0019884 | 2.7103e-07 | 6.5523e-08 | 0.011974 | 0.011974 | 0.011974 | 0.98708 | -0.090248 | 0.98704 | -0.090495 | 4.4349
77 | 0.0006958 | 0.00017387 | -0.00069577 | -0.00017438 | 2.7438e-08 | -5.065e-07 | 0.0010456 | 0.0010458 | 0.0010458 | 0.99003 | -0.069361 | 0.98999 | -0.069647 | 0.38733
78 | -0.0039342 | -0.00098562 | 0.0039344 | 0.00098558 | 2.2373e-07 | -3.7389e-08 | 0.0060115 | 0.0060114 | 0.0060115 | 0.9738 | -0.18417 | 0.97385 | -0.18376 | 2.2265
79 | -0.0059431 | -0.001489 | 0.0059442 | 0.0014892 | 1.087e-06 | 1.5518e-07 | 0.0090807 | 0.0090806 | 0.0090807 | 0.97385 | -0.18376 | 0.97404 | -0.18244 | 3.3632
80 | 0.010423 | 0.0026121 | -0.010421 | -0.0026115 | 1.8895e-06 | 5.7811e-07 | 0.015923 | 0.015923 | 0.015923 | 0.97404 | -0.18244 | 0.97385 | -0.18375 | 5.8974
81 | 0.029243 | 0.0073364 | -0.029202 | -0.007321 | 4.1121e-05 | 1.5405e-05 | 0.044677 | 0.044677 | 0.044677 | 0.97404 | -0.18244 | 0.97262 | -0.19259 | 16.5469
82 | 0.0086846 | 0.0021764 | -0.008681 | -0.0021754 | 3.6413e-06 | 9.8836e-07 | 0.01327 | 0.01327 | 0.01327 | 0.97385 | -0.18375 | 0.97343 | -0.18678 | 4.9148
83 | 0.027206 | 0.0068209 | -0.027198 | -0.0068175 | 8.9711e-06 | 3.3475e-06 | 0.041624 | 0.041624 | 0.041624 | 0.97262 | -0.19259 | 0.97229 | -0.19497 | 15.4163
84 | 0.0041936 | 0.0010507 | -0.0041935 | -0.0010508 | 1.0189e-07 | -1.0207e-08 | 0.0064104 | 0.0064104 | 0.0064104 | 0.97343 | -0.18678 | 0.97341 | -0.18696 | 2.3742
85 | 0.013191 | 0.0033059 | -0.013175 | -0.0033006 | 1.5924e-05 | 5.3488e-06 | 0.020188 | 0.020188 | 0.020188 | 0.97229 | -0.19497 | 0.97108 | -0.2037 | 7.477
86 | 0.014007 | 0.0035116 | -0.013999 | -0.003509 | 7.7196e-06 | 2.6354e-06 | 0.021437 | 0.021437 | 0.021437 | 0.97229 | -0.19497 | 0.97174 | -0.19895 | 7.9395
87 | -0.0014355 | -0.00035978 | 0.0014357 | 0.00035925 | 1.3264e-07 | -5.281e-07 | 0.0021652 | 0.002165 | 0.0021652 | 0.98657 | -0.093895 | 0.98666 | -0.093226 | 0.80192
88 | -0.0014357 | -0.00035925 | 0.0014358 | 0.00035882 | 1.0872e-07 | -4.3301e-07 | 0.002165 | 0.0021648 | 0.002165 | 0.98666 | -0.093226 | 0.98674 | -0.092677 | 0.80184
89 | -0.0015783 | -0.00039454 | 0.0015785 | 0.00039377 | 2.3827e-07 | -7.6987e-07 | 0.0023797 | 0.0023794 | 0.0023797 | 0.98674 | -0.092677 | 0.98689 | -0.091579 | 0.88139
90 | 0.003202 | 0.00080248 | -0.003202 | -0.00080249 | 2.3699e-08 | -1.1803e-08 | 0.0048222 | 0.0048222 | 0.0048222 | 0.98806 | -0.083309 | 0.98805 | -0.083362 | 1.786
91 | 0.0092627 | 0.0023205 | -0.0092603 | -0.0023198 | 2.3931e-06 | 6.6952e-07 | 0.01397 | 0.01397 | 0.01397 | 0.98663 | -0.093462 | 0.98636 | -0.09533 | 5.1739
92 | 0.002336 | 0.00058305 | -0.0023357 | -0.00058344 | 3.0642e-07 | -3.8839e-07 | 0.0035208 | 0.003521 | 0.003521 | 0.98704 | -0.090495 | 0.98691 | -0.09145 | 1.3041
93 | 0.0019268 | 0.00048266 | -0.0019267 | -0.00048276 | 5.2789e-08 | -1.0092e-07 | 0.0029453 | 0.0029454 | 0.0029454 | 0.97341 | -0.18696 | 0.97338 | -0.18715 | 1.0909
94 | 0.008039 | 0.0020134 | -0.0080366 | -0.0020128 | 2.4026e-06 | 6.1023e-07 | 0.012318 | 0.012318 | 0.012318 | 0.97108 | -0.2037 | 0.97078 | -0.20586 | 4.5622
95 | 0.012732 | 0.0031915 | -0.012728 | -0.0031901 | 4.0305e-06 | 1.3398e-06 | 0.019497 | 0.019497 | 0.019497 | 0.97174 | -0.19895 | 0.97142 | -0.20124 | 7.221
96 | -0.0023243 | -0.00058236 | 0.0023244 | 0.00058226 | 8.2357e-08 | -9.8774e-08 | 0.0035497 | 0.0035497 | 0.0035497 | 0.9743 | -0.18064 | 0.97434 | -0.18038 | 1.3147
97 | 0.0011345 | 0.00028417 | -0.0011345 | -0.00028432 | 2.4075e-08 | -1.5079e-07 | 0.0017326 | 0.0017326 | 0.0017326 | 0.9743 | -0.18064 | 0.97428 | -0.18079 | 0.64172
98 | -0.0037952 | -0.00095088 | 0.0037954 | 0.00095084 | 2.274e-07 | -4.7658e-08 | 0.0057959 | 0.0057959 | 0.0057959 | 0.97434 | -0.18038 | 0.9744 | -0.17995 | 2.1466
99 | -0.0051893 | -0.0013002 | 0.0051901 | 0.0013002 | 8.2645e-07 | 5.5117e-08 | 0.0079245 | 0.0079245 | 0.0079245 | 0.9744 | -0.17995 | 0.97456 | -0.1788 | 2.935
100 | -0.0061514 | -0.0015412 | 0.0061523 | 0.0015413 | 9.4403e-07 | 1.4936e-07 | 0.0093922 | 0.0093921 | 0.0093922 | 0.97456 | -0.1788 | 0.97471 | -0.17769 | 3.4786
101 | -0.0075188 | -0.001883 | 0.0075197 | 0.0018832 | 9.1189e-07 | 2.1245e-07 | 0.011478 | 0.011478 | 0.011478 | 0.97471 | -0.17769 | 0.97483 | -0.17681 | 4.2511
102 | 0.0013665 | 0.00034166 | -0.0013663 | -0.00034242 | 1.823e-07 | -7.6665e-07 | 0.0020858 | 0.0020861 | 0.0020861 | 0.97471 | -0.17769 | 0.97458 | -0.17865 | 0.77262
103 | 0.0058357 | 0.0014622 | -0.005834 | -0.001462 | 1.7059e-06 | 2.0539e-07 | 0.0088004 | 0.0088005 | 0.0088005 | 0.98671 | -0.092682 | 0.98641 | -0.094794 | 3.2595
104 | -0.0058357 | -0.0014622 | 0.0058388 | 0.0014626 | 3.1636e-06 | 3.8013e-07 | 0.0088004 | 0.0088001 | 0.0088004 | 0.98671 | -0.092682 | 0.98726 | -0.088764 | 3.2594
105 | 0.005834 | 0.001462 | -0.0058329 | -0.0014619 | 1.0083e-06 | 1.2152e-07 | 0.0088005 | 0.0088006 | 0.0088006 | 0.98641 | -0.094794 | 0.98624 | -0.096043 | 3.2595
106 | -0.0073774 | -0.0018482 | 0.00738 | 0.0018488 | 2.5682e-06 | 5.6194e-07 | 0.011119 | 0.011119 | 0.011119 | 0.98726 | -0.088764 | 0.98762 | -0.086247 | 4.1182
107 | -0.01187 | -0.002974 | 0.011873 | 0.0029749 | 2.8934e-06 | 9.2727e-07 | 0.017883 | 0.017883 | 0.017883 | 0.98762 | -0.086247 | 0.98787 | -0.084486 | 6.6235
108 | -0.0017271 | -0.00043285 | 0.0017272 | 0.00043268 | 6.8465e-08 | -1.7016e-07 | 0.0026374 | 0.0026374 | 0.0026374 | 0.97442 | -0.17981 | 0.97445 | -0.17952 | 0.97683
109 | -0.0031429 | -0.00078739 | 0.0031431 | 0.00078732 | 1.5125e-07 | -7.089e-08 | 0.0048181 | 0.0048181 | 0.0048181 | 0.97064 | -0.20693 | 0.97068 | -0.20659 | 1.7845
110 | 0.0016977 | 0.00042518 | -0.0016977 | -0.00042528 | 3.8912e-08 | -9.8824e-08 | 0.0026026 | 0.0026026 | 0.0026026 | 0.97064 | -0.20693 | 0.97061 | -0.2071 | 0.96393
111 | -0.0062474 | -0.0015653 | 0.006248 | 0.0015654 | 6.2322e-07 | 1.0507e-07 | 0.0095768 | 0.0095767 | 0.0095768 | 0.97068 | -0.20659 | 0.97078 | -0.20586 | 3.547
112 | 0.0016977 | 0.00042528 | -0.0016976 | -0.00042546 | 7.17e-08 | -1.8207e-07 | 0.0026026 | 0.0026027 | 0.0026027 | 0.97061 | -0.2071 | 0.97057 | -0.2074 | 0.96396
113 | 0.0017886 | 0.00044735 | -0.0017886 | -0.00044746 | 4.7806e-08 | -1.0766e-07 | 0.0027413 | 0.0027413 | 0.0027413 | 0.97078 | -0.20586 | 0.97076 | -0.20606 | 1.0153
114 | 0.0017886 | 0.00044746 | -0.0017883 | -0.00044818 | 3.1814e-07 | -7.1619e-07 | 0.0027413 | 0.0027416 | 0.0027416 | 0.97076 | -0.20606 | 0.97058 | -0.20735 | 1.0154
115 | 0.0062801 | 0.0015735 | -0.0062771 | -0.0015731 | 3.0576e-06 | 4.8074e-07 | 0.009478 | 0.0094782 | 0.0094782 | 0.98594 | -0.098307 | 0.98545 | -0.10183 | 3.5105
116 | -0.0070979 | -0.0017785 | 0.0070981 | 0.0017785 | 1.8101e-07 | 3.738e-08 | 0.010712 | 0.010712 | 0.010712 | 0.98594 | -0.098307 | 0.98597 | -0.098122 | 3.9675
117 | 0.0043819 | 0.0010981 | -0.0043817 | -0.0010981 | 1.6607e-07 | -1.3573e-08 | 0.0066166 | 0.0066166 | 0.0066166 | 0.98545 | -0.10183 | 0.98541 | -0.1021 | 2.4506
118 | 0.0021586 | 0.00054029 | -0.0021582 | -0.0005409 | 3.9722e-07 | -6.1211e-07 | 0.0032575 | 0.0032578 | 0.0032578 | 0.98597 | -0.098122 | 0.98578 | -0.099453 | 1.2066
119 | -0.0092567 | -0.0023188 | 0.0092603 | 0.0023198 | 3.5763e-06 | 1.0008e-06 | 0.01397 | 0.01397 | 0.01397 | 0.98597 | -0.098122 | 0.98636 | -0.09533 | 5.174
120 | 0.002347 | 0.00058815 | -0.002347 | -0.00058821 | 4.8017e-08 | -5.9573e-08 | 0.0035441 | 0.0035441 | 0.0035441 | 0.98541 | -0.1021 | 0.98539 | -0.10225 | 1.3126
121 | -0.012726 | -0.0031893 | 0.012728 | 0.0031901 | 2.338e-06 | 7.7721e-07 | 0.019497 | 0.019497 | 0.019497 | 0.97124 | -0.20257 | 0.97142 | -0.20124 | 7.221
122 | 0.0019267 | 0.00048276 | -0.0019267 | -0.00048287 | 5.862e-08 | -1.1205e-07 | 0.0029454 | 0.0029454 | 0.0029454 | 0.97338 | -0.18715 | 0.97335 | -0.18737 | 1.0909
123 | 0.0016905 | 0.00042173 | -0.0016904 | -0.00042181 | 2.9892e-08 | -8.2776e-08 | 0.0025481 | 0.0025482 | 0.0025482 | 0.98691 | -0.09145 | 0.98689 | -0.091579 | 0.94376

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.20711 | 0.052156

## res_load
| p_mw | q_mvar
0 | 0.0041206 | 0.0010327
1 | 0.0024025 | 0.00060212
2 | 0.0019143 | 0.00047977
3 | 0.002307 | 0.00057819
4 | 0.00094988 | 0.00023806
5 | 0.0018434 | 0.00046199
6 | 0.0011457 | 0.00028715
7 | 0.0013884 | 0.00034797
8 | 0.0023789 | 0.00059622
9 | 0.0021199 | 0.00053128
10 | 0.0026815 | 0.00067204
11 | 0.0023095 | 0.00057881
12 | 0.0023377 | 0.00058587
13 | 0.0017827 | 0.0004468
14 | 0.0020822 | 0.00052184
15 | 0.001368 | 0.00034286
16 | 0.0017912 | 0.00044893
17 | 0.0017147 | 0.00042974
18 | 0.0050981 | 0.0012777
19 | 0.0011981 | 0.00030028
20 | 0.00078284 | 0.0001962
21 | 0.0027525 | 0.00068985
22 | 0.0013096 | 0.00032821
23 | 0.0014551 | 0.00036467
24 | 0.0020945 | 0.00052492
25 | 0.0019976 | 0.00050064
26 | 0.00027094 | 6.7903e-05
27 | 0.0054684 | 0.0013705
28 | 0.00026839 | 6.7264e-05
29 | 0.0091158 | 0.0022846
30 | 0.0011028 | 0.00027638
31 | 0.0023353 | 0.00058527
32 | 0.0037508 | 0.00094003
33 | 0.00098289 | 0.00024634
34 | 0.0028684 | 0.0007189
35 | 0.0030627 | 0.00076758
36 | 0.0018501 | 0.00046367
37 | 0.0022087 | 0.00055356
38 | 0.0023809 | 0.00059671
39 | 0.0001036 | 2.5966e-05
40 | 0.00090736 | 0.00022741
41 | 0.0008263 | 0.00020709
42 | 0.0010638 | 0.00026662
43 | 0.0012524 | 0.00031388
44 | 0.0013677 | 0.00034279
45 | 0.00096485 | 0.00024181
46 | 0.0010971 | 0.00027495
47 | 0.0011904 | 0.00029835
48 | 0.001 | 0.00025063
49 | 0.00028756 | 7.2069e-05
50 | 0.0022983 | 0.00057601
51 | 7.1354e-05 | 1.7883e-05
52 | 0.0011867 | 0.00029741
53 | 0.0012772 | 0.00032011
54 | 0.0016465 | 0.00041265
55 | 0.0020087 | 0.00050343
56 | 0.0017364 | 0.00043518
57 | 0.0019953 | 0.00050008
58 | 0.0044873 | 0.0011246
59 | 0.00069577 | 0.00017438
60 | 0.0014355 | 0.00035978
61 | 0.00014254 | 3.5723e-05
62 | 0.0040955 | 0.0010264
63 | 0.0020414 | 0.00051163
64 | 0.0023963 | 0.00060058
65 | 0.0056075 | 0.0014054
66 | 0.0022667 | 0.0005681
67 | 0.0051359 | 0.0012872
68 | 0.001267 | 0.00031753
69 | 0.0011898 | 0.00029819
70 | 0.0014708 | 0.00036862
71 | 0.0011345 | 0.00028432
72 | 0.0013939 | 0.00034935
73 | 0.00096125 | 0.00024091
74 | 0.0015386 | 0.00038561
75 | 0.00088673 | 0.00022223
76 | 0.0013663 | 0.00034242
77 | 0.0044896 | 0.0011252
78 | 0.0021144 | 0.00052991
79 | 0.0058329 | 0.0014619
80 | 0.0017271 | 0.00043285
81 | 0.0018575 | 0.00046554
82 | 0.0014452 | 0.00036221
83 | 0.0031043 | 0.000778
84 | 0.0016976 | 0.00042546
85 | 0.0017883 | 0.00044818
86 | 0.00081783 | 0.00020497
87 | 0.0018952 | 0.00047497
88 | 0.0020347 | 0.00050994
89 | 0.0021582 | 0.0005409
90 | 0.002347 | 0.00058821
91 | 0.012726 | 0.0031893
92 | 0.0019267 | 0.00048287
93 | 0.003202 | 0.00080249
94 | 0.00064523 | 0.00016171
95 | 0.00011189 | 2.8043e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1