## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2430-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2430-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2430-5_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2430-5_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2430-5_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2430-5_0_4_node_73 | 0.4 | n |  | TRUE
6 | bus_LV_2430-5_0_4_node_41 | 0.4 | n |  | TRUE
7 | bus_LV_2430-5_0_4_node_80 | 0.4 | n |  | TRUE
8 | bus_LV_2430-5_0_4_node_39 | 0.4 | n |  | TRUE
9 | bus_LV_2430-5_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2430-5_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2430-5_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2430-5_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2430-5_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2430-5_0_4_node_55 | 0.4 | n |  | TRUE
15 | bus_LV_2430-5_0_4_node_40 | 0.4 | n |  | TRUE
16 | bus_LV_2430-5_0_4_node_45 | 0.4 | n |  | TRUE
17 | bus_LV_2430-5_0_4_node_53 | 0.4 | n |  | TRUE
18 | bus_LV_2430-5_0_4_node_38 | 0.4 | n |  | TRUE
19 | bus_LV_2430-5_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2430-5_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_2430-5_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2430-5_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2430-5_0_4_node_83 | 0.4 | n |  | TRUE
24 | bus_LV_2430-5_0_4_node_82 | 0.4 | n |  | TRUE
25 | bus_LV_2430-5_0_4_node_117 | 0.4 | n |  | TRUE
26 | bus_LV_2430-5_0_4_node_103 | 0.4 | n |  | TRUE
27 | bus_LV_2430-5_0_4_node_115 | 0.4 | n |  | TRUE
28 | bus_LV_2430-5_0_4_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_2430-5_0_4_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_2430-5_0_4_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_2430-5_0_4_node_59 | 0.4 | n |  | TRUE
32 | bus_LV_2430-5_0_4_node_58 | 0.4 | n |  | TRUE
33 | bus_LV_2430-5_0_4_node_51 | 0.4 | n |  | TRUE
34 | bus_LV_2430-5_0_4_node_49 | 0.4 | n |  | TRUE
35 | bus_LV_2430-5_0_4_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_2430-5_0_4_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_2430-5_0_4_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_2430-5_0_4_node_104 | 0.4 | n |  | TRUE
39 | bus_LV_2430-5_0_4_node_105 | 0.4 | n |  | TRUE
40 | bus_LV_2430-5_0_4_node_70 | 0.4 | n |  | TRUE
41 | bus_LV_2430-5_0_4_node_71 | 0.4 | n |  | TRUE
42 | bus_LV_2430-5_0_4_node_114 | 0.4 | n |  | TRUE
43 | bus_LV_2430-5_0_4_node_113 | 0.4 | n |  | TRUE
44 | bus_LV_2430-5_0_4_node_122 | 0.4 | n |  | TRUE
45 | bus_LV_2430-5_0_4_node_22 | 0.4 | n |  | TRUE
46 | bus_LV_2430-5_0_4_node_23 | 0.4 | n |  | TRUE
47 | bus_LV_2430-5_0_4_node_24 | 0.4 | n |  | TRUE
48 | bus_LV_2430-5_0_4_node_25 | 0.4 | n |  | TRUE
49 | bus_LV_2430-5_0_4_node_63 | 0.4 | n |  | TRUE
50 | bus_LV_2430-5_0_4_node_112 | 0.4 | n |  | TRUE
51 | bus_LV_2430-5_0_4_node_61 | 0.4 | n |  | TRUE
52 | bus_LV_2430-5_0_4_node_85 | 0.4 | n |  | TRUE
53 | bus_LV_2430-5_0_4_node_111 | 0.4 | n |  | TRUE
54 | bus_LV_2430-5_0_4_node_26 | 0.4 | n |  | TRUE
55 | bus_LV_2430-5_0_4_node_27 | 0.4 | n |  | TRUE
56 | bus_LV_2430-5_0_4_node_28 | 0.4 | n |  | TRUE
57 | bus_LV_2430-5_0_4_node_29 | 0.4 | n |  | TRUE
58 | bus_LV_2430-5_0_4_node_30 | 0.4 | n |  | TRUE
59 | bus_LV_2430-5_0_4_node_84 | 0.4 | n |  | TRUE
60 | bus_LV_2430-5_0_4_node_67 | 0.4 | n |  | TRUE
61 | bus_LV_2430-5_0_4_node_31 | 0.4 | n |  | TRUE
62 | bus_LV_2430-5_0_4_node_34 | 0.4 | n |  | TRUE
63 | bus_LV_2430-5_0_4_node_65 | 0.4 | n |  | TRUE
64 | bus_LV_2430-5_0_4_node_36 | 0.4 | n |  | TRUE
65 | bus_LV_2430-5_0_4_node_32 | 0.4 | n |  | TRUE
66 | bus_LV_2430-5_0_4_node_33 | 0.4 | n |  | TRUE
67 | bus_LV_2430-5_0_4_node_35 | 0.4 | n |  | TRUE
68 | bus_LV_2430-5_0_4_node_99 | 0.4 | n |  | TRUE
69 | bus_LV_2430-5_0_4_node_98 | 0.4 | n |  | TRUE
70 | bus_LV_2430-5_0_4_node_37 | 0.4 | n |  | TRUE
71 | bus_LV_2430-5_0_4_node_42 | 0.4 | n |  | TRUE
72 | bus_LV_2430-5_0_4_node_43 | 0.4 | n |  | TRUE
73 | bus_LV_2430-5_0_4_node_44 | 0.4 | n |  | TRUE
74 | bus_LV_2430-5_0_4_node_46 | 0.4 | n |  | TRUE
75 | bus_LV_2430-5_0_4_node_47 | 0.4 | n |  | TRUE
76 | bus_LV_2430-5_0_4_node_81 | 0.4 | n |  | TRUE
77 | bus_LV_2430-5_0_4_node_94 | 0.4 | n |  | TRUE
78 | bus_LV_2430-5_0_4_node_95 | 0.4 | n |  | TRUE
79 | bus_LV_2430-5_0_4_node_48 | 0.4 | n |  | TRUE
80 | bus_LV_2430-5_0_4_node_50 | 0.4 | n |  | TRUE
81 | bus_LV_2430-5_0_4_node_52 | 0.4 | n |  | TRUE
82 | bus_LV_2430-5_0_4_node_79 | 0.4 | n |  | TRUE
83 | bus_LV_2430-5_0_4_node_78 | 0.4 | n |  | TRUE
84 | bus_LV_2430-5_0_4_node_54 | 0.4 | n |  | TRUE
85 | bus_LV_2430-5_0_4_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_2430-5_0_4_node_57 | 0.4 | n |  | TRUE
87 | bus_LV_2430-5_0_4_node_75 | 0.4 | n |  | TRUE
88 | bus_LV_2430-5_0_4_node_125 | 0.4 | n |  | TRUE
89 | bus_LV_2430-5_0_4_node_74 | 0.4 | n |  | TRUE
90 | bus_LV_2430-5_0_4_node_124 | 0.4 | n |  | TRUE
91 | bus_LV_2430-5_0_4_node_60 | 0.4 | n |  | TRUE
92 | bus_LV_2430-5_0_4_node_62 | 0.4 | n |  | TRUE
93 | bus_LV_2430-5_0_4_node_64 | 0.4 | n |  | TRUE
94 | bus_LV_2430-5_0_4_node_87 | 0.4 | n |  | TRUE
95 | bus_LV_2430-5_0_4_node_86 | 0.4 | n |  | TRUE
96 | bus_LV_2430-5_0_4_node_66 | 0.4 | n |  | TRUE
97 | bus_LV_2430-5_0_4_node_68 | 0.4 | n |  | TRUE
98 | bus_LV_2430-5_0_4_node_97 | 0.4 | n |  | TRUE
99 | bus_LV_2430-5_0_4_node_69 | 0.4 | n |  | TRUE
100 | bus_LV_2430-5_0_4_node_116 | 0.4 | n |  | TRUE
101 | bus_LV_2430-5_0_4_node_72 | 0.4 | n |  | TRUE
102 | bus_LV_2430-5_0_4_node_126 | 0.4 | n |  | TRUE
103 | bus_LV_2430-5_0_4_node_127 | 0.4 | n |  | TRUE
104 | bus_LV_2430-5_0_4_node_88 | 0.4 | n |  | TRUE
105 | bus_LV_2430-5_0_4_node_129 | 0.4 | n |  | TRUE
106 | bus_LV_2430-5_0_4_node_102 | 0.4 | n |  | TRUE
107 | bus_LV_2430-5_0_4_node_76 | 0.4 | n |  | TRUE
108 | bus_LV_2430-5_0_4_node_77 | 0.4 | n |  | TRUE
109 | bus_LV_2430-5_0_4_node_100 | 0.4 | n |  | TRUE
110 | bus_LV_2430-5_0_4_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_2430-5_0_4_node_90 | 0.4 | n |  | TRUE
112 | bus_LV_2430-5_0_4_node_91 | 0.4 | n |  | TRUE
113 | bus_LV_2430-5_0_4_node_92 | 0.4 | n |  | TRUE
114 | bus_LV_2430-5_0_4_node_93 | 0.4 | n |  | TRUE
115 | bus_LV_2430-5_0_4_node_96 | 0.4 | n |  | TRUE
116 | bus_LV_2430-5_0_4_node_101 | 0.4 | n |  | TRUE
117 | bus_LV_2430-5_0_4_node_130 | 0.4 | n |  | TRUE
118 | bus_LV_2430-5_0_4_node_123 | 0.4 | n |  | TRUE
119 | bus_LV_2430-5_0_4_node_121 | 0.4 | n |  | TRUE
120 | bus_LV_2430-5_0_4_node_106 | 0.4 | n |  | TRUE
121 | bus_LV_2430-5_0_4_node_107 | 0.4 | n |  | TRUE
122 | bus_LV_2430-5_0_4_node_108 | 0.4 | n |  | TRUE
123 | bus_LV_2430-5_0_4_node_109 | 0.4 | n |  | TRUE
124 | bus_LV_2430-5_0_4_node_110 | 0.4 | n |  | TRUE
125 | bus_LV_2430-5_0_4_node_120 | 0.4 | n |  | TRUE
126 | bus_LV_2430-5_0_4_node_119 | 0.4 | n |  | TRUE
127 | bus_LV_2430-5_0_4_node_118 | 0.4 | n |  | TRUE
128 | bus_MV_292_0_node_19 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2430-5_0_4_load_0 | 0 | 0.0023464 | 0.00058807 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2430-5_0_4_load_1 | 1 | 0.001777 | 0.00044535 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2430-5_0_4_load_2 | 2 | 0.0021267 | 0.00053299 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2430-5_0_4_load_3 | 3 | 0.0027134 | 0.00068004 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2430-5_0_4_load_4 | 4 | 0.0018131 | 0.00045441 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2430-5_0_4_load_73 | 5 | 0.0020609 | 0.00051652 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2430-5_0_4_load_41 | 6 | 0.0019259 | 0.00048269 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2430-5_0_4_load_39 | 8 | 0.0018864 | 0.00047278 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2430-5_0_4_load_5 | 9 | 0.0026392 | 0.00066146 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2430-5_0_4_load_6 | 10 | 0.0016798 | 0.000421 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2430-5_0_4_load_7 | 11 | 0.0011936 | 0.00029914 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2430-5_0_4_load_8 | 12 | 0.0012095 | 0.00030312 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2430-5_0_4_load_9 | 13 | 0.0015379 | 0.00038545 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2430-5_0_4_load_40 | 15 | 0.0018584 | 0.00046577 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2430-5_0_4_load_45 | 16 | 0.0034176 | 0.00085653 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2430-5_0_4_load_53 | 17 | 0.0017931 | 0.0004494 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2430-5_0_4_load_38 | 18 | 0.0016545 | 0.00041466 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2430-5_0_4_load_10 | 19 | 0.0030359 | 0.00076087 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2430-5_0_4_load_11 | 20 | 0.0021291 | 0.00053361 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2430-5_0_4_load_12 | 21 | 0.0020826 | 0.00052195 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2430-5_0_4_load_83 | 23 | 0.0028385 | 0.0007114 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2430-5_0_4_load_82 | 24 | 0.0031247 | 0.00078312 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2430-5_0_4_load_103 | 26 | 0.0038095 | 0.00095475 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2430-5_0_4_load_115 | 27 | 0.00090917 | 0.00022786 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2430-5_0_4_load_14 | 28 | 0.0021815 | 0.00054673 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2430-5_0_4_load_16 | 30 | 0.0023669 | 0.00059321 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2430-5_0_4_load_59 | 31 | 0.0022963 | 0.00057551 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2430-5_0_4_load_58 | 32 | 0.0018358 | 0.0004601 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2430-5_0_4_load_51 | 33 | 0.0013243 | 0.00033191 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2430-5_0_4_load_49 | 34 | 0.0019824 | 0.00049683 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2430-5_0_4_load_18 | 35 | 0.0016342 | 0.00040957 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2430-5_0_4_load_19 | 36 | 0.00071224 | 0.0001785 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2430-5_0_4_load_105 | 39 | 0.0019275 | 0.00048308 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2430-5_0_4_load_70 | 40 | 0.0011717 | 0.00029365 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2430-5_0_4_load_71 | 41 | 0.0012146 | 0.00030441 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2430-5_0_4_load_114 | 42 | 0.00022747 | 5.7009e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2430-5_0_4_load_113 | 43 | 0.0011668 | 0.00029242 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2430-5_0_4_load_22 | 45 | 0.0011878 | 0.00029769 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2430-5_0_4_load_24 | 47 | 0.0018694 | 0.00046853 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2430-5_0_4_load_63 | 49 | 0.0018616 | 0.00046655 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2430-5_0_4_load_61 | 51 | 0.0022056 | 0.00055277 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2430-5_0_4_load_85 | 52 | 0.0013415 | 0.00033621 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2430-5_0_4_load_111 | 53 | 0.0016778 | 0.0004205 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2430-5_0_4_load_26 | 54 | 0.001166 | 0.00029223 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2430-5_0_4_load_27 | 55 | 0.00091191 | 0.00022855 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2430-5_0_4_load_29 | 57 | 0.0019072 | 0.00047798 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2430-5_0_4_load_30 | 58 | 0.0010696 | 0.00026806 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2430-5_0_4_load_67 | 60 | 0.0015719 | 0.00039395 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2430-5_0_4_load_31 | 61 | 0.0010833 | 0.0002715 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2430-5_0_4_load_65 | 63 | 0.001406 | 0.00035237 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2430-5_0_4_load_36 | 64 | 0.0018169 | 0.00045536 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2430-5_0_4_load_32 | 65 | 0.0025232 | 0.00063238 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2430-5_0_4_load_33 | 66 | 0.0015305 | 0.00038357 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2430-5_0_4_load_35 | 67 | 0.0015122 | 0.000379 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2430-5_0_4_load_99 | 68 | 0.0021892 | 0.00054866 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2430-5_0_4_load_37 | 70 | 0.0018678 | 0.00046811 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2430-5_0_4_load_42 | 71 | 0.0019191 | 0.00048096 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2430-5_0_4_load_43 | 72 | 0.0024045 | 0.00060263 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2430-5_0_4_load_46 | 74 | 0.0029886 | 0.000749 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2430-5_0_4_load_47 | 75 | 0.0026377 | 0.00066107 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2430-5_0_4_load_81 | 76 | 0.0019283 | 0.00048328 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2430-5_0_4_load_94 | 77 | 0.0039901 | 0.001 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2430-5_0_4_load_95 | 78 | 0.0031009 | 0.00077716 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2430-5_0_4_load_48 | 79 | 0.0023582 | 0.00059101 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2430-5_0_4_load_50 | 80 | 0.0016295 | 0.0004084 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2430-5_0_4_load_52 | 81 | 0.0019268 | 0.0004829 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2430-5_0_4_load_78 | 83 | 0.0018237 | 0.00045707 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2430-5_0_4_load_56 | 85 | 0.00169 | 0.00042356 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2430-5_0_4_load_57 | 86 | 0.001553 | 0.00038921 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2430-5_0_4_load_75 | 87 | 0.0021166 | 0.00053047 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2430-5_0_4_load_125 | 88 | 0.0021305 | 0.00053395 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2430-5_0_4_load_74 | 89 | 0.0019114 | 0.00047905 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2430-5_0_4_load_124 | 90 | 0.0029072 | 0.00072861 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2430-5_0_4_load_60 | 91 | 0.0043615 | 0.0010931 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2430-5_0_4_load_62 | 92 | 0.0023575 | 0.00059084 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2430-5_0_4_load_64 | 93 | 0.0015949 | 0.00039972 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2430-5_0_4_load_87 | 94 | 0.0020515 | 0.00051417 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2430-5_0_4_load_86 | 95 | 0.0015471 | 0.00038774 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2430-5_0_4_load_66 | 96 | 0.0015573 | 0.00039029 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2430-5_0_4_load_68 | 97 | 0.00090807 | 0.00022758 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2430-5_0_4_load_97 | 98 | 0.0011976 | 0.00030014 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2430-5_0_4_load_69 | 99 | 0.00068387 | 0.00017139 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2430-5_0_4_load_116 | 100 | 0.0022258 | 0.00055784 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2430-5_0_4_load_126 | 102 | 0.00012305 | 3.0839e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2430-5_0_4_load_127 | 103 | 0.0021501 | 0.00053887 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2430-5_0_4_load_88 | 104 | 0.00062779 | 0.00015734 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2430-5_0_4_load_129 | 105 | 0.00012661 | 3.173e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2430-5_0_4_load_102 | 106 | 0.0024378 | 0.00061097 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2430-5_0_4_load_76 | 107 | 0.0015126 | 0.00037909 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2430-5_0_4_load_77 | 108 | 0.0013121 | 0.00032885 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2430-5_0_4_load_100 | 109 | 0.0014241 | 0.00035692 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2430-5_0_4_load_89 | 110 | 0.0016863 | 0.00042263 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2430-5_0_4_load_90 | 111 | 0.00091188 | 0.00022854 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2430-5_0_4_load_91 | 112 | 0.0013373 | 0.00033515 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2430-5_0_4_load_92 | 113 | 0.0019705 | 0.00049385 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2430-5_0_4_load_96 | 115 | 0.0010789 | 0.00027039 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2430-5_0_4_load_101 | 116 | 0.0026762 | 0.00067072 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2430-5_0_4_load_130 | 117 | 0.00045575 | 0.00011422 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2430-5_0_4_load_123 | 118 | 0.0012117 | 0.00030368 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2430-5_0_4_load_121 | 119 | 0.00029053 | 7.2813e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2430-5_0_4_load_106 | 120 | 0.0012466 | 0.00031243 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2430-5_0_4_load_108 | 122 | 0.0034931 | 0.00087544 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2430-5_0_4_load_109 | 123 | 0.00034687 | 8.6935e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2430-5_0_4_load_110 | 124 | 0.00022919 | 5.7439e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2430-5_0_4_load_119 | 126 | 0.0016057 | 0.00040242 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2430-5_0_4_load_118 | 127 | 0.0021885 | 0.0005485 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 87 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2430-5_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0040706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2430-5_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.016095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2430-5_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.019797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2430-5_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.010514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2430-5_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2430-5_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.010915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2430-5_0_4_line_6 | NAYY 4x150 SE | 5 | 7 | 0.0091456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2430-5_0_4_line_7 | NAYY 4x150 SE | 6 | 8 | 0.0050045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2430-5_0_4_line_8 | NAYY 4x150 SE | 7 | 106 | 0.0080232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2430-5_0_4_line_9 | NAYY 4x150 SE | 7 | 82 | 0.027105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2430-5_0_4_line_10 | NAYY 4x150 SE | 8 | 70 | 0.0073071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2430-5_0_4_line_11 | NAYY 4x150 SE | 9 | 10 | 0.0024394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2430-5_0_4_line_12 | NAYY 4x150 SE | 9 | 11 | 0.010281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2430-5_0_4_line_13 | NAYY 4x150 SE | 10 | 12 | 0.019139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2430-5_0_4_line_14 | NAYY 4x150 SE | 11 | 13 | 0.0097864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2430-5_0_4_line_15 | NAYY 4x150 SE | 12 | 14 | 0.0085495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2430-5_0_4_line_16 | NAYY 4x150 SE | 13 | 15 | 0.0078649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2430-5_0_4_line_17 | NAYY 4x150 SE | 14 | 16 | 0.044876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2430-5_0_4_line_18 | NAYY 4x150 SE | 14 | 17 | 0.012605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2430-5_0_4_line_19 | NAYY 4x150 SE | 15 | 18 | 0.012259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2430-5_0_4_line_20 | NAYY 4x150 SE | 16 | 72 | 0.026245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2430-5_0_4_line_21 | NAYY 4x150 SE | 17 | 84 | 0.025076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2430-5_0_4_line_22 | NAYY 4x150 SE | 18 | 70 | 0.0086455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2430-5_0_4_line_23 | NAYY 4x150 SE | 19 | 20 | 0.0014559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2430-5_0_4_line_24 | NAYY 4x150 SE | 19 | 21 | 0.008869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2430-5_0_4_line_25 | NAYY 4x150 SE | 20 | 22 | 0.020284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2430-5_0_4_line_26 | NAYY 4x150 SE | 22 | 23 | 0.010716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2430-5_0_4_line_27 | NAYY 4x150 SE | 23 | 24 | 0.013852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2430-5_0_4_line_28 | NAYY 4x150 SE | 24 | 76 | 0.01095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2430-5_0_4_line_29 | NAYY 4x150 SE | 25 | 26 | 0.017974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2430-5_0_4_line_30 | NAYY 4x150 SE | 25 | 27 | 0.00629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2430-5_0_4_line_31 | NAYY 4x150 SE | 26 | 116 | 0.010186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2430-5_0_4_line_32 | NAYY 4x150 SE | 27 | 100 | 0.017489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2430-5_0_4_line_33 | NAYY 4x150 SE | 28 | 29 | 0.038643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2430-5_0_4_line_34 | NAYY 4x150 SE | 29 | 30 | 0.048362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2430-5_0_4_line_35 | NAYY 4x150 SE | 30 | 31 | 0.0317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2430-5_0_4_line_36 | NAYY 4x150 SE | 31 | 32 | 0.0081234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2430-5_0_4_line_37 | NAYY 4x150 SE | 32 | 64 | 0.010229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2430-5_0_4_line_38 | NAYY 4x150 SE | 33 | 34 | 0.00080363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2430-5_0_4_line_39 | NAYY 4x150 SE | 34 | 79 | 0.021285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2430-5_0_4_line_40 | NAYY 4x150 SE | 35 | 36 | 0.026271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2430-5_0_4_line_41 | NAYY 4x150 SE | 36 | 37 | 0.017262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2430-5_0_4_line_42 | NAYY 4x150 SE | 37 | 38 | 0.078545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_2430-5_0_4_line_43 | NAYY 4x150 SE | 37 | 39 | 0.010138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_2430-5_0_4_line_44 | NAYY 4x150 SE | 38 | 42 | 0.034533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2430-5_0_4_line_45 | NAYY 4x150 SE | 38 | 43 | 0.016772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_2430-5_0_4_line_46 | NAYY 4x150 SE | 39 | 44 | 0.018375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_2430-5_0_4_line_47 | NAYY 4x150 SE | 40 | 41 | 0.020225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2430-5_0_4_line_48 | NAYY 4x150 SE | 41 | 101 | 0.01671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2430-5_0_4_line_49 | NAYY 4x150 SE | 42 | 117 | 0.0029451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2430-5_0_4_line_50 | NAYY 4x150 SE | 43 | 114 | 0.04725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_2430-5_0_4_line_51 | NAYY 4x150 SE | 44 | 118 | 0.026318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2430-5_0_4_line_52 | NAYY 4x150 SE | 44 | 119 | 0.0021293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
53 | LV_2430-5_0_4_line_53 | NAYY 4x150 SE | 45 | 46 | 0.022614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2430-5_0_4_line_54 | NAYY 4x150 SE | 46 | 47 | 0.019082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2430-5_0_4_line_55 | NAYY 4x150 SE | 46 | 48 | 0.023079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2430-5_0_4_line_56 | NAYY 4x150 SE | 48 | 49 | 0.018584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2430-5_0_4_line_57 | NAYY 4x150 SE | 48 | 50 | 0.02204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2430-5_0_4_line_58 | NAYY 4x150 SE | 49 | 51 | 0.016434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2430-5_0_4_line_59 | NAYY 4x150 SE | 50 | 52 | 0.021509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2430-5_0_4_line_60 | NAYY 4x150 SE | 50 | 53 | 0.014756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2430-5_0_4_line_61 | NAYY 4x150 SE | 51 | 91 | 0.00060967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2430-5_0_4_line_62 | NAYY 4x150 SE | 52 | 59 | 0.022267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2430-5_0_4_line_63 | NAYY 4x150 SE | 54 | 55 | 0.011193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
64 | LV_2430-5_0_4_line_64 | NAYY 4x150 SE | 54 | 56 | 0.03438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
65 | LV_2430-5_0_4_line_65 | NAYY 4x150 SE | 55 | 57 | 0.01369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
66 | LV_2430-5_0_4_line_66 | NAYY 4x150 SE | 56 | 58 | 0.014403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
67 | LV_2430-5_0_4_line_67 | NAYY 4x150 SE | 57 | 59 | 0.013794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2430-5_0_4_line_68 | NAYY 4x150 SE | 58 | 60 | 0.00042835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
69 | LV_2430-5_0_4_line_69 | NAYY 4x150 SE | 60 | 63 | 0.038579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
70 | LV_2430-5_0_4_line_70 | NAYY 4x150 SE | 61 | 62 | 0.013815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2430-5_0_4_line_71 | NAYY 4x150 SE | 62 | 64 | 0.01238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2430-5_0_4_line_72 | NAYY 4x150 SE | 62 | 65 | 0.023857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2430-5_0_4_line_73 | NAYY 4x150 SE | 63 | 96 | 0.020359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_2430-5_0_4_line_74 | NAYY 4x150 SE | 65 | 66 | 0.020104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2430-5_0_4_line_75 | NAYY 4x150 SE | 66 | 67 | 0.0056552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2430-5_0_4_line_76 | NAYY 4x150 SE | 67 | 68 | 0.023213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2430-5_0_4_line_77 | NAYY 4x150 SE | 68 | 69 | 0.030377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2430-5_0_4_line_78 | NAYY 4x150 SE | 69 | 98 | 0.0027072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
79 | LV_2430-5_0_4_line_79 | NAYY 4x150 SE | 69 | 97 | 0.0061418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
80 | LV_2430-5_0_4_line_80 | NAYY 4x150 SE | 71 | 72 | 0.011369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2430-5_0_4_line_81 | NAYY 4x150 SE | 71 | 73 | 0.0051329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2430-5_0_4_line_82 | NAYY 4x150 SE | 73 | 74 | 0.018946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2430-5_0_4_line_83 | NAYY 4x150 SE | 73 | 75 | 0.035552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2430-5_0_4_line_84 | NAYY 4x150 SE | 74 | 76 | 0.0020729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2430-5_0_4_line_85 | NAYY 4x150 SE | 75 | 77 | 0.0087359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2430-5_0_4_line_86 | NAYY 4x150 SE | 77 | 78 | 0.031088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2430-5_0_4_line_87 | NAYY 4x150 SE | 79 | 80 | 0.0010399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2430-5_0_4_line_88 | NAYY 4x150 SE | 80 | 81 | 0.024014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2430-5_0_4_line_89 | NAYY 4x150 SE | 81 | 82 | 0.011098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2430-5_0_4_line_90 | NAYY 4x150 SE | 82 | 83 | 0.023305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2430-5_0_4_line_91 | NAYY 4x150 SE | 83 | 108 | 0.023027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2430-5_0_4_line_92 | NAYY 4x150 SE | 84 | 85 | 0.03687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
93 | LV_2430-5_0_4_line_93 | NAYY 4x150 SE | 84 | 86 | 0.0086536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
94 | LV_2430-5_0_4_line_94 | NAYY 4x150 SE | 85 | 87 | 0.02229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
95 | LV_2430-5_0_4_line_95 | NAYY 4x150 SE | 86 | 88 | 0.0085182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_2430-5_0_4_line_96 | NAYY 4x150 SE | 87 | 89 | 0.040455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2430-5_0_4_line_97 | NAYY 4x150 SE | 88 | 90 | 0.02443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_2430-5_0_4_line_98 | NAYY 4x150 SE | 90 | 125 | 0.023413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
99 | LV_2430-5_0_4_line_99 | NAYY 4x150 SE | 91 | 92 | 0.020346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2430-5_0_4_line_100 | NAYY 4x150 SE | 92 | 93 | 0.022919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2430-5_0_4_line_101 | NAYY 4x150 SE | 93 | 94 | 0.0098503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2430-5_0_4_line_102 | NAYY 4x150 SE | 94 | 95 | 0.012326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2430-5_0_4_line_103 | NAYY 4x150 SE | 95 | 104 | 0.036317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2430-5_0_4_line_104 | NAYY 4x150 SE | 96 | 97 | 0.0037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
105 | LV_2430-5_0_4_line_105 | NAYY 4x150 SE | 98 | 115 | 0.0074184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
106 | LV_2430-5_0_4_line_106 | NAYY 4x150 SE | 99 | 100 | 0.087533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2430-5_0_4_line_107 | NAYY 4x150 SE | 101 | 102 | 0.0026298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2430-5_0_4_line_108 | NAYY 4x150 SE | 101 | 103 | 0.033223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2430-5_0_4_line_109 | NAYY 4x150 SE | 102 | 105 | 0.0058901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2430-5_0_4_line_110 | NAYY 4x150 SE | 104 | 105 | 0.13822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2430-5_0_4_line_111 | NAYY 4x150 SE | 106 | 109 | 0.0023728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2430-5_0_4_line_112 | NAYY 4x150 SE | 107 | 108 | 0.027368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2430-5_0_4_line_113 | NAYY 4x150 SE | 109 | 116 | 0.014797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2430-5_0_4_line_114 | NAYY 4x150 SE | 110 | 111 | 0.027544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
115 | LV_2430-5_0_4_line_115 | NAYY 4x150 SE | 110 | 112 | 0.012514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
116 | LV_2430-5_0_4_line_116 | NAYY 4x150 SE | 111 | 113 | 0.0067066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
117 | LV_2430-5_0_4_line_117 | NAYY 4x150 SE | 112 | 114 | 0.017724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
118 | LV_2430-5_0_4_line_118 | NAYY 4x150 SE | 113 | 115 | 0.020068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
119 | LV_2430-5_0_4_line_119 | NAYY 4x150 SE | 119 | 123 | 0.025022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
120 | LV_2430-5_0_4_line_120 | NAYY 4x150 SE | 120 | 121 | 0.016238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2430-5_0_4_line_121 | NAYY 4x150 SE | 120 | 122 | 0.010916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2430-5_0_4_line_122 | NAYY 4x150 SE | 121 | 123 | 0.0052938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
123 | LV_2430-5_0_4_line_123 | NAYY 4x150 SE | 121 | 124 | 0.019461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
124 | LV_2430-5_0_4_line_124 | NAYY 4x150 SE | 124 | 125 | 0.012443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
125 | LV_2430-5_0_4_line_125 | NAYY 4x150 SE | 125 | 126 | 0.021242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_2430-5_0_4_line_126 | NAYY 4x150 SE | 126 | 127 | 0.0019634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2430-5_0_4_trafo_75 | 0.25 MVA 20/0.4 kV | 128 | 87 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2606513.9133 | 1236834.8306 | 2606517.4137 | 1236832.753
1 | 2606513.9133 | 1236834.8306 | 2606500.0726 | 1236843.0453
2 | 2606517.4137 | 1236832.753 | 2606533.0005 | 1236823.502 | 2606534.5769 | 1236822.947
3 | 2606500.0726 | 1236843.0453 | 2606491.0314 | 1236848.4114
4 | 2606534.5769 | 1236822.947 | 2606561.4598 | 1236813.4826
5 | 2606491.0314 | 1236848.4114 | 2606481.6454 | 1236853.9822
6 | 2606570.0864 | 1236810.4456 | 2606561.4598 | 1236813.4826
7 | 2606477.3419 | 1236856.5365 | 2606481.6454 | 1236853.9822
8 | 2606570.0864 | 1236810.4456 | 2606570.3996 | 1236818.4627
9 | 2606570.7441 | 1236783.3519 | 2606570.0864 | 1236810.4456
10 | 2606477.3419 | 1236856.5365 | 2606474.7002 | 1236858.1044 | 2606470.7434 | 1236859.6146
11 | 2606425.1171 | 1236877.0293 | 2606422.838 | 1236877.8992
12 | 2606425.1171 | 1236877.0293 | 2606434.7218 | 1236873.3633
13 | 2606404.9573 | 1236884.7239 | 2606422.838 | 1236877.8992
14 | 2606434.7218 | 1236873.3633 | 2606443.8649 | 1236869.8736
15 | 2606396.9699 | 1236887.7725 | 2606404.9573 | 1236884.7239
16 | 2606451.2127 | 1236867.0691 | 2606443.8649 | 1236869.8736
17 | 2606396.9699 | 1236887.7725 | 2606427.9814 | 1236915.6894 | 2606430.8276 | 1236917.0392
18 | 2606396.9699 | 1236887.7725 | 2606386.7634 | 1236880.3755
19 | 2606451.2127 | 1236867.0691 | 2606462.6663 | 1236862.6975
20 | 2606430.8276 | 1236917.0392 | 2606434.9835 | 1236919.0101 | 2606442.0126 | 1236918.3728 | 2606455.7453 | 1236913.4525
21 | 2606366.4587 | 1236865.6599 | 2606386.7634 | 1236880.3755
22 | 2606462.6663 | 1236862.6975 | 2606470.7434 | 1236859.6146
23 | 2606531.6633 | 1236903.4743 | 2606531.0447 | 1236902.1563
24 | 2606535.4315 | 1236911.5029 | 2606531.6633 | 1236903.4743
25 | 2606522.4263 | 1236883.794 | 2606531.0447 | 1236902.1563
26 | 2606522.4263 | 1236883.794 | 2606512.7316 | 1236888.3607
27 | 2606512.7316 | 1236888.3607 | 2606500.2007 | 1236894.2634
28 | 2606490.2946 | 1236898.9297 | 2606500.2007 | 1236894.2634
29 | 2606572.1691 | 1236863.7582 | 2606571.4675 | 1236845.7974
30 | 2606572.1691 | 1236863.7582 | 2606572.9184 | 1236870.0034
31 | 2606571.4675 | 1236845.7974 | 2606571.0699 | 1236835.6197
32 | 2606572.9184 | 1236870.0034 | 2606574.7331 | 1236885.1297 | 2606575.6297 | 1236887.1979
33 | 2606591.0846 | 1236710.9077 | 2606582.9717 | 1236740.6281 | 2606575.191 | 1236741.5491
34 | 2606591.0846 | 1236710.9077 | 2606580.9012 | 1236717.7007 | 2606546.5303 | 1236728.8085
35 | 2606546.5303 | 1236728.8085 | 2606527.9978 | 1236734.7978 | 2606517.6975 | 1236741.3799
36 | 2606517.6975 | 1236741.3799 | 2606510.8523 | 1236745.7541
37 | 2606502.2332 | 1236751.2618 | 2606510.8523 | 1236745.7541
38 | 2606622.8305 | 1236759.5584 | 2606623.5917 | 1236759.3005
39 | 2606602.8829 | 1236766.9384 | 2606609.4411 | 1236764.0938 | 2606622.8305 | 1236759.5584
40 | 2606209.0394 | 1236912.1446 | 2606199.3547 | 1236936.5654
41 | 2606215.403 | 1236896.0981 | 2606209.0394 | 1236912.1446
42 | 2606274.4953 | 1236847.5743 | 2606268.2226 | 1236855.606 | 2606259.6825 | 1236861.4117 | 2606238.8145 | 1236870.7624 | 2606229.0484 | 1236877.0116 | 2606221.4066 | 1236884.8529 | 2606215.403 | 1236896.0981
43 | 2606215.403 | 1236896.0981 | 2606223.6599 | 1236900.5871 | 2606224.3951 | 1236900.5088
44 | 2606274.4953 | 1236847.5743 | 2606244.7469 | 1236830.0358
45 | 2606274.4953 | 1236847.5743 | 2606282.7378 | 1236832.9676
46 | 2606242.6667 | 1236898.5612 | 2606224.3951 | 1236900.5088
47 | 2606008.0302 | 1236848.4358 | 2606027.4465 | 1236842.7752
48 | 2606043.489 | 1236838.0983 | 2606027.4465 | 1236842.7752
49 | 2606242.2099 | 1236828.5401 | 2606244.7469 | 1236830.0358
50 | 2606305.9587 | 1236791.8176 | 2606282.7378 | 1236832.9676
51 | 2606242.6667 | 1236898.5612 | 2606246.5283 | 1236924.5922
52 | 2606242.6667 | 1236898.5612 | 2606244.7747 | 1236898.2606
53 | 2606321.4312 | 1236719.3228 | 2606316.2793 | 1236711.8128 | 2606311.5712 | 1236699.1528
54 | 2606321.4312 | 1236719.3228 | 2606334.4977 | 1236705.416
55 | 2606321.4312 | 1236719.3228 | 2606310.954 | 1236732.431 | 2606309.6008 | 1236738.6
56 | 2606309.6008 | 1236738.6 | 2606292.2701 | 1236745.3103
57 | 2606309.6008 | 1236738.6 | 2606317.7225 | 1236742.333 | 2606330.703 | 1236744.5036
58 | 2606276.9452 | 1236751.244 | 2606292.2701 | 1236745.3103
59 | 2606330.703 | 1236744.5036 | 2606345.808 | 1236729.1912
60 | 2606330.703 | 1236744.5036 | 2606326.1357 | 1236756.5617 | 2606325.2109 | 1236758.1776
61 | 2606276.9452 | 1236751.244 | 2606276.3767 | 1236751.4641
62 | 2606361.4454 | 1236713.3392 | 2606345.808 | 1236729.1912
63 | 2606383.9406 | 1236729.1293 | 2606391.4742 | 1236734.4173 | 2606393.3707 | 1236735.0166
64 | 2606427.1661 | 1236737.5018 | 2606414.8625 | 1236739.1007 | 2606401.4652 | 1236737.5744 | 2606393.3707 | 1236735.0166
65 | 2606372.7352 | 1236721.2639 | 2606383.9406 | 1236729.1293
66 | 2606427.1661 | 1236737.5018 | 2606427.8243 | 1236744.6068 | 2606428.9038 | 1236751.7938
67 | 2606361.4454 | 1236713.3392 | 2606372.7352 | 1236721.2639
68 | 2606428.9038 | 1236751.7938 | 2606428.9674 | 1236752.2174
69 | 2606422.0711 | 1236783.959 | 2606427.8899 | 1236782.2077 | 2606432.1071 | 1236779.2993 | 2606432.5494 | 1236776.0645 | 2606428.9674 | 1236752.2174
70 | 2606491.8009 | 1236757.9283 | 2606485.5328 | 1236747.3706 | 2606484.0123 | 1236747.1466
71 | 2606491.8009 | 1236757.9283 | 2606502.2332 | 1236751.2618
72 | 2606491.8009 | 1236757.9283 | 2606470.8091 | 1236769.2635
73 | 2606422.0711 | 1236783.959 | 2606402.5757 | 1236789.8269
74 | 2606470.8091 | 1236769.2635 | 2606464.5333 | 1236772.6523 | 2606452.7475 | 1236778.0696
75 | 2606447.6091 | 1236780.4315 | 2606452.7475 | 1236778.0696
76 | 2606447.6091 | 1236780.4315 | 2606434.3691 | 1236786.5172 | 2606426.019 | 1236788.7416
77 | 2606396.6661 | 1236796.5609 | 2606426.019 | 1236788.7416
78 | 2606396.6661 | 1236796.5609 | 2606394.0501 | 1236797.2573
79 | 2606396.6661 | 1236796.5609 | 2606399.0327 | 1236790.8933
80 | 2606466.4477 | 1236909.618 | 2606455.7453 | 1236913.4525
81 | 2606471.2798 | 1236907.8867 | 2606466.4477 | 1236909.618
82 | 2606471.2798 | 1236907.8867 | 2606488.4193 | 1236899.8131
83 | 2606471.2798 | 1236907.8867 | 2606478.3009 | 1236928.6403 | 2606476.337 | 1236932.6851 | 2606467.79 | 1236935.9425
84 | 2606490.2946 | 1236898.9297 | 2606488.4193 | 1236899.8131
85 | 2606467.79 | 1236935.9425 | 2606459.6267 | 1236939.0535
86 | 2606430.5773 | 1236950.1244 | 2606459.6267 | 1236939.0535
87 | 2606602.8829 | 1236766.9384 | 2606601.9289 | 1236767.3522
88 | 2606580.3264 | 1236777.753 | 2606587.1722 | 1236773.753 | 2606601.9289 | 1236767.3522
89 | 2606570.7441 | 1236783.3519 | 2606580.3264 | 1236777.753
90 | 2606570.7441 | 1236783.3519 | 2606553.7685 | 1236788.5921 | 2606548.34 | 1236789.6956
91 | 2606548.34 | 1236789.6956 | 2606529.0157 | 1236793.6238 | 2606525.8055 | 1236794.4188
92 | 2606366.4587 | 1236865.6599 | 2606372.0018 | 1236860.874 | 2606399.8343 | 1236850.9563
93 | 2606366.4587 | 1236865.6599 | 2606358.5991 | 1236864.7066 | 2606357.9178 | 1236864.9859
94 | 2606399.8343 | 1236850.9563 | 2606420.831 | 1236843.4744
95 | 2606350.0362 | 1236868.2169 | 2606357.9178 | 1236864.9859
96 | 2606458.3252 | 1236828.2851 | 2606421.9916 | 1236843.0608 | 2606420.831 | 1236843.4744
97 | 2606350.0362 | 1236868.2169 | 2606327.432 | 1236877.4833
98 | 2606305.7686 | 1236886.3641 | 2606327.432 | 1236877.4833
99 | 2606276.3767 | 1236751.4641 | 2606257.4037 | 1236758.8103
100 | 2606236.031 | 1236767.0857 | 2606257.4037 | 1236758.8103
101 | 2606236.031 | 1236767.0857 | 2606226.8452 | 1236770.6424
102 | 2606215.3508 | 1236775.0929 | 2606226.8452 | 1236770.6424
103 | 2606181.4834 | 1236788.2062 | 2606215.3508 | 1236775.0929
104 | 2606402.5757 | 1236789.8269 | 2606399.0327 | 1236790.8933 | 2606399.0327 | 1236790.8933
105 | 2606386.8814 | 1236799.1657 | 2606394.0501 | 1236797.2573
106 | 2606575.6297 | 1236887.1979 | 2606662.077 | 1236873.4551
107 | 2606043.489 | 1236838.0983 | 2606045.9891 | 1236837.2827
108 | 2606043.489 | 1236838.0983 | 2606040.825 | 1236816.4156 | 2606040.3338 | 1236805.0494
109 | 2606051.5888 | 1236835.4562 | 2606045.9891 | 1236837.2827
110 | 2606181.4834 | 1236788.2062 | 2606051.5888 | 1236835.4562
111 | 2606570.4922 | 1236820.8337 | 2606570.3996 | 1236818.4627
112 | 2606501.099 | 1236805.828 | 2606512.3346 | 1236799.4426 | 2606519.942 | 1236795.8709 | 2606525.8055 | 1236794.4188
113 | 2606570.4922 | 1236820.8337 | 2606571.0699 | 1236835.6197
114 | 2606333.9141 | 1236803.3164 | 2606340.4515 | 1236805.2732 | 2606349.6348 | 1236806.6838 | 2606359.4779 | 1236806.4608 | 2606361.0076 | 1236806.0535
115 | 2606333.9141 | 1236803.3164 | 2606332.1395 | 1236802.7852 | 2606322.3058 | 1236798.6657
116 | 2606361.0076 | 1236806.0535 | 2606367.4885 | 1236804.3283
117 | 2606305.9587 | 1236791.8176 | 2606322.3058 | 1236798.6657
118 | 2606386.8814 | 1236799.1657 | 2606367.4885 | 1236804.3283
119 | 2606244.7747 | 1236898.2606 | 2606269.5464 | 1236894.7281
120 | 2606274.7872 | 1236893.9807 | 2606277.2814 | 1236910.0263
121 | 2606278.958 | 1236920.8126 | 2606277.2814 | 1236910.0263
122 | 2606274.7872 | 1236893.9807 | 2606269.5464 | 1236894.7281
123 | 2606274.7872 | 1236893.9807 | 2606293.6858 | 1236889.3346
124 | 2606305.7686 | 1236886.3641 | 2606293.6858 | 1236889.3346
125 | 2606305.7686 | 1236886.3641 | 2606312.048 | 1236900.6794 | 2606311.6586 | 1236906.2755
126 | 2606311.5223 | 1236908.2342 | 2606311.6586 | 1236906.2755

## bus_geodata
| x | y | coords
0 | 2606513.9133 | 1236834.8306
1 | 2606517.4137 | 1236832.753
2 | 2606500.0726 | 1236843.0453
3 | 2606534.5769 | 1236822.947
4 | 2606491.0314 | 1236848.4114
5 | 2606561.4598 | 1236813.4826
6 | 2606481.6454 | 1236853.9822
7 | 2606570.0864 | 1236810.4456
8 | 2606477.3419 | 1236856.5365
9 | 2606425.1171 | 1236877.0293
10 | 2606422.838 | 1236877.8992
11 | 2606434.7218 | 1236873.3633
12 | 2606404.9573 | 1236884.7239
13 | 2606443.8649 | 1236869.8736
14 | 2606396.9699 | 1236887.7725
15 | 2606451.2127 | 1236867.0691
16 | 2606430.8276 | 1236917.0392
17 | 2606386.7634 | 1236880.3755
18 | 2606462.6663 | 1236862.6975
19 | 2606531.6633 | 1236903.4743
20 | 2606531.0447 | 1236902.1563
21 | 2606535.4315 | 1236911.5029
22 | 2606522.4263 | 1236883.794
23 | 2606512.7316 | 1236888.3607
24 | 2606500.2007 | 1236894.2634
25 | 2606572.1691 | 1236863.7582
26 | 2606571.4675 | 1236845.7974
27 | 2606572.9184 | 1236870.0034
28 | 2606575.191 | 1236741.5491
29 | 2606591.0846 | 1236710.9077
30 | 2606546.5303 | 1236728.8085
31 | 2606517.6975 | 1236741.3799
32 | 2606510.8523 | 1236745.7541
33 | 2606623.5917 | 1236759.3005
34 | 2606622.8305 | 1236759.5584
35 | 2606199.3547 | 1236936.5654
36 | 2606209.0394 | 1236912.1446
37 | 2606215.403 | 1236896.0981
38 | 2606274.4953 | 1236847.5743
39 | 2606224.3951 | 1236900.5088
40 | 2606008.0302 | 1236848.4358
41 | 2606027.4465 | 1236842.7752
42 | 2606244.7469 | 1236830.0358
43 | 2606282.7378 | 1236832.9676
44 | 2606242.6667 | 1236898.5612
45 | 2606311.5712 | 1236699.1528
46 | 2606321.4312 | 1236719.3228
47 | 2606334.4977 | 1236705.416
48 | 2606309.6008 | 1236738.6
49 | 2606292.2701 | 1236745.3103
50 | 2606330.703 | 1236744.5036
51 | 2606276.9452 | 1236751.244
52 | 2606345.808 | 1236729.1912
53 | 2606325.2109 | 1236758.1776
54 | 2606393.3707 | 1236735.0166
55 | 2606383.9406 | 1236729.1293
56 | 2606427.1661 | 1236737.5018
57 | 2606372.7352 | 1236721.2639
58 | 2606428.9038 | 1236751.7938
59 | 2606361.4454 | 1236713.3392
60 | 2606428.9674 | 1236752.2174
61 | 2606484.0123 | 1236747.1466
62 | 2606491.8009 | 1236757.9283
63 | 2606422.0711 | 1236783.959
64 | 2606502.2332 | 1236751.2618
65 | 2606470.8091 | 1236769.2635
66 | 2606452.7475 | 1236778.0696
67 | 2606447.6091 | 1236780.4315
68 | 2606426.019 | 1236788.7416
69 | 2606396.6661 | 1236796.5609
70 | 2606470.7434 | 1236859.6146
71 | 2606466.4477 | 1236909.618
72 | 2606455.7453 | 1236913.4525
73 | 2606471.2798 | 1236907.8867
74 | 2606488.4193 | 1236899.8131
75 | 2606467.79 | 1236935.9425
76 | 2606490.2946 | 1236898.9297
77 | 2606459.6267 | 1236939.0535
78 | 2606430.5773 | 1236950.1244
79 | 2606602.8829 | 1236766.9384
80 | 2606601.9289 | 1236767.3522
81 | 2606580.3264 | 1236777.753
82 | 2606570.7441 | 1236783.3519
83 | 2606548.34 | 1236789.6956
84 | 2606366.4587 | 1236865.6599
85 | 2606399.8343 | 1236850.9563
86 | 2606357.9178 | 1236864.9859
87 | 2606420.831 | 1236843.4744
88 | 2606350.0362 | 1236868.2169
89 | 2606458.3252 | 1236828.2851
90 | 2606327.432 | 1236877.4833
91 | 2606276.3767 | 1236751.4641
92 | 2606257.4037 | 1236758.8103
93 | 2606236.031 | 1236767.0857
94 | 2606226.8452 | 1236770.6424
95 | 2606215.3508 | 1236775.0929
96 | 2606402.5757 | 1236789.8269
97 | 2606399.0327 | 1236790.8933
98 | 2606394.0501 | 1236797.2573
99 | 2606662.077 | 1236873.4551
100 | 2606575.6297 | 1236887.1979
101 | 2606043.489 | 1236838.0983
102 | 2606045.9891 | 1236837.2827
103 | 2606040.3338 | 1236805.0494
104 | 2606181.4834 | 1236788.2062
105 | 2606051.5888 | 1236835.4562
106 | 2606570.3996 | 1236818.4627
107 | 2606501.099 | 1236805.828
108 | 2606525.8055 | 1236794.4188
109 | 2606570.4922 | 1236820.8337
110 | 2606333.9141 | 1236803.3164
111 | 2606361.0076 | 1236806.0535
112 | 2606322.3058 | 1236798.6657
113 | 2606367.4885 | 1236804.3283
114 | 2606305.9587 | 1236791.8176
115 | 2606386.8814 | 1236799.1657
116 | 2606571.0699 | 1236835.6197
117 | 2606242.2099 | 1236828.5401
118 | 2606246.5283 | 1236924.5922
119 | 2606244.7746 | 1236898.2606
120 | 2606277.2814 | 1236910.0263
121 | 2606274.7872 | 1236893.9807
122 | 2606278.958 | 1236920.8126
123 | 2606269.5464 | 1236894.7281
124 | 2606293.6858 | 1236889.3346
125 | 2606305.7686 | 1236886.3641
126 | 2606311.6586 | 1236906.2755
127 | 2606311.5223 | 1236908.2342
128 | 2606366.4587 | 1236865.6599

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98053 | -0.13643 | 0.0023464 | 0.00058807
1 | 0.98033 | -0.1379 | 0.001777 | 0.00044535
2 | 0.9814 | -0.13026 | 0.0021267 | 0.00053299
3 | 0.97938 | -0.14466 | 0.0027134 | 0.00068004
4 | 0.982 | -0.126 | 0.0018131 | 0.00045441
5 | 0.97813 | -0.1536 | 0.0020609 | 0.00051652
6 | 0.98265 | -0.12139 | 0.0019259 | 0.00048269
7 | 0.97776 | -0.15628 | 0 | 0
8 | 0.98296 | -0.11917 | 0.0018864 | 0.00047278
9 | 0.98698 | -0.090737 | 0.0026392 | 0.00066146
10 | 0.98718 | -0.089351 | 0.0016798 | 0.000421
11 | 0.98619 | -0.096307 | 0.0011936 | 0.00029914
12 | 0.98877 | -0.078164 | 0.0012095 | 0.00030312
13 | 0.98546 | -0.1015 | 0.0015379 | 0.00038545
14 | 0.98949 | -0.073073 | 0 | 0
15 | 0.98488 | -0.10555 | 0.0018584 | 0.00046577
16 | 0.98718 | -0.089405 | 0.0034176 | 0.00085653
17 | 0.99121 | -0.061017 | 0.0017931 | 0.0004494
18 | 0.98402 | -0.11164 | 0.0016545 | 0.00041466
19 | 0.98397 | -0.1122 | 0.0030359 | 0.00076087
20 | 0.98398 | -0.11212 | 0.0021291 | 0.00053361
21 | 0.98395 | -0.11239 | 0.0020826 | 0.00052195
22 | 0.9842 | -0.11061 | 0 | 0
23 | 0.98431 | -0.10981 | 0.0028385 | 0.0007114
24 | 0.98451 | -0.10837 | 0.0031247 | 0.00078312
25 | 0.97711 | -0.16089 | 0 | 0
26 | 0.97721 | -0.16017 | 0.0038095 | 0.00095475
27 | 0.97708 | -0.16114 | 0.00090917 | 0.00022786
28 | 0.97794 | -0.15502 | 0.0021815 | 0.00054673
29 | 0.97806 | -0.15414 | 0 | 0
30 | 0.97821 | -0.15303 | 0.0023669 | 0.00059321
31 | 0.97842 | -0.15153 | 0.0022963 | 0.00057551
32 | 0.9785 | -0.15095 | 0.0018358 | 0.0004601
33 | 0.97669 | -0.16392 | 0.0013243 | 0.00033191
34 | 0.97669 | -0.16391 | 0.0019824 | 0.00049683
35 | 0.98856 | -0.079649 | 0.0016342 | 0.00040957
36 | 0.98862 | -0.07921 | 0.00071224 | 0.0001785
37 | 0.98868 | -0.078796 | 0 | 0
38 | 0.98611 | -0.09689 | 0 | 0
39 | 0.98902 | -0.076386 | 0.0019275 | 0.00048308
40 | 0.97228 | -0.19557 | 0.0011717 | 0.00029365
41 | 0.97232 | -0.19532 | 0.0012146 | 0.00030441
42 | 0.98607 | -0.097132 | 0.00022747 | 5.7009e-05
43 | 0.98557 | -0.10072 | 0.0011668 | 0.00029242
44 | 0.98966 | -0.071902 | 0 | 0
45 | 0.97561 | -0.17159 | 0.0011878 | 0.00029769
46 | 0.97565 | -0.1713 | 0 | 0
47 | 0.9756 | -0.17168 | 0.0018694 | 0.00046853
48 | 0.97576 | -0.17056 | 0 | 0
49 | 0.97517 | -0.17474 | 0.0018616 | 0.00046655
50 | 0.97654 | -0.16491 | 0 | 0
51 | 0.9747 | -0.17811 | 0.0022056 | 0.00055277
52 | 0.97737 | -0.15902 | 0.0013415 | 0.00033621
53 | 0.97651 | -0.16517 | 0.0016778 | 0.0004205
54 | 0.97928 | -0.1454 | 0.001166 | 0.00029223
55 | 0.97911 | -0.14657 | 0.00091191 | 0.00022855
56 | 0.9798 | -0.14164 | 0 | 0
57 | 0.97882 | -0.14867 | 0.0019072 | 0.00047798
58 | 0.98002 | -0.14007 | 0.0010696 | 0.00026806
59 | 0.97826 | -0.15263 | 0 | 0
60 | 0.98003 | -0.14002 | 0.0015719 | 0.00039395
61 | 0.9788 | -0.14882 | 0.0010833 | 0.0002715
62 | 0.97882 | -0.14866 | 0 | 0
63 | 0.98067 | -0.13545 | 0.001406 | 0.00035237
64 | 0.97863 | -0.15002 | 0.0018169 | 0.00045536
65 | 0.97923 | -0.14578 | 0.0025232 | 0.00063238
66 | 0.97964 | -0.14283 | 0.0015305 | 0.00038357
67 | 0.97977 | -0.14191 | 0.0015122 | 0.000379
68 | 0.98035 | -0.13777 | 0.0021892 | 0.00054866
69 | 0.9812 | -0.13167 | 0 | 0
70 | 0.98344 | -0.1158 | 0.0018678 | 0.00046811
71 | 0.98547 | -0.10155 | 0.0019191 | 0.00048096
72 | 0.98596 | -0.09807 | 0.0024045 | 0.00060263
73 | 0.98526 | -0.10302 | 0 | 0
74 | 0.98477 | -0.10655 | 0.0029886 | 0.000749
75 | 0.98476 | -0.10658 | 0.0026377 | 0.00066107
76 | 0.98472 | -0.10688 | 0.0019283 | 0.00048328
77 | 0.98467 | -0.10722 | 0.0039901 | 0.001
78 | 0.98453 | -0.10821 | 0.0031009 | 0.00077716
79 | 0.9768 | -0.16318 | 0.0023582 | 0.00059101
80 | 0.9768 | -0.16311 | 0.0016295 | 0.0004084
81 | 0.97706 | -0.16128 | 0.0019268 | 0.0004829
82 | 0.97721 | -0.16021 | 0 | 0
83 | 0.97705 | -0.16134 | 0.0018237 | 0.00045707
84 | 0.9947 | -0.036701 | 0 | 0
85 | 0.99799 | -0.013861 | 0.00169 | 0.00042356
86 | 0.99433 | -0.039294 | 0.001553 | 0.00038921
87 | 1 | 0 | -0.19229 | -0.048395
88 | 0.99397 | -0.041802 | 0.0021305 | 0.00053395
89 | 0.99989 | -0.00077263 | 0.0019114 | 0.00047905
90 | 0.99296 | -0.048831 | 0.0029072 | 0.00072861
91 | 0.97469 | -0.17823 | 0.0043615 | 0.0010931
92 | 0.9743 | -0.181 | 0.0023575 | 0.00059084
93 | 0.97395 | -0.18357 | 0.0015949 | 0.00039972
94 | 0.97382 | -0.1845 | 0.0020515 | 0.00051417
95 | 0.97369 | -0.18541 | 0.0015471 | 0.00038774
96 | 0.98102 | -0.13295 | 0.0015573 | 0.00039029
97 | 0.98109 | -0.13247 | 0.00090807 | 0.00022758
98 | 0.98128 | -0.13113 | 0.0011976 | 0.00030014
99 | 0.97692 | -0.1623 | 0.00068387 | 0.00017139
100 | 0.97701 | -0.16167 | 0.0022258 | 0.00055784
101 | 0.97238 | -0.1949 | 0 | 0
102 | 0.97239 | -0.19477 | 0.00012305 | 3.0839e-05
103 | 0.97227 | -0.19566 | 0.0021501 | 0.00053887
104 | 0.9734 | -0.18749 | 0.00062779 | 0.00015734
105 | 0.97243 | -0.19448 | 0.00012661 | 3.173e-05
106 | 0.97759 | -0.15747 | 0.0024378 | 0.00061097
107 | 0.9769 | -0.16246 | 0.0015126 | 0.00037909
108 | 0.97696 | -0.16203 | 0.0013121 | 0.00032885
109 | 0.97755 | -0.15776 | 0.0014241 | 0.00035692
110 | 0.98311 | -0.11813 | 0.0016863 | 0.00042263
111 | 0.98227 | -0.12407 | 0.00091188 | 0.00022854
112 | 0.9835 | -0.11536 | 0.0013373 | 0.00033515
113 | 0.98207 | -0.12549 | 0.0019705 | 0.00049385
114 | 0.98406 | -0.11136 | 0 | 0
115 | 0.98149 | -0.12963 | 0.0010789 | 0.00027039
116 | 0.97733 | -0.15935 | 0.0026762 | 0.00067072
117 | 0.98607 | -0.097146 | 0.00045575 | 0.00011422
118 | 0.98961 | -0.072227 | 0.0012117 | 0.00030368
119 | 0.98974 | -0.071374 | 0.00029053 | 7.2813e-05
120 | 0.9907 | -0.06461 | 0.0012466 | 0.00031243
121 | 0.99081 | -0.063828 | 0 | 0
122 | 0.99065 | -0.064998 | 0.0034931 | 0.00087544
123 | 0.99062 | -0.065149 | 0.00034687 | 8.6935e-05
124 | 0.99155 | -0.05866 | 0.00022919 | 5.7439e-05
125 | 0.99202 | -0.055351 | 0 | 0
126 | 0.99191 | -0.056168 | 0.0016057 | 0.00040242
127 | 0.9919 | -0.056212 | 0.0021885 | 0.0005485
128 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.034692 | 0.0087038 | -0.034685 | -0.0087012 | 7.0412e-06 | 2.6568e-06 | 0.05265 | 0.05265 | 0.05265 | 0.98053 | -0.13643 | 0.98033 | -0.1379 | 19.5002
1 | -0.037038 | -0.0092919 | 0.03707 | 0.0093039 | 3.1733e-05 | 1.2002e-05 | 0.056211 | 0.056211 | 0.056211 | 0.98053 | -0.13643 | 0.9814 | -0.13026 | 20.819
2 | 0.032908 | 0.0082558 | -0.032877 | -0.0082442 | 3.0825e-05 | 1.1606e-05 | 0.049953 | 0.049953 | 0.049953 | 0.98033 | -0.1379 | 0.97938 | -0.14466 | 18.5012
3 | -0.039197 | -0.0098369 | 0.03922 | 0.0098457 | 2.3176e-05 | 8.7809e-06 | 0.059436 | 0.059436 | 0.059436 | 0.9814 | -0.13026 | 0.982 | -0.126 | 22.0132
4 | 0.030164 | 0.0075642 | -0.030126 | -0.0075502 | 3.7355e-05 | 1.4009e-05 | 0.045831 | 0.045831 | 0.045831 | 0.97938 | -0.14466 | 0.97813 | -0.1536 | 16.9744
5 | -0.041033 | -0.0103 | 0.04106 | 0.01031 | 2.6335e-05 | 9.9908e-06 | 0.062183 | 0.062183 | 0.062183 | 0.982 | -0.126 | 0.98265 | -0.12139 | 23.0308
6 | 0.028065 | 0.0070336 | -0.028055 | -0.0070298 | 1.0403e-05 | 3.8864e-06 | 0.042696 | 0.042696 | 0.042696 | 0.97813 | -0.1536 | 0.97776 | -0.15628 | 15.8132
7 | -0.042985 | -0.010793 | 0.042999 | 0.010798 | 1.3234e-05 | 5.0267e-06 | 0.065099 | 0.065099 | 0.065099 | 0.98265 | -0.12139 | 0.98296 | -0.11917 | 24.1109
8 | 0.014173 | 0.003551 | -0.014171 | -0.0035502 | 2.3292e-06 | 7.9524e-07 | 0.021569 | 0.021569 | 0.021569 | 0.97776 | -0.15628 | 0.97759 | -0.15747 | 7.9886
9 | 0.013882 | 0.0034788 | -0.013874 | -0.0034762 | 7.5489e-06 | 2.5636e-06 | 0.021126 | 0.021126 | 0.021126 | 0.97776 | -0.15628 | 0.97721 | -0.16021 | 7.8246
10 | -0.044885 | -0.011271 | 0.044906 | 0.011279 | 2.1056e-05 | 8.0058e-06 | 0.067955 | 0.067955 | 0.067955 | 0.98296 | -0.11917 | 0.98344 | -0.1158 | 25.1685
11 | -0.055833 | -0.01404 | 0.055844 | 0.014044 | 1.079e-05 | 4.1188e-06 | 0.084193 | 0.084193 | 0.084193 | 0.98698 | -0.090737 | 0.98718 | -0.089351 | 31.1825
12 | 0.053194 | 0.013379 | -0.053152 | -0.013363 | 4.1276e-05 | 1.5744e-05 | 0.080214 | 0.080214 | 0.080214 | 0.98698 | -0.090737 | 0.98619 | -0.096307 | 29.7088
13 | -0.057524 | -0.014465 | 0.057613 | 0.014499 | 8.9823e-05 | 3.4302e-05 | 0.086725 | 0.086725 | 0.086725 | 0.98718 | -0.089351 | 0.98877 | -0.078164 | 32.1203
14 | 0.051959 | 0.013064 | -0.051921 | -0.013049 | 3.7548e-05 | 1.4317e-05 | 0.078413 | 0.078413 | 0.078413 | 0.98619 | -0.096307 | 0.98546 | -0.1015 | 29.0418
15 | -0.058823 | -0.014803 | 0.058865 | 0.014818 | 4.1826e-05 | 1.5977e-05 | 0.088545 | 0.088545 | 0.088545 | 0.98877 | -0.078164 | 0.98949 | -0.073073 | 32.7944
16 | 0.050383 | 0.012664 | -0.050355 | -0.012653 | 2.8414e-05 | 1.0828e-05 | 0.076091 | 0.076091 | 0.076091 | 0.98546 | -0.1015 | 0.98488 | -0.10555 | 28.1817
17 | 0.03576 | 0.0089808 | -0.035679 | -0.0089503 | 8.1001e-05 | 3.0579e-05 | 0.053783 | 0.053783 | 0.053783 | 0.98949 | -0.073073 | 0.98718 | -0.089405 | 19.9196
18 | -0.094625 | -0.023799 | 0.094784 | 0.02386 | 0.00015933 | 6.112e-05 | 0.14233 | 0.14233 | 0.14233 | 0.98949 | -0.073073 | 0.99121 | -0.061017 | 52.714
19 | 0.048497 | 0.012187 | -0.048455 | -0.012172 | 4.1083e-05 | 1.5645e-05 | 0.073283 | 0.073283 | 0.073283 | 0.98488 | -0.10555 | 0.98402 | -0.11164 | 27.1418
20 | 0.032261 | 0.0080937 | -0.032223 | -0.0080792 | 3.8732e-05 | 1.4562e-05 | 0.048632 | 0.048632 | 0.048632 | 0.98718 | -0.089405 | 0.98596 | -0.09807 | 18.0117
21 | -0.096577 | -0.02431 | 0.096906 | 0.024436 | 0.00032908 | 0.00012625 | 0.14502 | 0.14502 | 0.14502 | 0.99121 | -0.061017 | 0.9947 | -0.036701 | 53.7109
22 | 0.046801 | 0.011757 | -0.046774 | -0.011747 | 2.7028e-05 | 1.0286e-05 | 0.070781 | 0.070781 | 0.070781 | 0.98402 | -0.11164 | 0.98344 | -0.1158 | 26.2152
23 | -0.0051186 | -0.0012827 | 0.0051186 | 0.0012827 | 5.4434e-08 | 2.4425e-09 | 0.0077405 | 0.0077405 | 0.0077405 | 0.98397 | -0.1122 | 0.98398 | -0.11212 | 2.8669
24 | 0.0020827 | 0.00052186 | -0.0020826 | -0.00052195 | 5.4896e-08 | -9.1538e-08 | 0.0031495 | 0.0031495 | 0.0031495 | 0.98397 | -0.1122 | 0.98395 | -0.11239 | 1.1665
25 | -0.0072477 | -0.0018163 | 0.0072493 | 0.0018167 | 1.5205e-06 | 3.2709e-07 | 0.01096 | 0.01096 | 0.01096 | 0.98398 | -0.11212 | 0.9842 | -0.11061 | 4.0594
26 | -0.0072493 | -0.0018167 | 0.0072501 | 0.0018168 | 8.0328e-07 | 1.7275e-07 | 0.01096 | 0.01096 | 0.01096 | 0.9842 | -0.11061 | 0.98431 | -0.10981 | 4.0593
27 | -0.010089 | -0.0025282 | 0.010091 | 0.0025288 | 2.0104e-06 | 5.9714e-07 | 0.015251 | 0.015251 | 0.015251 | 0.98431 | -0.10981 | 0.98451 | -0.10837 | 5.6486
28 | -0.013215 | -0.003312 | 0.013218 | 0.0033129 | 2.726e-06 | 9.092e-07 | 0.019974 | 0.019974 | 0.019974 | 0.98451 | -0.10837 | 0.98472 | -0.10688 | 7.3977
29 | -0.0038192 | -0.00095585 | 0.0038196 | 0.00095577 | 3.7935e-07 | -7.9261e-08 | 0.0058157 | 0.0058156 | 0.0058157 | 0.97711 | -0.16089 | 0.97721 | -0.16017 | 2.154
30 | 0.0038192 | 0.00095585 | -0.0038191 | -0.00095588 | 1.3275e-07 | -2.7725e-08 | 0.0058157 | 0.0058158 | 0.0058158 | 0.97711 | -0.16089 | 0.97708 | -0.16114 | 2.154
31 | -0.0076291 | -0.0019105 | 0.00763 | 0.0019107 | 8.5765e-07 | 2.0224e-07 | 0.011616 | 0.011616 | 0.011616 | 0.97721 | -0.16017 | 0.97733 | -0.15935 | 4.3024
32 | 0.0029099 | 0.00072802 | -0.0029097 | -0.00072816 | 2.1428e-07 | -1.3661e-07 | 0.0044312 | 0.0044312 | 0.0044312 | 0.97708 | -0.16114 | 0.97701 | -0.16167 | 1.6412
33 | -0.0021815 | -0.00054673 | 0.0021817 | 0.00054635 | 2.6566e-07 | -3.8273e-07 | 0.0033193 | 0.0033191 | 0.0033193 | 0.97794 | -0.15502 | 0.97806 | -0.15414 | 1.2294
34 | -0.0021817 | -0.00054635 | 0.0021821 | 0.00054587 | 3.3244e-07 | -4.7918e-07 | 0.0033191 | 0.0033189 | 0.0033191 | 0.97806 | -0.15414 | 0.97821 | -0.15303 | 1.2293
35 | -0.004549 | -0.0011391 | 0.00455 | 0.001139 | 9.4705e-07 | -3.3794e-08 | 0.0069194 | 0.0069193 | 0.0069194 | 0.97821 | -0.15303 | 0.97842 | -0.15153 | 2.5627
36 | -0.0068463 | -0.0017146 | 0.0068468 | 0.0017147 | 5.4948e-07 | 1.0931e-07 | 0.010412 | 0.010412 | 0.010412 | 0.97842 | -0.15153 | 0.9785 | -0.15095 | 3.8561
37 | -0.0086827 | -0.0021748 | 0.0086838 | 0.0021751 | 1.1127e-06 | 2.9945e-07 | 0.013203 | 0.013203 | 0.013203 | 0.9785 | -0.15095 | 0.97863 | -0.15002 | 4.8901
38 | -0.0013243 | -0.00033191 | 0.0013243 | 0.0003319 | 2.0413e-09 | -9.2722e-09 | 0.0020177 | 0.0020177 | 0.0020177 | 0.97669 | -0.16392 | 0.97669 | -0.16391 | 0.74729
39 | -0.0033067 | -0.00082874 | 0.0033071 | 0.0008286 | 3.3709e-07 | -1.3676e-07 | 0.0050379 | 0.0050378 | 0.0050379 | 0.97669 | -0.16391 | 0.9768 | -0.16318 | 1.8659
40 | -0.0016342 | -0.00040957 | 0.0016343 | 0.00040928 | 9.9191e-08 | -2.9869e-07 | 0.0024599 | 0.0024598 | 0.0024599 | 0.98856 | -0.079649 | 0.98862 | -0.07921 | 0.91107
41 | -0.0023466 | -0.00058778 | 0.0023467 | 0.00058761 | 1.3436e-07 | -1.6968e-07 | 0.0035318 | 0.0035317 | 0.0035318 | 0.98862 | -0.07921 | 0.98868 | -0.078796 | 1.3081
42 | 0.068059 | 0.01713 | -0.067888 | -0.017067 | 0.00017151 | 6.2951e-05 | 0.10246 | 0.10246 | 0.10246 | 0.98868 | -0.078796 | 0.98611 | -0.09689 | 12.6494
43 | -0.070406 | -0.017717 | 0.07043 | 0.017726 | 2.3688e-05 | 8.7208e-06 | 0.10599 | 0.10599 | 0.10599 | 0.98868 | -0.078796 | 0.98902 | -0.076386 | 13.0853
44 | 0.00068324 | 0.00017076 | -0.00068322 | -0.00017119 | 2.2902e-08 | -4.3173e-07 | 0.0010308 | 0.001031 | 0.001031 | 0.98611 | -0.09689 | 0.98607 | -0.097132 | 0.38185
45 | 0.067205 | 0.016896 | -0.067169 | -0.016883 | 3.589e-05 | 1.3162e-05 | 0.10143 | 0.10143 | 0.10143 | 0.98611 | -0.09689 | 0.98557 | -0.10072 | 12.5222
46 | -0.072357 | -0.018209 | 0.072403 | 0.018226 | 4.5318e-05 | 1.6722e-05 | 0.10889 | 0.10889 | 0.10889 | 0.98902 | -0.076386 | 0.98966 | -0.071902 | 13.4433
47 | -0.0011717 | -0.00029365 | 0.0011717 | 0.00029342 | 4.0579e-08 | -2.3523e-07 | 0.0017932 | 0.0017931 | 0.0017932 | 0.97228 | -0.19557 | 0.97232 | -0.19532 | 0.66415
48 | -0.0023863 | -0.00059783 | 0.0023865 | 0.00059768 | 1.3906e-07 | -1.5379e-07 | 0.0036519 | 0.0036519 | 0.0036519 | 0.97232 | -0.19532 | 0.97238 | -0.1949 | 1.3526
49 | 0.00045575 | 0.00011419 | -0.00045575 | -0.00011422 | 8.6924e-10 | -3.7235e-08 | 0.00068773 | 0.00068775 | 0.00068775 | 0.98607 | -0.097132 | 0.98607 | -0.097146 | 0.25472
50 | 0.066002 | 0.01659 | -0.065904 | -0.016555 | 9.7628e-05 | 3.5746e-05 | 0.099668 | 0.099669 | 0.099669 | 0.98557 | -0.10072 | 0.98406 | -0.11136 | 12.3048
51 | 0.0012118 | 0.00030337 | -0.0012117 | -0.00030368 | 5.4512e-08 | -3.1719e-07 | 0.0018218 | 0.001822 | 0.001822 | 0.98966 | -0.071902 | 0.98961 | -0.072227 | 0.6748
52 | -0.073614 | -0.018529 | 0.07362 | 0.018531 | 5.4286e-06 | 2.0058e-06 | 0.11071 | 0.11071 | 0.11071 | 0.98966 | -0.071902 | 0.98974 | -0.071374 | 13.6682
53 | -0.0011878 | -0.00029769 | 0.0011878 | 0.00029742 | 4.6311e-08 | -2.6459e-07 | 0.0018116 | 0.0018115 | 0.0018116 | 0.97561 | -0.17159 | 0.97565 | -0.1713 | 0.67098
54 | 0.0018695 | 0.00046833 | -0.0018694 | -0.00046853 | 9.6805e-08 | -2.0106e-07 | 0.0028513 | 0.0028513 | 0.0028513 | 0.97565 | -0.1713 | 0.9756 | -0.17168 | 1.0561
55 | -0.0030574 | -0.00076575 | 0.0030577 | 0.00076558 | 3.131e-07 | -1.6782e-07 | 0.0046628 | 0.0046627 | 0.0046628 | 0.97565 | -0.1713 | 0.97576 | -0.17056 | 1.727
56 | 0.021433 | 0.0053725 | -0.021421 | -0.0053679 | 1.2389e-05 | 4.533e-06 | 0.032685 | 0.032685 | 0.032685 | 0.97576 | -0.17056 | 0.97517 | -0.17474 | 12.1057
57 | -0.024491 | -0.0061381 | 0.02451 | 0.0061452 | 1.9183e-05 | 7.1027e-06 | 0.037348 | 0.037348 | 0.037348 | 0.97576 | -0.17056 | 0.97654 | -0.16491 | 13.8326
58 | 0.019559 | 0.0049014 | -0.01955 | -0.0048981 | 9.1338e-06 | 3.3081e-06 | 0.029845 | 0.029845 | 0.029845 | 0.97517 | -0.17474 | 0.9747 | -0.17811 | 11.0536
59 | -0.026188 | -0.0065655 | 0.026209 | 0.0065734 | 2.1372e-05 | 7.9506e-06 | 0.039904 | 0.039904 | 0.039904 | 0.97654 | -0.16491 | 0.97737 | -0.15902 | 14.7794
60 | 0.0016779 | 0.00042034 | -0.0016778 | -0.0004205 | 6.0185e-08 | -1.6146e-07 | 0.0025566 | 0.0025567 | 0.0025567 | 0.97654 | -0.16491 | 0.97651 | -0.16517 | 0.94691
61 | 0.017344 | 0.0043453 | -0.017344 | -0.0043452 | 2.6671e-07 | 9.4983e-08 | 0.026478 | 0.026478 | 0.026478 | 0.9747 | -0.17811 | 0.97469 | -0.17823 | 9.8066
62 | -0.02755 | -0.0069097 | 0.027575 | 0.0069188 | 2.4448e-05 | 9.1236e-06 | 0.041947 | 0.041947 | 0.041947 | 0.97737 | -0.15902 | 0.97826 | -0.15263 | 15.5358
63 | 0.030423 | 0.0076354 | -0.030418 | -0.0076339 | 4.9762e-06 | 1.4915e-06 | 0.046231 | 0.046232 | 0.046232 | 0.97928 | -0.1454 | 0.97911 | -0.14657 | 5.7076
64 | -0.031589 | -0.0079276 | 0.031605 | 0.0079327 | 1.6478e-05 | 5.0394e-06 | 0.048003 | 0.048003 | 0.048003 | 0.97928 | -0.1454 | 0.9798 | -0.14164 | 5.9263
65 | 0.029506 | 0.0074054 | -0.029497 | -0.0074024 | 8.5903e-06 | 2.9597e-06 | 0.044846 | 0.044846 | 0.044846 | 0.97911 | -0.14657 | 0.97882 | -0.14867 | 8.3048
66 | -0.031605 | -0.0079327 | 0.031612 | 0.0079348 | 6.9032e-06 | 2.1107e-06 | 0.048003 | 0.048003 | 0.048003 | 0.9798 | -0.14164 | 0.98002 | -0.14007 | 5.9263
67 | 0.02759 | 0.0069244 | -0.027575 | -0.0069188 | 1.5144e-05 | 5.6515e-06 | 0.041947 | 0.041947 | 0.041947 | 0.97882 | -0.14867 | 0.97826 | -0.15263 | 15.5358
68 | -0.032682 | -0.0082028 | 0.032682 | 0.0082029 | 2.1943e-07 | 6.8203e-08 | 0.049627 | 0.049627 | 0.049627 | 0.98002 | -0.14007 | 0.98003 | -0.14002 | 6.1267
69 | -0.034254 | -0.0085969 | 0.034275 | 0.0086037 | 2.1709e-05 | 6.8902e-06 | 0.052013 | 0.052013 | 0.052013 | 0.98003 | -0.14002 | 0.98067 | -0.13545 | 6.4214
70 | -0.0010833 | -0.0002715 | 0.0010833 | 0.00027134 | 2.3381e-08 | -1.6465e-07 | 0.0016469 | 0.0016468 | 0.0016469 | 0.9788 | -0.14882 | 0.97882 | -0.14866 | 0.60996
71 | 0.010503 | 0.002631 | -0.010501 | -0.0026304 | 1.9693e-06 | 6.0182e-07 | 0.015966 | 0.015966 | 0.015966 | 0.97882 | -0.14866 | 0.97863 | -0.15002 | 5.9133
72 | -0.011586 | -0.0029024 | 0.011591 | 0.0029038 | 4.6179e-06 | 1.4761e-06 | 0.017613 | 0.017613 | 0.017613 | 0.97882 | -0.14866 | 0.97923 | -0.14578 | 6.5232
73 | -0.035681 | -0.0089561 | 0.035694 | 0.0089601 | 1.2415e-05 | 4.0042e-06 | 0.054146 | 0.054146 | 0.054146 | 0.98067 | -0.13545 | 0.98102 | -0.13295 | 6.6847
74 | -0.014114 | -0.0035362 | 0.01412 | 0.0035382 | 5.7701e-06 | 1.9663e-06 | 0.021447 | 0.021447 | 0.021447 | 0.97923 | -0.14578 | 0.97964 | -0.14283 | 7.9433
75 | -0.01565 | -0.0039218 | 0.015652 | 0.0039225 | 1.9941e-06 | 6.9574e-07 | 0.023771 | 0.023771 | 0.023771 | 0.97964 | -0.14283 | 0.97977 | -0.14191 | 8.8042
76 | -0.017164 | -0.0043015 | 0.017174 | 0.004305 | 9.8431e-06 | 3.4933e-06 | 0.026068 | 0.026068 | 0.026068 | 0.97977 | -0.14191 | 0.98035 | -0.13777 | 9.6548
77 | -0.019363 | -0.0048536 | 0.01938 | 0.0048595 | 1.6374e-05 | 5.9142e-06 | 0.029391 | 0.029391 | 0.029391 | 0.98035 | -0.13777 | 0.9812 | -0.13167 | 10.8855
78 | -0.057546 | -0.01444 | 0.05755 | 0.014441 | 4.2891e-06 | 1.547e-06 | 0.087276 | 0.087275 | 0.087276 | 0.9812 | -0.13167 | 0.98128 | -0.13113 | 10.7748
79 | 0.038166 | 0.0095802 | -0.038162 | -0.0095788 | 4.2805e-06 | 1.4136e-06 | 0.057885 | 0.057885 | 0.057885 | 0.9812 | -0.13167 | 0.98109 | -0.13247 | 7.1463
80 | -0.029804 | -0.0074712 | 0.029818 | 0.0074765 | 1.4367e-05 | 5.3809e-06 | 0.045003 | 0.045003 | 0.045003 | 0.98547 | -0.10155 | 0.98596 | -0.09807 | 16.6677
81 | 0.027885 | 0.0069902 | -0.027879 | -0.0069881 | 5.6783e-06 | 2.1186e-06 | 0.042105 | 0.042105 | 0.042105 | 0.98547 | -0.10155 | 0.98526 | -0.10302 | 15.5945
82 | 0.018144 | 0.0045486 | -0.018136 | -0.0045454 | 8.8779e-06 | 3.1734e-06 | 0.027403 | 0.027404 | 0.027404 | 0.98526 | -0.10302 | 0.98477 | -0.10655 | 10.1494
83 | 0.0097345 | 0.0024395 | -0.0097297 | -0.0024381 | 4.795e-06 | 1.3917e-06 | 0.014702 | 0.014702 | 0.014702 | 0.98526 | -0.10302 | 0.98476 | -0.10658 | 5.4451
84 | 0.015147 | 0.0037964 | -0.015146 | -0.0037961 | 6.776e-07 | 2.3424e-07 | 0.022888 | 0.022888 | 0.022888 | 0.98477 | -0.10655 | 0.98472 | -0.10688 | 8.4769
85 | 0.007092 | 0.0017771 | -0.0070914 | -0.0017769 | 6.2601e-07 | 1.2964e-07 | 0.010716 | 0.010716 | 0.010716 | 0.98476 | -0.10658 | 0.98467 | -0.10722 | 3.969
86 | 0.0031013 | 0.00077693 | -0.0031009 | -0.00077716 | 4.2608e-07 | -2.3151e-07 | 0.0046866 | 0.0046867 | 0.0046867 | 0.98467 | -0.10722 | 0.98453 | -0.10821 | 1.7358
87 | -0.0056652 | -0.0014196 | 0.0056653 | 0.0014196 | 4.8328e-08 | 5.571e-09 | 0.0086301 | 0.0086301 | 0.0086301 | 0.9768 | -0.16318 | 0.9768 | -0.16311 | 3.1963
88 | -0.0072948 | -0.001828 | 0.0072967 | 0.0018284 | 1.8504e-06 | 4.1101e-07 | 0.011112 | 0.011112 | 0.011112 | 0.9768 | -0.16311 | 0.97706 | -0.16128 | 4.1157
89 | -0.0092234 | -0.0023113 | 0.0092248 | 0.0023117 | 1.3664e-06 | 3.8653e-07 | 0.014047 | 0.014047 | 0.014047 | 0.97706 | -0.16128 | 0.97721 | -0.16021 | 5.2025
90 | 0.0046495 | 0.0011645 | -0.0046488 | -0.0011645 | 7.2891e-07 | -1.1576e-08 | 0.0070797 | 0.0070798 | 0.0070798 | 0.97721 | -0.16021 | 0.97705 | -0.16134 | 2.6221
91 | 0.0028251 | 0.00070744 | -0.0028248 | -0.00070763 | 2.6596e-07 | -1.8607e-07 | 0.0043023 | 0.0043024 | 0.0043024 | 0.97705 | -0.16134 | 0.97696 | -0.16203 | 1.5935
92 | -0.18691 | -0.047122 | 0.18751 | 0.047352 | 0.00060001 | 0.00022933 | 0.27971 | 0.27971 | 0.27971 | 0.9947 | -0.036701 | 0.99799 | -0.013861 | 34.5324
93 | 0.090008 | 0.022686 | -0.089976 | -0.022674 | 3.2655e-05 | 1.2223e-05 | 0.13469 | 0.13469 | 0.13469 | 0.9947 | -0.036701 | 0.99433 | -0.039294 | 16.6288
94 | -0.1892 | -0.047775 | 0.18957 | 0.047916 | 0.0003693 | 0.00014116 | 0.28223 | 0.28223 | 0.28223 | 0.99799 | -0.013861 | 1 | 0 | 34.8434
95 | 0.088423 | 0.022285 | -0.088392 | -0.022273 | 3.1045e-05 | 1.1609e-05 | 0.13237 | 0.13237 | 0.13237 | 0.99433 | -0.039294 | 0.99397 | -0.041802 | 16.3419
96 | 0.0019116 | 0.00047859 | -0.0019114 | -0.00047905 | 2.0424e-07 | -4.5213e-07 | 0.0028443 | 0.0028445 | 0.0028445 | 1 | 0 | 0.99989 | -0.00077263 | 1.0535
97 | 0.086261 | 0.021739 | -0.086176 | -0.021708 | 8.4796e-05 | 3.1665e-05 | 0.12918 | 0.12918 | 0.12918 | 0.99397 | -0.041802 | 0.99296 | -0.048831 | 15.9482
98 | 0.083269 | 0.020979 | -0.083193 | -0.020951 | 7.5878e-05 | 2.8276e-05 | 0.12482 | 0.12482 | 0.12482 | 0.99296 | -0.048831 | 0.99202 | -0.055351 | 15.4104
99 | 0.012983 | 0.0032521 | -0.012978 | -0.0032505 | 4.9869e-06 | 1.6646e-06 | 0.019819 | 0.019819 | 0.019819 | 0.97469 | -0.17823 | 0.9743 | -0.181 | 7.3405
100 | 0.01062 | 0.0026596 | -0.010616 | -0.0026585 | 3.762e-06 | 1.1616e-06 | 0.016219 | 0.016219 | 0.016219 | 0.9743 | -0.181 | 0.97395 | -0.18357 | 6.007
101 | 0.0090214 | 0.0022587 | -0.0090202 | -0.0022584 | 1.1676e-06 | 3.2649e-07 | 0.013782 | 0.013782 | 0.013782 | 0.97395 | -0.18357 | 0.97382 | -0.1845 | 5.1046
102 | 0.0069687 | 0.0017443 | -0.0069678 | -0.0017441 | 8.7197e-07 | 1.8204e-07 | 0.010647 | 0.010648 | 0.010648 | 0.97382 | -0.1845 | 0.97369 | -0.18541 | 3.9435
103 | 0.0054207 | 0.0013563 | -0.0054192 | -0.0013562 | 1.5549e-06 | 1.4646e-07 | 0.0082832 | 0.0082834 | 0.0082834 | 0.97369 | -0.18541 | 0.9734 | -0.18749 | 3.0679
104 | -0.037251 | -0.0093504 | 0.037254 | 0.0093512 | 2.4575e-06 | 8.0501e-07 | 0.056508 | 0.056508 | 0.056508 | 0.98102 | -0.13295 | 0.98109 | -0.13247 | 6.9763
105 | -0.058747 | -0.014741 | 0.05876 | 0.014746 | 1.2247e-05 | 4.4293e-06 | 0.089091 | 0.089091 | 0.089091 | 0.98128 | -0.13113 | 0.98149 | -0.12963 | 10.9989
106 | -0.00068387 | -0.00017139 | 0.00068393 | 0.00017032 | 5.9243e-08 | -1.0733e-06 | 0.0010417 | 0.0010413 | 0.0010417 | 0.97692 | -0.1623 | 0.97701 | -0.16167 | 0.3858
107 | -0.0045368 | -0.0011362 | 0.0045369 | 0.0011362 | 7.9089e-08 | -2.2028e-09 | 0.0069423 | 0.0069423 | 0.0069423 | 0.97238 | -0.1949 | 0.97239 | -0.19477 | 2.5712
108 | 0.0021503 | 0.00053854 | -0.0021501 | -0.00053887 | 2.2447e-07 | -3.2573e-07 | 0.0032905 | 0.0032906 | 0.0032906 | 0.97238 | -0.1949 | 0.97227 | -0.19566 | 1.2188
109 | -0.0046599 | -0.0011671 | 0.0046601 | 0.0011671 | 1.8688e-07 | -1.1926e-09 | 0.0071306 | 0.0071306 | 0.0071306 | 0.97239 | -0.19477 | 0.97243 | -0.19448 | 2.641
110 | 0.0047914 | 0.0011988 | -0.0047867 | -0.0011988 | 4.6266e-06 | 6.2973e-08 | 0.0073237 | 0.0073243 | 0.0073243 | 0.9734 | -0.18749 | 0.97243 | -0.19448 | 2.7127
111 | 0.011733 | 0.0029392 | -0.011733 | -0.0029391 | 4.7222e-07 | 1.5188e-07 | 0.017859 | 0.017859 | 0.017859 | 0.97759 | -0.15747 | 0.97755 | -0.15776 | 6.6143
112 | -0.0015126 | -0.00037909 | 0.0015127 | 0.00037878 | 9.0649e-08 | -3.0781e-07 | 0.002304 | 0.0023039 | 0.002304 | 0.9769 | -0.16246 | 0.97696 | -0.16203 | 0.85333
113 | 0.010308 | 0.0025821 | -0.010306 | -0.0025814 | 2.2733e-06 | 6.8889e-07 | 0.015691 | 0.015691 | 0.015691 | 0.97755 | -0.15776 | 0.97733 | -0.15935 | 5.8115
114 | 0.062819 | 0.015774 | -0.062768 | -0.015756 | 5.1807e-05 | 1.8879e-05 | 0.095093 | 0.095094 | 0.095094 | 0.98311 | -0.11813 | 0.98227 | -0.12407 | 11.74
115 | -0.064506 | -0.016197 | 0.064531 | 0.016206 | 2.4818e-05 | 9.0692e-06 | 0.097646 | 0.097646 | 0.097646 | 0.98311 | -0.11813 | 0.9835 | -0.11536 | 12.055
116 | 0.061856 | 0.015527 | -0.061843 | -0.015523 | 1.2251e-05 | 4.4571e-06 | 0.093712 | 0.093712 | 0.093712 | 0.98227 | -0.12407 | 0.98207 | -0.12549 | 11.5694
117 | -0.065868 | -0.016541 | 0.065904 | 0.016555 | 3.6621e-05 | 1.341e-05 | 0.099669 | 0.099669 | 0.099669 | 0.9835 | -0.11536 | 0.98406 | -0.11136 | 12.3048
118 | 0.059873 | 0.015029 | -0.059839 | -0.015016 | 3.4359e-05 | 1.2454e-05 | 0.090727 | 0.090727 | 0.090727 | 0.98207 | -0.12549 | 0.98149 | -0.12963 | 11.2009
119 | -0.07391 | -0.018604 | 0.073975 | 0.018628 | 6.4299e-05 | 2.3765e-05 | 0.11115 | 0.11115 | 0.11115 | 0.98974 | -0.071374 | 0.99062 | -0.065149 | 13.7221
120 | -0.0047399 | -0.0011878 | 0.0047404 | 0.0011878 | 5.1354e-07 | -1.1598e-08 | 0.0071192 | 0.0071191 | 0.0071192 | 0.9907 | -0.06461 | 0.99081 | -0.063828 | 2.6367
121 | 0.0034932 | 0.00087537 | -0.0034931 | -0.00087544 | 1.8751e-07 | -6.843e-08 | 0.0052468 | 0.0052468 | 0.0052468 | 0.9907 | -0.06461 | 0.99065 | -0.064998 | 1.9433
122 | 0.074335 | 0.01872 | -0.074322 | -0.018715 | 1.3731e-05 | 5.0767e-06 | 0.11167 | 0.11167 | 0.11167 | 0.99081 | -0.063828 | 0.99062 | -0.065149 | 13.7864
123 | -0.079076 | -0.019908 | 0.079133 | 0.019929 | 5.712e-05 | 2.1217e-05 | 0.11879 | 0.11879 | 0.11879 | 0.99081 | -0.063828 | 0.99155 | -0.05866 | 14.6653
124 | -0.079362 | -0.019986 | 0.079399 | 0.02 | 3.6731e-05 | 1.3646e-05 | 0.11913 | 0.11913 | 0.11913 | 0.99155 | -0.05866 | 0.99202 | -0.055351 | 14.7077
125 | 0.0037947 | 0.00095079 | -0.0037942 | -0.0009509 | 4.2942e-07 | -1.0905e-07 | 0.0056918 | 0.0056919 | 0.0056919 | 0.99202 | -0.055351 | 0.99191 | -0.056168 | 2.1081
126 | 0.0021885 | 0.00054848 | -0.0021885 | -0.0005485 | 1.3206e-08 | -2.0264e-08 | 0.0032831 | 0.0032831 | 0.0032831 | 0.99191 | -0.056168 | 0.9919 | -0.056212 | 1.216

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.1944 | 0.048926

## res_load
| p_mw | q_mvar
0 | 0.0023464 | 0.00058807
1 | 0.001777 | 0.00044535
2 | 0.0021267 | 0.00053299
3 | 0.0027134 | 0.00068004
4 | 0.0018131 | 0.00045441
5 | 0.0020609 | 0.00051652
6 | 0.0019259 | 0.00048269
7 | 0.0018864 | 0.00047278
8 | 0.0026392 | 0.00066146
9 | 0.0016798 | 0.000421
10 | 0.0011936 | 0.00029914
11 | 0.0012095 | 0.00030312
12 | 0.0015379 | 0.00038545
13 | 0.0018584 | 0.00046577
14 | 0.0034176 | 0.00085653
15 | 0.0017931 | 0.0004494
16 | 0.0016545 | 0.00041466
17 | 0.0030359 | 0.00076087
18 | 0.0021291 | 0.00053361
19 | 0.0020826 | 0.00052195
20 | 0.0028385 | 0.0007114
21 | 0.0031247 | 0.00078312
22 | 0.0038095 | 0.00095475
23 | 0.00090917 | 0.00022786
24 | 0.0021815 | 0.00054673
25 | 0.0023669 | 0.00059321
26 | 0.0022963 | 0.00057551
27 | 0.0018358 | 0.0004601
28 | 0.0013243 | 0.00033191
29 | 0.0019824 | 0.00049683
30 | 0.0016342 | 0.00040957
31 | 0.00071224 | 0.0001785
32 | 0.0019275 | 0.00048308
33 | 0.0011717 | 0.00029365
34 | 0.0012146 | 0.00030441
35 | 0.00022747 | 5.7009e-05
36 | 0.0011668 | 0.00029242
37 | 0.0011878 | 0.00029769
38 | 0.0018694 | 0.00046853
39 | 0.0018616 | 0.00046655
40 | 0.0022056 | 0.00055277
41 | 0.0013415 | 0.00033621
42 | 0.0016778 | 0.0004205
43 | 0.001166 | 0.00029223
44 | 0.00091191 | 0.00022855
45 | 0.0019072 | 0.00047798
46 | 0.0010696 | 0.00026806
47 | 0.0015719 | 0.00039395
48 | 0.0010833 | 0.0002715
49 | 0.001406 | 0.00035237
50 | 0.0018169 | 0.00045536
51 | 0.0025232 | 0.00063238
52 | 0.0015305 | 0.00038357
53 | 0.0015122 | 0.000379
54 | 0.0021892 | 0.00054866
55 | 0.0018678 | 0.00046811
56 | 0.0019191 | 0.00048096
57 | 0.0024045 | 0.00060263
58 | 0.0029886 | 0.000749
59 | 0.0026377 | 0.00066107
60 | 0.0019283 | 0.00048328
61 | 0.0039901 | 0.001
62 | 0.0031009 | 0.00077716
63 | 0.0023582 | 0.00059101
64 | 0.0016295 | 0.0004084
65 | 0.0019268 | 0.0004829
66 | 0.0018237 | 0.00045707
67 | 0.00169 | 0.00042356
68 | 0.001553 | 0.00038921
69 | 0.0021166 | 0.00053047
70 | 0.0021305 | 0.00053395
71 | 0.0019114 | 0.00047905
72 | 0.0029072 | 0.00072861
73 | 0.0043615 | 0.0010931
74 | 0.0023575 | 0.00059084
75 | 0.0015949 | 0.00039972
76 | 0.0020515 | 0.00051417
77 | 0.0015471 | 0.00038774
78 | 0.0015573 | 0.00039029
79 | 0.00090807 | 0.00022758
80 | 0.0011976 | 0.00030014
81 | 0.00068387 | 0.00017139
82 | 0.0022258 | 0.00055784
83 | 0.00012305 | 3.0839e-05
84 | 0.0021501 | 0.00053887
85 | 0.00062779 | 0.00015734
86 | 0.00012661 | 3.173e-05
87 | 0.0024378 | 0.00061097
88 | 0.0015126 | 0.00037909
89 | 0.0013121 | 0.00032885
90 | 0.0014241 | 0.00035692
91 | 0.0016863 | 0.00042263
92 | 0.00091188 | 0.00022854
93 | 0.0013373 | 0.00033515
94 | 0.0019705 | 0.00049385
95 | 0.0010789 | 0.00027039
96 | 0.0026762 | 0.00067072
97 | 0.00045575 | 0.00011422
98 | 0.0012117 | 0.00030368
99 | 0.00029053 | 7.2813e-05
100 | 0.0012466 | 0.00031243
101 | 0.0034931 | 0.00087544
102 | 0.00034687 | 8.6935e-05
103 | 0.00022919 | 5.7439e-05
104 | 0.0016057 | 0.00040242
105 | 0.0021885 | 0.0005485

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1