## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2615-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2615-3_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2615-3_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2615-3_0_3_node_81 | 0.4 | n |  | TRUE
4 | bus_LV_2615-3_0_3_node_62 | 0.4 | n |  | TRUE
5 | bus_LV_2615-3_0_3_node_101 | 0.4 | n |  | TRUE
6 | bus_LV_2615-3_0_3_node_78 | 0.4 | n |  | TRUE
7 | bus_LV_2615-3_0_3_node_128 | 0.4 | n |  | TRUE
8 | bus_LV_2615-3_0_3_node_60 | 0.4 | n |  | TRUE
9 | bus_LV_2615-3_0_3_node_3 | 0.4 | n |  | TRUE
10 | bus_LV_2615-3_0_3_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_2615-3_0_3_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_2615-3_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2615-3_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2615-3_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2615-3_0_3_node_50 | 0.4 | n |  | TRUE
16 | bus_LV_2615-3_0_3_node_106 | 0.4 | n |  | TRUE
17 | bus_LV_2615-3_0_3_node_40 | 0.4 | n |  | TRUE
18 | bus_LV_2615-3_0_3_node_48 | 0.4 | n |  | TRUE
19 | bus_LV_2615-3_0_3_node_126 | 0.4 | n |  | TRUE
20 | bus_LV_2615-3_0_3_node_39 | 0.4 | n |  | TRUE
21 | bus_LV_2615-3_0_3_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_2615-3_0_3_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_2615-3_0_3_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_2615-3_0_3_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_2615-3_0_3_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2615-3_0_3_node_98 | 0.4 | n |  | TRUE
27 | bus_LV_2615-3_0_3_node_99 | 0.4 | n |  | TRUE
28 | bus_LV_2615-3_0_3_node_38 | 0.4 | n |  | TRUE
29 | bus_LV_2615-3_0_3_node_133 | 0.4 | n |  | TRUE
30 | bus_LV_2615-3_0_3_node_131 | 0.4 | n |  | TRUE
31 | bus_LV_2615-3_0_3_node_107 | 0.4 | n |  | TRUE
32 | bus_LV_2615-3_0_3_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_2615-3_0_3_node_36 | 0.4 | n |  | TRUE
34 | bus_LV_2615-3_0_3_node_14 | 0.4 | n |  | TRUE
35 | bus_LV_2615-3_0_3_node_15 | 0.4 | n |  | TRUE
36 | bus_LV_2615-3_0_3_node_16 | 0.4 | n |  | TRUE
37 | bus_LV_2615-3_0_3_node_18 | 0.4 | n |  | TRUE
38 | bus_LV_2615-3_0_3_node_19 | 0.4 | n |  | TRUE
39 | bus_LV_2615-3_0_3_node_71 | 0.4 | n |  | TRUE
40 | bus_LV_2615-3_0_3_node_69 | 0.4 | n |  | TRUE
41 | bus_LV_2615-3_0_3_node_93 | 0.4 | n |  | TRUE
42 | bus_LV_2615-3_0_3_node_109 | 0.4 | n |  | TRUE
43 | bus_LV_2615-3_0_3_node_70 | 0.4 | n |  | TRUE
44 | bus_LV_2615-3_0_3_node_94 | 0.4 | n |  | TRUE
45 | bus_LV_2615-3_0_3_node_20 | 0.4 | n |  | TRUE
46 | bus_LV_2615-3_0_3_node_21 | 0.4 | n |  | TRUE
47 | bus_LV_2615-3_0_3_node_22 | 0.4 | n |  | TRUE
48 | bus_LV_2615-3_0_3_node_23 | 0.4 | n |  | TRUE
49 | bus_LV_2615-3_0_3_node_24 | 0.4 | n |  | TRUE
50 | bus_LV_2615-3_0_3_node_25 | 0.4 | n |  | TRUE
51 | bus_LV_2615-3_0_3_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_2615-3_0_3_node_108 | 0.4 | n |  | TRUE
53 | bus_LV_2615-3_0_3_node_89 | 0.4 | n |  | TRUE
54 | bus_LV_2615-3_0_3_node_111 | 0.4 | n |  | TRUE
55 | bus_LV_2615-3_0_3_node_44 | 0.4 | n |  | TRUE
56 | bus_LV_2615-3_0_3_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_2615-3_0_3_node_88 | 0.4 | n |  | TRUE
58 | bus_LV_2615-3_0_3_node_26 | 0.4 | n |  | TRUE
59 | bus_LV_2615-3_0_3_node_27 | 0.4 | n |  | TRUE
60 | bus_LV_2615-3_0_3_node_28 | 0.4 | n |  | TRUE
61 | bus_LV_2615-3_0_3_node_29 | 0.4 | n |  | TRUE
62 | bus_LV_2615-3_0_3_node_130 | 0.4 | n |  | TRUE
63 | bus_LV_2615-3_0_3_node_85 | 0.4 | n |  | TRUE
64 | bus_LV_2615-3_0_3_node_30 | 0.4 | n |  | TRUE
65 | bus_LV_2615-3_0_3_node_31 | 0.4 | n |  | TRUE
66 | bus_LV_2615-3_0_3_node_32 | 0.4 | n |  | TRUE
67 | bus_LV_2615-3_0_3_node_33 | 0.4 | n |  | TRUE
68 | bus_LV_2615-3_0_3_node_34 | 0.4 | n |  | TRUE
69 | bus_LV_2615-3_0_3_node_127 | 0.4 | n |  | TRUE
70 | bus_LV_2615-3_0_3_node_52 | 0.4 | n |  | TRUE
71 | bus_LV_2615-3_0_3_node_47 | 0.4 | n |  | TRUE
72 | bus_LV_2615-3_0_3_node_37 | 0.4 | n |  | TRUE
73 | bus_LV_2615-3_0_3_node_82 | 0.4 | n |  | TRUE
74 | bus_LV_2615-3_0_3_node_129 | 0.4 | n |  | TRUE
75 | bus_LV_2615-3_0_3_node_83 | 0.4 | n |  | TRUE
76 | bus_LV_2615-3_0_3_node_42 | 0.4 | n |  | TRUE
77 | bus_LV_2615-3_0_3_node_41 | 0.4 | n |  | TRUE
78 | bus_LV_2615-3_0_3_node_43 | 0.4 | n |  | TRUE
79 | bus_LV_2615-3_0_3_node_45 | 0.4 | n |  | TRUE
80 | bus_LV_2615-3_0_3_node_49 | 0.4 | n |  | TRUE
81 | bus_LV_2615-3_0_3_node_53 | 0.4 | n |  | TRUE
82 | bus_LV_2615-3_0_3_node_54 | 0.4 | n |  | TRUE
83 | bus_LV_2615-3_0_3_node_132 | 0.4 | n |  | TRUE
84 | bus_LV_2615-3_0_3_node_55 | 0.4 | n |  | TRUE
85 | bus_LV_2615-3_0_3_node_97 | 0.4 | n |  | TRUE
86 | bus_LV_2615-3_0_3_node_96 | 0.4 | n |  | TRUE
87 | bus_LV_2615-3_0_3_node_56 | 0.4 | n |  | TRUE
88 | bus_LV_2615-3_0_3_node_57 | 0.4 | n |  | TRUE
89 | bus_LV_2615-3_0_3_node_58 | 0.4 | n |  | TRUE
90 | bus_LV_2615-3_0_3_node_91 | 0.4 | n |  | TRUE
91 | bus_LV_2615-3_0_3_node_92 | 0.4 | n |  | TRUE
92 | bus_LV_2615-3_0_3_node_118 | 0.4 | n |  | TRUE
93 | bus_LV_2615-3_0_3_node_119 | 0.4 | n |  | TRUE
94 | bus_LV_2615-3_0_3_node_120 | 0.4 | n |  | TRUE
95 | bus_LV_2615-3_0_3_node_59 | 0.4 | n |  | TRUE
96 | bus_LV_2615-3_0_3_node_63 | 0.4 | n |  | TRUE
97 | bus_LV_2615-3_0_3_node_87 | 0.4 | n |  | TRUE
98 | bus_LV_2615-3_0_3_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_2615-3_0_3_node_64 | 0.4 | n |  | TRUE
100 | bus_LV_2615-3_0_3_node_105 | 0.4 | n |  | TRUE
101 | bus_LV_2615-3_0_3_node_103 | 0.4 | n |  | TRUE
102 | bus_LV_2615-3_0_3_node_90 | 0.4 | n |  | TRUE
103 | bus_LV_2615-3_0_3_node_112 | 0.4 | n |  | TRUE
104 | bus_LV_2615-3_0_3_node_104 | 0.4 | n |  | TRUE
105 | bus_LV_2615-3_0_3_node_65 | 0.4 | n |  | TRUE
106 | bus_LV_2615-3_0_3_node_66 | 0.4 | n |  | TRUE
107 | bus_LV_2615-3_0_3_node_67 | 0.4 | n |  | TRUE
108 | bus_LV_2615-3_0_3_node_68 | 0.4 | n |  | TRUE
109 | bus_LV_2615-3_0_3_node_76 | 0.4 | n |  | TRUE
110 | bus_LV_2615-3_0_3_node_75 | 0.4 | n |  | TRUE
111 | bus_LV_2615-3_0_3_node_110 | 0.4 | n |  | TRUE
112 | bus_LV_2615-3_0_3_node_72 | 0.4 | n |  | TRUE
113 | bus_LV_2615-3_0_3_node_73 | 0.4 | n |  | TRUE
114 | bus_LV_2615-3_0_3_node_74 | 0.4 | n |  | TRUE
115 | bus_LV_2615-3_0_3_node_77 | 0.4 | n |  | TRUE
116 | bus_LV_2615-3_0_3_node_79 | 0.4 | n |  | TRUE
117 | bus_LV_2615-3_0_3_node_80 | 0.4 | n |  | TRUE
118 | bus_LV_2615-3_0_3_node_100 | 0.4 | n |  | TRUE
119 | bus_LV_2615-3_0_3_node_84 | 0.4 | n |  | TRUE
120 | bus_LV_2615-3_0_3_node_95 | 0.4 | n |  | TRUE
121 | bus_LV_2615-3_0_3_node_116 | 0.4 | n |  | TRUE
122 | bus_LV_2615-3_0_3_node_114 | 0.4 | n |  | TRUE
123 | bus_LV_2615-3_0_3_node_121 | 0.4 | n |  | TRUE
124 | bus_LV_2615-3_0_3_node_122 | 0.4 | n |  | TRUE
125 | bus_LV_2615-3_0_3_node_123 | 0.4 | n |  | TRUE
126 | bus_LV_2615-3_0_3_node_124 | 0.4 | n |  | TRUE
127 | bus_LV_2615-3_0_3_node_125 | 0.4 | n |  | TRUE
128 | bus_LV_2615-3_0_3_node_113 | 0.4 | n |  | TRUE
129 | bus_LV_2615-3_0_3_node_115 | 0.4 | n |  | TRUE
130 | bus_MV_294_0_node_61 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2615-3_0_3_load_0 | 0 | 0.00071525 | 0.00017926 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2615-3_0_3_load_1 | 1 | 0.0010339 | 0.00025913 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2615-3_0_3_load_101 | 5 | 0.0012133 | 0.00030408 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2615-3_0_3_load_128 | 7 | 0.0017367 | 0.00043526 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2615-3_0_3_load_3 | 9 | 0.00051878 | 0.00013002 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2615-3_0_3_load_4 | 10 | 0.0021163 | 0.0005304 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2615-3_0_3_load_6 | 12 | 0.001084 | 0.00027167 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2615-3_0_3_load_7 | 13 | 0.00083033 | 0.0002081 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2615-3_0_3_load_8 | 14 | 0.00045845 | 0.0001149 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2615-3_0_3_load_50 | 15 | 0.00096299 | 0.00024135 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2615-3_0_3_load_40 | 17 | 0.00050603 | 0.00012682 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2615-3_0_3_load_48 | 18 | 0.0011493 | 0.00028804 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2615-3_0_3_load_126 | 19 | 0.00075897 | 0.00019021 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2615-3_0_3_load_39 | 20 | 0.00062891 | 0.00015762 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2615-3_0_3_load_9 | 21 | 0.00058231 | 0.00014594 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2615-3_0_3_load_10 | 22 | 0.00056214 | 0.00014089 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2615-3_0_3_load_11 | 23 | 0.00030519 | 7.6488e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2615-3_0_3_load_99 | 27 | 0.00064177 | 0.00016084 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2615-3_0_3_load_38 | 28 | 0.00095933 | 0.00024043 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2615-3_0_3_load_133 | 29 | 0.0011848 | 0.00029694 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2615-3_0_3_load_131 | 30 | 0.0010758 | 0.00026961 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2615-3_0_3_load_107 | 31 | 0.00071325 | 0.00017876 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2615-3_0_3_load_35 | 32 | 0.00062941 | 0.00015774 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2615-3_0_3_load_36 | 33 | 0.00049963 | 0.00012522 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2615-3_0_3_load_14 | 34 | 0.0050082 | 0.0012552 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2615-3_0_3_load_15 | 35 | 0.003247 | 0.00081377 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2615-3_0_3_load_19 | 38 | 0.0032405 | 0.00081214 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2615-3_0_3_load_71 | 39 | 0.0026784 | 0.00067126 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2615-3_0_3_load_69 | 40 | 0.0010408 | 0.00026086 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2615-3_0_3_load_93 | 41 | 0.00097611 | 0.00024464 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2615-3_0_3_load_109 | 42 | 0.0029504 | 0.00073943 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2615-3_0_3_load_70 | 43 | 0.0032206 | 0.00080715 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2615-3_0_3_load_94 | 44 | 0.0012747 | 0.00031947 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2615-3_0_3_load_20 | 45 | 0.0035745 | 0.00089585 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2615-3_0_3_load_21 | 46 | 0.0042441 | 0.0010637 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2615-3_0_3_load_24 | 49 | 0.0028896 | 0.0007242 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2615-3_0_3_load_25 | 50 | 0.0023031 | 0.00057721 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2615-3_0_3_load_108 | 52 | 0.0013225 | 0.00033145 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2615-3_0_3_load_89 | 53 | 0.0022454 | 0.00056274 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2615-3_0_3_load_111 | 54 | 0.0071076 | 0.0017813 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2615-3_0_3_load_44 | 55 | 0.0027082 | 0.00067873 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2615-3_0_3_load_51 | 56 | 0.0013859 | 0.00034735 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2615-3_0_3_load_88 | 57 | 0.0032799 | 0.00082203 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2615-3_0_3_load_26 | 58 | 0.00061958 | 0.00015528 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2615-3_0_3_load_27 | 59 | 0.0034221 | 0.00085767 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2615-3_0_3_load_28 | 60 | 0.0015863 | 0.00039756 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2615-3_0_3_load_130 | 62 | 0.0011389 | 0.00028543 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2615-3_0_3_load_30 | 64 | 0.0030737 | 0.00077033 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2615-3_0_3_load_31 | 65 | 0.0021314 | 0.00053418 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2615-3_0_3_load_32 | 66 | 0.0017468 | 0.00043778 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2615-3_0_3_load_33 | 67 | 0.0016612 | 0.00041633 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2615-3_0_3_load_34 | 68 | 0.0019708 | 0.00049393 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2615-3_0_3_load_127 | 69 | 0.0015983 | 0.00040058 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2615-3_0_3_load_52 | 70 | 0.0015264 | 0.00038255 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2615-3_0_3_load_47 | 71 | 0.0030882 | 0.00077398 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2615-3_0_3_load_82 | 73 | 0.00061958 | 0.00015528 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2615-3_0_3_load_129 | 74 | 0.00066237 | 0.00016601 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2615-3_0_3_load_83 | 75 | 0.00044659 | 0.00011193 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2615-3_0_3_load_42 | 76 | 0.00041837 | 0.00010485 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2615-3_0_3_load_41 | 77 | 0.00051291 | 0.00012855 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2615-3_0_3_load_43 | 78 | 0.0010202 | 0.00025568 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2615-3_0_3_load_45 | 79 | 0.0015395 | 0.00038582 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2615-3_0_3_load_49 | 80 | 0.0024653 | 0.00061787 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2615-3_0_3_load_53 | 81 | 0.0018099 | 0.0004536 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2615-3_0_3_load_54 | 82 | 0.00010392 | 2.6044e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2615-3_0_3_load_132 | 83 | 0.00082126 | 0.00020583 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2615-3_0_3_load_96 | 86 | 0.00060115 | 0.00015066 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2615-3_0_3_load_56 | 87 | 0.0060445 | 0.0015149 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2615-3_0_3_load_58 | 89 | 0.00090828 | 0.00022764 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2615-3_0_3_load_91 | 90 | 0.0024961 | 0.00062559 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2615-3_0_3_load_118 | 92 | 0.0016782 | 0.0004206 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2615-3_0_3_load_120 | 94 | 0.0051521 | 0.0012912 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2615-3_0_3_load_59 | 95 | 0.0057919 | 0.0014516 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2615-3_0_3_load_86 | 98 | 0.0012038 | 0.00030169 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2615-3_0_3_load_105 | 100 | 0.0030449 | 0.00076313 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2615-3_0_3_load_103 | 101 | 0.0025917 | 0.00064955 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2615-3_0_3_load_90 | 102 | 0.0013469 | 0.00033756 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2615-3_0_3_load_112 | 103 | 0.0053519 | 0.0013413 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2615-3_0_3_load_104 | 104 | 0.0019279 | 0.00048317 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2615-3_0_3_load_65 | 105 | 0.00036134 | 9.0559e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2615-3_0_3_load_66 | 106 | 0.0016899 | 0.00042352 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2615-3_0_3_load_68 | 108 | 0.00026866 | 6.7332e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2615-3_0_3_load_75 | 110 | 0.00017676 | 4.43e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2615-3_0_3_load_72 | 112 | 0.00021757 | 5.4528e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2615-3_0_3_load_73 | 113 | 0.00037699 | 9.4483e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2615-3_0_3_load_74 | 114 | 0.00015413 | 3.863e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2615-3_0_3_load_77 | 115 | 0.00072366 | 0.00018137 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2615-3_0_3_load_79 | 116 | 0.0014497 | 0.00036333 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2615-3_0_3_load_80 | 117 | 0.0012471 | 0.00031255 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2615-3_0_3_load_100 | 118 | 0.00064099 | 0.00016065 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2615-3_0_3_load_84 | 119 | 0.0019809 | 0.00049646 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2615-3_0_3_load_95 | 120 | 0.0049152 | 0.0012319 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2615-3_0_3_load_116 | 121 | 0.0024872 | 0.00062336 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2615-3_0_3_load_114 | 122 | 0.00079729 | 0.00019982 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2615-3_0_3_load_122 | 124 | 0.0012048 | 0.00030194 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2615-3_0_3_load_124 | 126 | 0.0012428 | 0.00031149 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2615-3_0_3_load_125 | 127 | 0.0012799 | 0.00032078 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2615-3_0_3_load_113 | 128 | 0.00078354 | 0.00019637 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2615-3_0_3_load_115 | 129 | 0.0026644 | 0.00066777 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 77 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2615-3_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.021331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2615-3_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.015511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2615-3_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.011369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2615-3_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.014411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2615-3_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.018402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2615-3_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.028123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2615-3_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.029741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2615-3_0_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.008667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2615-3_0_3_line_8 | NAYY 4x150 SE | 5 | 118 | 0.0035693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2615-3_0_3_line_9 | NAYY 4x150 SE | 6 | 117 | 0.020069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2615-3_0_3_line_10 | NAYY 4x150 SE | 6 | 115 | 0.013155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2615-3_0_3_line_11 | NAYY 4x150 SE | 7 | 74 | 0.03614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2615-3_0_3_line_12 | NAYY 4x150 SE | 8 | 96 | 0.008917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2615-3_0_3_line_13 | NAYY 4x150 SE | 8 | 95 | 0.026666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2615-3_0_3_line_14 | NAYY 4x150 SE | 9 | 10 | 0.018265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_2615-3_0_3_line_15 | NAYY 4x150 SE | 9 | 11 | 0.016209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_2615-3_0_3_line_16 | NAYY 4x150 SE | 10 | 12 | 0.0041378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_2615-3_0_3_line_17 | NAYY 4x150 SE | 11 | 13 | 0.055246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2615-3_0_3_line_18 | NAYY 4x150 SE | 11 | 14 | 0.0097425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_2615-3_0_3_line_19 | NAYY 4x150 SE | 12 | 15 | 0.011682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_2615-3_0_3_line_20 | NAYY 4x150 SE | 13 | 16 | 0.020739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2615-3_0_3_line_21 | NAYY 4x150 SE | 14 | 17 | 0.0066432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_2615-3_0_3_line_22 | NAYY 4x150 SE | 15 | 18 | 0.0075933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_2615-3_0_3_line_23 | NAYY 4x150 SE | 16 | 19 | 0.026876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2615-3_0_3_line_24 | NAYY 4x150 SE | 17 | 20 | 0.019387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_2615-3_0_3_line_25 | NAYY 4x150 SE | 18 | 80 | 0.011112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_2615-3_0_3_line_26 | NAYY 4x150 SE | 19 | 127 | 0.013035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2615-3_0_3_line_27 | NAYY 4x150 SE | 20 | 77 | 0.0063593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_2615-3_0_3_line_28 | NAYY 4x150 SE | 21 | 22 | 0.010844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2615-3_0_3_line_29 | NAYY 4x150 SE | 21 | 23 | 0.015552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2615-3_0_3_line_30 | NAYY 4x150 SE | 22 | 24 | 0.020016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2615-3_0_3_line_31 | NAYY 4x150 SE | 23 | 25 | 0.0011203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2615-3_0_3_line_32 | NAYY 4x150 SE | 24 | 26 | 0.015593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2615-3_0_3_line_33 | NAYY 4x150 SE | 24 | 27 | 0.0055511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2615-3_0_3_line_34 | NAYY 4x150 SE | 25 | 28 | 0.011282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2615-3_0_3_line_35 | NAYY 4x150 SE | 26 | 29 | 0.022088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2615-3_0_3_line_36 | NAYY 4x150 SE | 26 | 30 | 0.01347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2615-3_0_3_line_37 | NAYY 4x150 SE | 28 | 31 | 0.0064331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2615-3_0_3_line_38 | NAYY 4x150 SE | 30 | 83 | 0.019349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2615-3_0_3_line_39 | NAYY 4x150 SE | 31 | 76 | 0.015548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2615-3_0_3_line_40 | NAYY 4x150 SE | 32 | 33 | 0.0074756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2615-3_0_3_line_41 | NAYY 4x150 SE | 33 | 72 | 0.016065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2615-3_0_3_line_42 | NAYY 4x150 SE | 34 | 35 | 0.01828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2615-3_0_3_line_43 | NAYY 4x150 SE | 34 | 36 | 0.036337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2615-3_0_3_line_44 | NAYY 4x150 SE | 36 | 37 | 0.02154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2615-3_0_3_line_45 | NAYY 4x150 SE | 36 | 38 | 0.016996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2615-3_0_3_line_46 | NAYY 4x150 SE | 37 | 39 | 0.0066464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2615-3_0_3_line_47 | NAYY 4x150 SE | 37 | 40 | 0.023058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2615-3_0_3_line_48 | NAYY 4x150 SE | 38 | 41 | 0.013592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2615-3_0_3_line_49 | NAYY 4x150 SE | 39 | 42 | 0.013543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2615-3_0_3_line_50 | NAYY 4x150 SE | 40 | 43 | 0.002986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2615-3_0_3_line_51 | NAYY 4x150 SE | 41 | 44 | 0.0028729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2615-3_0_3_line_52 | NAYY 4x150 SE | 42 | 111 | 0.025253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2615-3_0_3_line_53 | NAYY 4x150 SE | 43 | 51 | 0.011851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2615-3_0_3_line_54 | NAYY 4x150 SE | 44 | 120 | 0.010292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2615-3_0_3_line_55 | NAYY 4x150 SE | 45 | 46 | 0.01653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2615-3_0_3_line_56 | NAYY 4x150 SE | 45 | 47 | 0.0060375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2615-3_0_3_line_57 | NAYY 4x150 SE | 46 | 48 | 0.018755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2615-3_0_3_line_58 | NAYY 4x150 SE | 47 | 49 | 0.0059535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2615-3_0_3_line_59 | NAYY 4x150 SE | 47 | 50 | 0.015856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2615-3_0_3_line_60 | NAYY 4x150 SE | 48 | 51 | 0.01634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2615-3_0_3_line_61 | NAYY 4x150 SE | 48 | 52 | 0.018991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
62 | LV_2615-3_0_3_line_62 | NAYY 4x150 SE | 49 | 53 | 0.018292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2615-3_0_3_line_63 | NAYY 4x150 SE | 50 | 54 | 0.0024856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2615-3_0_3_line_64 | NAYY 4x150 SE | 51 | 55 | 0.0066357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2615-3_0_3_line_65 | NAYY 4x150 SE | 52 | 56 | 0.00036597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
66 | LV_2615-3_0_3_line_66 | NAYY 4x150 SE | 53 | 57 | 0.019771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2615-3_0_3_line_67 | NAYY 4x150 SE | 55 | 78 | 0.0022277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2615-3_0_3_line_68 | NAYY 4x150 SE | 56 | 80 | 0.005201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
69 | LV_2615-3_0_3_line_69 | NAYY 4x150 SE | 57 | 97 | 0.02225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2615-3_0_3_line_70 | NAYY 4x150 SE | 58 | 59 | 0.036466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2615-3_0_3_line_71 | NAYY 4x150 SE | 58 | 60 | 0.012458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2615-3_0_3_line_72 | NAYY 4x150 SE | 60 | 61 | 0.0076795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2615-3_0_3_line_73 | NAYY 4x150 SE | 61 | 62 | 0.024471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2615-3_0_3_line_74 | NAYY 4x150 SE | 62 | 63 | 0.013314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2615-3_0_3_line_75 | NAYY 4x150 SE | 63 | 74 | 0.017075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2615-3_0_3_line_76 | NAYY 4x150 SE | 64 | 65 | 0.0084465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2615-3_0_3_line_77 | NAYY 4x150 SE | 64 | 66 | 0.0098789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2615-3_0_3_line_78 | NAYY 4x150 SE | 65 | 67 | 0.0015294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2615-3_0_3_line_79 | NAYY 4x150 SE | 66 | 68 | 0.0078983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2615-3_0_3_line_80 | NAYY 4x150 SE | 67 | 69 | 0.01086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2615-3_0_3_line_81 | NAYY 4x150 SE | 68 | 70 | 0.00020281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2615-3_0_3_line_82 | NAYY 4x150 SE | 70 | 71 | 0.015494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2615-3_0_3_line_83 | NAYY 4x150 SE | 71 | 79 | 0.0002351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2615-3_0_3_line_84 | NAYY 4x150 SE | 72 | 73 | 0.0090551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2615-3_0_3_line_85 | NAYY 4x150 SE | 73 | 75 | 0.0098994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2615-3_0_3_line_86 | NAYY 4x150 SE | 75 | 119 | 0.011834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2615-3_0_3_line_87 | NAYY 4x150 SE | 76 | 77 | 0.01082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2615-3_0_3_line_88 | NAYY 4x150 SE | 78 | 79 | 0.010032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2615-3_0_3_line_89 | NAYY 4x150 SE | 81 | 82 | 0.022945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2615-3_0_3_line_90 | NAYY 4x150 SE | 81 | 83 | 0.38995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2615-3_0_3_line_91 | NAYY 4x150 SE | 82 | 84 | 0.01425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2615-3_0_3_line_92 | NAYY 4x150 SE | 84 | 85 | 0.010074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2615-3_0_3_line_93 | NAYY 4x150 SE | 85 | 86 | 0.040431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2615-3_0_3_line_94 | NAYY 4x150 SE | 86 | 114 | 0.021746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2615-3_0_3_line_95 | NAYY 4x150 SE | 87 | 88 | 0.0016574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2615-3_0_3_line_96 | NAYY 4x150 SE | 88 | 89 | 0.0073852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2615-3_0_3_line_97 | NAYY 4x150 SE | 88 | 90 | 0.31622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2615-3_0_3_line_98 | NAYY 4x150 SE | 90 | 91 | 0.020518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2615-3_0_3_line_99 | NAYY 4x150 SE | 91 | 106 | 0.19842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2615-3_0_3_line_100 | NAYY 4x150 SE | 92 | 93 | 0.020814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2615-3_0_3_line_101 | NAYY 4x150 SE | 92 | 94 | 0.0027755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2615-3_0_3_line_102 | NAYY 4x150 SE | 93 | 123 | 0.03149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2615-3_0_3_line_103 | NAYY 4x150 SE | 96 | 97 | 0.020124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2615-3_0_3_line_104 | NAYY 4x150 SE | 96 | 98 | 0.029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2615-3_0_3_line_105 | NAYY 4x150 SE | 97 | 102 | 0.024979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2615-3_0_3_line_106 | NAYY 4x150 SE | 99 | 100 | 0.025342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2615-3_0_3_line_107 | NAYY 4x150 SE | 99 | 101 | 0.015077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2615-3_0_3_line_108 | NAYY 4x150 SE | 100 | 103 | 0.014463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2615-3_0_3_line_109 | NAYY 4x150 SE | 101 | 104 | 0.017516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2615-3_0_3_line_110 | NAYY 4x150 SE | 102 | 119 | 0.015731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2615-3_0_3_line_111 | NAYY 4x150 SE | 103 | 111 | 0.0033553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2615-3_0_3_line_112 | NAYY 4x150 SE | 105 | 106 | 0.028327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2615-3_0_3_line_113 | NAYY 4x150 SE | 105 | 107 | 0.045869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2615-3_0_3_line_114 | NAYY 4x150 SE | 107 | 108 | 0.025771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2615-3_0_3_line_115 | NAYY 4x150 SE | 108 | 109 | 0.11134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2615-3_0_3_line_116 | NAYY 4x150 SE | 109 | 110 | 0.023122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2615-3_0_3_line_117 | NAYY 4x150 SE | 110 | 114 | 0.11146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2615-3_0_3_line_118 | NAYY 4x150 SE | 112 | 113 | 0.015243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2615-3_0_3_line_119 | NAYY 4x150 SE | 113 | 114 | 0.0038574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2615-3_0_3_line_120 | NAYY 4x150 SE | 115 | 116 | 0.021672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2615-3_0_3_line_121 | NAYY 4x150 SE | 120 | 121 | 0.01513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2615-3_0_3_line_122 | NAYY 4x150 SE | 121 | 122 | 0.0044801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_2615-3_0_3_line_123 | NAYY 4x150 SE | 122 | 128 | 0.017744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_2615-3_0_3_line_124 | NAYY 4x150 SE | 123 | 124 | 0.075577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_2615-3_0_3_line_125 | NAYY 4x150 SE | 124 | 125 | 0.043551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_2615-3_0_3_line_126 | NAYY 4x150 SE | 125 | 126 | 0.037834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_2615-3_0_3_line_127 | NAYY 4x150 SE | 126 | 127 | 0.016903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_2615-3_0_3_line_128 | NAYY 4x150 SE | 128 | 129 | 0.0061474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2615-3_0_3_trafo_41 | 0.25 MVA 20/0.4 kV | 130 | 77 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2607699.2689 | 1247043.4661 | 2607719.9321 | 1247048.7626
1 | 2607734.9574 | 1247052.6139 | 2607719.9321 | 1247048.7626
2 | 2607734.9574 | 1247052.6139 | 2607733.3946 | 1247063.8746
3 | 2607734.9574 | 1247052.6139 | 2607736.9396 | 1247038.3406
4 | 2607733.3946 | 1247063.8746 | 2607750.9655 | 1247069.3434
5 | 2607733.3946 | 1247063.8746 | 2607729.552 | 1247091.7319
6 | 2607736.9396 | 1247038.3406 | 2607708.2867 | 1247030.3694
7 | 2607737.9779 | 1247029.7365 | 2607736.9396 | 1247038.3406
8 | 2607754.3735 | 1247070.4041 | 2607750.9655 | 1247069.3434
9 | 2607729.552 | 1247091.7319 | 2607725.9231 | 1247111.4704
10 | 2607729.552 | 1247091.7319 | 2607716.6205 | 1247089.3172
11 | 2607708.2867 | 1247030.3694 | 2607673.4693 | 1247020.6832
12 | 2607738.7522 | 1247020.854 | 2607737.9779 | 1247029.7365
13 | 2607737.9779 | 1247029.7365 | 2607764.5868 | 1247031.473
14 | 2607673.08 | 1246874.8801 | 2607682.2328 | 1246876.2111 | 2607690.961 | 1246878.4726
15 | 2607656.9392 | 1246875.6561 | 2607664.055 | 1246874.7758 | 2607671.8195 | 1246874.6968 | 2607673.08 | 1246874.8801
16 | 2607690.961 | 1246878.4726 | 2607694.9666 | 1246879.5104
17 | 2607656.9392 | 1246875.6561 | 2607654.2891 | 1246868.9707 | 2607652.9757 | 1246862.4648 | 2607650.5704 | 1246859.3375 | 2607646.6842 | 1246856.553 | 2607639.9606 | 1246851.8859 | 2607634.2253 | 1246848.0761 | 2607628.1502 | 1246844.177 | 2607619.6813 | 1246838.1367
18 | 2607656.9392 | 1246875.6561 | 2607653.3391 | 1246879.4873 | 2607651.1195 | 1246883.3848
19 | 2607706.275 | 1246882.4405 | 2607694.9666 | 1246879.5104
20 | 2607602.0918 | 1246827.1663 | 2607616.6878 | 1246836.0016 | 2607619.6813 | 1246838.1367
21 | 2607647.8465 | 1246889.1657 | 2607648.29 | 1246888.3531 | 2607651.1195 | 1246883.3848
22 | 2607713.6256 | 1246884.345 | 2607706.275 | 1246882.4405
23 | 2607602.0918 | 1246827.1663 | 2607618.0031 | 1246805.5061
24 | 2607647.8465 | 1246889.1657 | 2607638.5587 | 1246906.1828
25 | 2607713.6256 | 1246884.345 | 2607724.3826 | 1246887.1321
26 | 2607618.0031 | 1246805.5061 | 2607619.4969 | 1246795.0013 | 2607619.8079 | 1246792.5972
27 | 2607635.512 | 1246911.7648 | 2607638.5587 | 1246906.1828
28 | 2607603.2256 | 1246963.0574 | 2607596.9182 | 1246969.7063 | 2607595.6475 | 1246970.8045
29 | 2607612.8989 | 1246950.8859 | 2607604.05 | 1246962.1883 | 2607603.2256 | 1246963.0574
30 | 2607580.0886 | 1246983.3825 | 2607588.9414 | 1246976.6005 | 2607595.6475 | 1246970.8045
31 | 2607613.5895 | 1246950.0038 | 2607612.8989 | 1246950.8859
32 | 2607580.0886 | 1246983.3825 | 2607584.098 | 1246990.1697 | 2607586.0106 | 1246994.7084 | 2607586.566 | 1246997.4442
33 | 2607580.0886 | 1246983.3825 | 2607575.1333 | 1246985.8846
34 | 2607613.5895 | 1246950.0038 | 2607619.3156 | 1246940.2834
35 | 2607586.566 | 1246997.4442 | 2607607.743 | 1247003.9307
36 | 2607586.566 | 1246997.4442 | 2607586.0993 | 1247002.1799 | 2607584.4003 | 1247010.724
37 | 2607619.3156 | 1246940.2834 | 2607622.5808 | 1246934.7406
38 | 2607580.6265 | 1247029.7017 | 2607584.4003 | 1247010.724
39 | 2607630.3285 | 1246921.262 | 2607627.9027 | 1246925.7065 | 2607622.5808 | 1246934.7406
40 | 2607651.2433 | 1246967.616 | 2607654.848 | 1246969.3021 | 2607658.0169 | 1246970.7786
41 | 2607672.5787 | 1246977.5634 | 2607658.0169 | 1246970.7786
42 | 2607801.0942 | 1246833.2146 | 2607804.1301 | 1246822.379 | 2607806.0227 | 1246815.6114
43 | 2607791.8421 | 1246868.3479 | 2607795.601 | 1246852.8206 | 2607801.0942 | 1246833.2146
44 | 2607789.3218 | 1246889.7249 | 2607789.7763 | 1246882.9323 | 2607791.8421 | 1246868.3479
45 | 2607791.8421 | 1246868.3479 | 2607808.5154 | 1246871.6438
46 | 2607789.3218 | 1246889.7249 | 2607789.2728 | 1246896.3711
47 | 2607789.3218 | 1246889.7249 | 2607783.4242 | 1246888.8611 | 2607775.9877 | 1246886.5611 | 2607767.2655 | 1246883.2954
48 | 2607821.8493 | 1246874.2797 | 2607808.5154 | 1246871.6438
49 | 2607790.7963 | 1246909.7992 | 2607790.1007 | 1246906.3921 | 2607789.2576 | 1246898.4415 | 2607789.2728 | 1246896.3711
50 | 2607767.2655 | 1246883.2954 | 2607764.4691 | 1246882.2484
51 | 2607821.8493 | 1246874.2797 | 2607821.8493 | 1246874.2797 | 2607824.5394 | 1246873.2715
52 | 2607797.7609 | 1246934.0308 | 2607794.9914 | 1246926.4001 | 2607792.2171 | 1246916.7125 | 2607791.6242 | 1246913.8544 | 2607790.7963 | 1246909.7992
53 | 2607753.3704 | 1246878.093 | 2607764.4691 | 1246882.2484
54 | 2607824.5394 | 1246873.2715 | 2607824.5394 | 1246873.2715 | 2607826.9908 | 1246863.2756
55 | 2607744.8344 | 1246928.6293 | 2607746.3649 | 1246912.17
56 | 2607744.3999 | 1246934.6508 | 2607744.7004 | 1246930.0705 | 2607744.8344 | 1246928.6293
57 | 2607748.1013 | 1246893.496 | 2607746.3649 | 1246912.17
58 | 2607744.3999 | 1246934.6508 | 2607744.0122 | 1246940.5916
59 | 2607744.3999 | 1246934.6508 | 2607760.2381 | 1246935.3986
60 | 2607753.3704 | 1246878.093 | 2607749.901 | 1246886.0046 | 2607748.1013 | 1246893.496
61 | 2607748.1013 | 1246893.496 | 2607732.9481 | 1246889.3515 | 2607729.7715 | 1246888.5284
62 | 2607742.8211 | 1246958.8446 | 2607744.0122 | 1246940.5916
63 | 2607762.721 | 1246935.5158 | 2607760.2381 | 1246935.3986
64 | 2607753.3704 | 1246878.093 | 2607756.0389 | 1246872.0174
65 | 2607729.4173 | 1246888.4366 | 2607729.7715 | 1246888.5284
66 | 2607741.5337 | 1246978.5732 | 2607742.8211 | 1246958.8446
67 | 2607756.0389 | 1246872.0174 | 2607756.9347 | 1246869.9778
68 | 2607724.3826 | 1246887.1321 | 2607729.4173 | 1246888.4366
69 | 2607740.0848 | 1247000.7763 | 2607741.5337 | 1246978.5732
70 | 2607654.8353 | 1247049.998 | 2607654.8353 | 1247049.998 | 2607651.7471 | 1247067.0605 | 2607650.4027 | 1247067.1144 | 2607646.5907 | 1247084.4817
71 | 2607654.8353 | 1247049.998 | 2607642.7608 | 1247046.931
72 | 2607638.5326 | 1247041.4495 | 2607640.3616 | 1247046.3216 | 2607642.7608 | 1247046.931
73 | 2607638.5326 | 1247041.4495 | 2607643.3048 | 1247024.5448 | 2607646.8772 | 1247018.6345
74 | 2607658.9309 | 1247012.9796 | 2607652.3108 | 1247016.0954 | 2607646.8772 | 1247018.6345
75 | 2607658.9309 | 1247012.9796 | 2607663.4637 | 1247017.8997 | 2607673.4693 | 1247020.6832
76 | 2607770.7083 | 1246828.4981 | 2607772.9643 | 1246820.3584
77 | 2607767.9871 | 1246837.9946 | 2607769.6003 | 1246832.4961 | 2607770.7083 | 1246828.4981
78 | 2607772.9643 | 1246820.3584 | 2607773.3728 | 1246818.8846
79 | 2607767.9871 | 1246837.9946 | 2607765.7635 | 1246845.5734
80 | 2607776.2082 | 1246808.4012 | 2607775.0033 | 1246813.0018 | 2607773.3728 | 1246818.8846
81 | 2607765.7635 | 1246845.5734 | 2607765.7064 | 1246845.768
82 | 2607765.7064 | 1246845.768 | 2607764.6994 | 1246849.2003 | 2607760.5953 | 1246860.3885
83 | 2607760.5953 | 1246860.3885 | 2607760.5143 | 1246860.6093
84 | 2607672.5787 | 1246977.5634 | 2607681.0573 | 1246980.7428
85 | 2607681.0573 | 1246980.7428 | 2607690.3264 | 1246984.2186
86 | 2607690.3264 | 1246984.2186 | 2607695.8146 | 1246986.2766 | 2607701.3841 | 1246988.4346
87 | 2607630.3285 | 1246921.262 | 2607635.512 | 1246911.7648
88 | 2607760.5143 | 1246860.6093 | 2607757.8019 | 1246868.0034 | 2607756.9347 | 1246869.9778
89 | 2607265.6026 | 1247259.5258 | 2607254.8901 | 1247271.9637 | 2607251.7689 | 1247277.699
90 | 2607580.6265 | 1247029.7017 | 2607265.6026 | 1247259.5258
91 | 2607249.927 | 1247291.6481 | 2607250.6816 | 1247279.6969 | 2607251.7689 | 1247277.699
92 | 2607249.927 | 1247291.6481 | 2607245.9512 | 1247294.3783 | 2607242.1329 | 1247298.0094
93 | 2607242.1329 | 1247298.0094 | 2607230.5091 | 1247292.4918 | 2607219.5924 | 1247289.1987 | 2607214.2249 | 1247287.38 | 2607204.4273 | 1247283.6214
94 | 2607204.4273 | 1247283.6214 | 2607199.7463 | 1247281.8257 | 2607192.586 | 1247282.473 | 2607183.1964 | 1247284.1739 | 2607183.1964 | 1247284.1739
95 | 2606638.5015 | 1246950.8992 | 2606639.1447 | 1246949.3717
96 | 2606638.5015 | 1246950.8992 | 2606637.1028 | 1246945.4052 | 2606636.9452 | 1246943.6965
97 | 2606875.7763 | 1247159.9287 | 2606638.5015 | 1246950.8992
98 | 2606888.5774 | 1247175.9586 | 2606876.8576 | 1247161.4803 | 2606875.7763 | 1247159.9287
99 | 2607062.8049 | 1247081.0099 | 2606888.5774 | 1247175.9586
100 | 2607472.7561 | 1246760.7944 | 2607473.7983 | 1246773.0035 | 2607475.5388 | 1246781.3848
101 | 2607476.1031 | 1246784.1023 | 2607475.5388 | 1246781.3848
102 | 2607472.7561 | 1246760.7944 | 2607488.3043 | 1246763.5045 | 2607504.0659 | 1246764.5916
103 | 2607740.0848 | 1247000.7763 | 2607738.7522 | 1247020.854
104 | 2607738.7522 | 1247020.854 | 2607710.9694 | 1247012.5413
105 | 2607740.0848 | 1247000.7763 | 2607735.124 | 1246999.747 | 2607721.4658 | 1246996.216 | 2607716.0526 | 1246994.1185
106 | 2607812.9722 | 1246974.4209 | 2607810.1496 | 1246967.0236 | 2607804.5947 | 1246952.4737 | 2607803.9519 | 1246950.739
107 | 2607812.9722 | 1246974.4209 | 2607821.2379 | 1246972.0524 | 2607827.7163 | 1246972.0092
108 | 2607803.9519 | 1246950.739 | 2607798.9267 | 1246937.1771
109 | 2607845.2316 | 1246971.8924 | 2607827.7163 | 1246972.0092
110 | 2607716.0526 | 1246994.1185 | 2607701.3841 | 1246988.4346
111 | 2607797.7609 | 1246934.0308 | 2607798.9267 | 1246937.1771
112 | 2607087.6971 | 1247067.5382 | 2607064.8972 | 1247079.5024 | 2607062.8049 | 1247081.0099
113 | 2607128.1973 | 1247046.0227 | 2607121.4036 | 1247049.3279 | 2607104.1119 | 1247058.9246 | 2607087.6971 | 1247067.5382
114 | 2607128.1973 | 1247046.0227 | 2607125.8984 | 1247048.4994 | 2607117.9013 | 1247060.2974 | 2607113.4243 | 1247067.0939
115 | 2607113.4243 | 1247067.0939 | 2607165.7419 | 1247165.3771
116 | 2607165.7419 | 1247165.3771 | 2607163.8661 | 1247167.6875 | 2607154.9536 | 1247174.47 | 2607147.0861 | 1247178.7278
117 | 2607183.1964 | 1247284.1739 | 2607147.0861 | 1247178.7278
118 | 2607168.8671 | 1247296.7484 | 2607171.3427 | 1247293.9549 | 2607180.2211 | 1247286.6289
119 | 2607183.1964 | 1247284.1739 | 2607180.2211 | 1247286.6289
120 | 2607695.317 | 1247085.3392 | 2607716.6205 | 1247089.3172
121 | 2607841.0219 | 1246863.6504 | 2607829.57 | 1246861.3927 | 2607827.1971 | 1246862.4347 | 2607826.9908 | 1246863.2756
122 | 2607845.4174 | 1246864.517 | 2607841.0219 | 1246863.6504
123 | 2607862.826 | 1246867.949 | 2607845.4174 | 1246864.517
124 | 2607504.0659 | 1246764.5916 | 2607519.2392 | 1246759.096 | 2607526.4844 | 1246757.6041 | 2607546.1969 | 1246758.196 | 2607558.1079 | 1246758.1999 | 2607565.5485 | 1246757.4867 | 2607569.915 | 1246756.814 | 2607574.4998 | 1246756.6864 | 2607578.3666 | 1246755.9848
125 | 2607617.9815 | 1246739.4862 | 2607611.5714 | 1246743.5028 | 2607600.7317 | 1246750.4268 | 2607595.525 | 1246752.5437 | 2607587.7054 | 1246754.2905 | 2607578.3666 | 1246755.9848
126 | 2607617.9815 | 1246739.4862 | 2607621.1034 | 1246743.4038 | 2607622.715 | 1246747.1749 | 2607623.1998 | 1246757.9046 | 2607622.6015 | 1246771.001 | 2607621.9764 | 1246775.8334
127 | 2607619.8079 | 1246792.5972 | 2607621.9764 | 1246775.8334
128 | 2607868.8573 | 1246869.1381 | 2607862.826 | 1246867.949

## bus_geodata
| x | y | coords
0 | 2607699.2689 | 1247043.4661
1 | 2607719.9321 | 1247048.7626
2 | 2607734.9574 | 1247052.6139
3 | 2607733.3946 | 1247063.8746
4 | 2607736.9396 | 1247038.3406
5 | 2607750.9655 | 1247069.3434
6 | 2607729.552 | 1247091.7319
7 | 2607708.2867 | 1247030.3694
8 | 2607737.9779 | 1247029.7365
9 | 2607673.08 | 1246874.8801
10 | 2607690.961 | 1246878.4726
11 | 2607656.9392 | 1246875.6561
12 | 2607694.9666 | 1246879.5104
13 | 2607619.6813 | 1246838.1367
14 | 2607651.1195 | 1246883.3848
15 | 2607706.275 | 1246882.4405
16 | 2607602.0918 | 1246827.1663
17 | 2607647.8465 | 1246889.1657
18 | 2607713.6256 | 1246884.345
19 | 2607618.0031 | 1246805.5061
20 | 2607638.5587 | 1246906.1828
21 | 2607603.2256 | 1246963.0574
22 | 2607595.6475 | 1246970.8045
23 | 2607612.8989 | 1246950.8859
24 | 2607580.0886 | 1246983.3825
25 | 2607613.5895 | 1246950.0038
26 | 2607586.566 | 1246997.4442
27 | 2607575.1333 | 1246985.8846
28 | 2607619.3156 | 1246940.2834
29 | 2607607.743 | 1247003.9307
30 | 2607584.4003 | 1247010.724
31 | 2607622.5808 | 1246934.7406
32 | 2607651.2433 | 1246967.616
33 | 2607658.0169 | 1246970.7786
34 | 2607801.0942 | 1246833.2146
35 | 2607806.0227 | 1246815.6114
36 | 2607791.8421 | 1246868.3479
37 | 2607789.3218 | 1246889.7249
38 | 2607808.5154 | 1246871.6438
39 | 2607789.2728 | 1246896.3711
40 | 2607767.2655 | 1246883.2954
41 | 2607821.8493 | 1246874.2797
42 | 2607790.7963 | 1246909.7992
43 | 2607764.4691 | 1246882.2484
44 | 2607824.5394 | 1246873.2715
45 | 2607744.8344 | 1246928.6293
46 | 2607746.3649 | 1246912.17
47 | 2607744.3999 | 1246934.6508
48 | 2607748.1013 | 1246893.496
49 | 2607744.0122 | 1246940.5916
50 | 2607760.2381 | 1246935.3985
51 | 2607753.3704 | 1246878.093
52 | 2607729.7715 | 1246888.5284
53 | 2607742.8211 | 1246958.8446
54 | 2607762.721 | 1246935.5158
55 | 2607756.0389 | 1246872.0174
56 | 2607729.4173 | 1246888.4366
57 | 2607741.5337 | 1246978.5732
58 | 2607654.8353 | 1247049.998
59 | 2607646.5907 | 1247084.4817
60 | 2607642.7608 | 1247046.931
61 | 2607638.5326 | 1247041.4495
62 | 2607646.8772 | 1247018.6345
63 | 2607658.9309 | 1247012.9796
64 | 2607770.7083 | 1246828.4981
65 | 2607772.9643 | 1246820.3584
66 | 2607767.9871 | 1246837.9946
67 | 2607773.3728 | 1246818.8846
68 | 2607765.7635 | 1246845.5734
69 | 2607776.2082 | 1246808.4012
70 | 2607765.7064 | 1246845.768
71 | 2607760.5953 | 1246860.3885
72 | 2607672.5787 | 1246977.5634
73 | 2607681.0573 | 1246980.7428
74 | 2607673.4693 | 1247020.6832
75 | 2607690.3264 | 1246984.2186
76 | 2607630.3285 | 1246921.262
77 | 2607635.512 | 1246911.7648
78 | 2607756.9347 | 1246869.9778
79 | 2607760.5143 | 1246860.6093
80 | 2607724.3826 | 1246887.1321
81 | 2607265.6026 | 1247259.5258
82 | 2607251.7689 | 1247277.699
83 | 2607580.6265 | 1247029.7017
84 | 2607249.927 | 1247291.6481
85 | 2607242.1329 | 1247298.0094
86 | 2607204.4273 | 1247283.6214
87 | 2606639.1447 | 1246949.3717
88 | 2606638.5015 | 1246950.8992
89 | 2606636.9452 | 1246943.6965
90 | 2606875.7763 | 1247159.9287
91 | 2606888.5774 | 1247175.9586
92 | 2607475.5388 | 1246781.3848
93 | 2607472.7561 | 1246760.7944
94 | 2607476.1031 | 1246784.1023
95 | 2607764.5868 | 1247031.473
96 | 2607738.7522 | 1247020.854
97 | 2607740.0848 | 1247000.7763
98 | 2607710.9694 | 1247012.5413
99 | 2607812.9722 | 1246974.4209
100 | 2607803.9519 | 1246950.739
101 | 2607827.7163 | 1246972.0092
102 | 2607716.0526 | 1246994.1185
103 | 2607798.9267 | 1246937.1771
104 | 2607845.2316 | 1246971.8924
105 | 2607087.6971 | 1247067.5382
106 | 2607062.8049 | 1247081.0099
107 | 2607128.1973 | 1247046.0227
108 | 2607113.4243 | 1247067.0939
109 | 2607165.7419 | 1247165.3771
110 | 2607147.0861 | 1247178.7278
111 | 2607797.7609 | 1246934.0308
112 | 2607168.8671 | 1247296.7484
113 | 2607180.2211 | 1247286.6289
114 | 2607183.1964 | 1247284.1739
115 | 2607716.6205 | 1247089.3172
116 | 2607695.317 | 1247085.3392
117 | 2607725.9231 | 1247111.4704
118 | 2607754.3735 | 1247070.4041
119 | 2607701.3841 | 1246988.4346
120 | 2607826.9908 | 1246863.2756
121 | 2607841.0219 | 1246863.6504
122 | 2607845.4174 | 1246864.517
123 | 2607504.0659 | 1246764.5916
124 | 2607578.3666 | 1246755.9848
125 | 2607617.9815 | 1246739.4862
126 | 2607621.9764 | 1246775.8334
127 | 2607619.8079 | 1246792.5972
128 | 2607862.826 | 1246867.949
129 | 2607868.8573 | 1246869.1381
130 | 2607656.9392 | 1246875.6561

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.979 | -0.14754 | 0.00071525 | 0.00017926
1 | 0.97903 | -0.14738 | 0.0010339 | 0.00025913
2 | 0.97907 | -0.1471 | 0 | 0
3 | 0.97898 | -0.14772 | 0 | 0
4 | 0.97921 | -0.14604 | 0 | 0
5 | 0.97893 | -0.14808 | 0.0012133 | 0.00030408
6 | 0.97884 | -0.14873 | 0 | 0
7 | 0.97882 | -0.14888 | 0.0017367 | 0.00043526
8 | 0.97942 | -0.14458 | 0 | 0
9 | 0.99387 | -0.0425 | 0.00051878 | 0.00013002
10 | 0.99208 | -0.054999 | 0.0021163 | 0.0005304
11 | 0.99546 | -0.031402 | 0 | 0
12 | 0.99168 | -0.057793 | 0.001084 | 0.00027167
13 | 0.9945 | -0.038185 | 0.00083033 | 0.0002081
14 | 0.99651 | -0.024153 | 0.00045845 | 0.0001149
15 | 0.99056 | -0.065627 | 0.00096299 | 0.00024135
16 | 0.99416 | -0.040559 | 0 | 0
17 | 0.99722 | -0.019203 | 0.00050603 | 0.00012682
18 | 0.98984 | -0.070692 | 0.0011493 | 0.00028804
19 | 0.99373 | -0.043639 | 0.00075897 | 0.00019021
20 | 0.99931 | -0.0047483 | 0.00062891 | 0.00015762
21 | 0.99813 | -0.012972 | 0.00058231 | 0.00014594
22 | 0.99783 | -0.015106 | 0.00056214 | 0.00014089
23 | 0.99859 | -0.0098227 | 0.00030519 | 7.6488e-05
24 | 0.99728 | -0.018935 | 0 | 0
25 | 0.99862 | -0.0095925 | 0 | 0
26 | 0.99686 | -0.02182 | 0 | 0
27 | 0.99727 | -0.018971 | 0.00064177 | 0.00016084
28 | 0.99895 | -0.0072755 | 0.00095933 | 0.00024043
29 | 0.99682 | -0.022083 | 0.0011848 | 0.00029694
30 | 0.99653 | -0.024153 | 0.0010758 | 0.00026961
31 | 0.99915 | -0.0058932 | 0.00071325 | 0.00017876
32 | 0.97998 | -0.14059 | 0.00062941 | 0.00015774
33 | 0.97998 | -0.14054 | 0.00049963 | 0.00012522
34 | 0.98117 | -0.13211 | 0.0050082 | 0.0012552
35 | 0.98108 | -0.13272 | 0.003247 | 0.00081377
36 | 0.9816 | -0.129 | 0 | 0
37 | 0.9824 | -0.12333 | 0 | 0
38 | 0.98118 | -0.13202 | 0.0032405 | 0.00081214
39 | 0.98222 | -0.12461 | 0.0026784 | 0.00067126
40 | 0.98387 | -0.11286 | 0.0010408 | 0.00026086
41 | 0.9809 | -0.13398 | 0.00097611 | 0.00024464
42 | 0.98191 | -0.12683 | 0.0029504 | 0.00073943
43 | 0.98406 | -0.11148 | 0.0032206 | 0.00080715
44 | 0.98085 | -0.13436 | 0.0012747 | 0.00031947
45 | 0.98387 | -0.11281 | 0.0035745 | 0.00089585
46 | 0.98508 | -0.10427 | 0.0042441 | 0.0010637
47 | 0.98347 | -0.11572 | 0 | 0
48 | 0.98656 | -0.093794 | 0 | 0
49 | 0.98314 | -0.118 | 0.0028896 | 0.0007242
50 | 0.98325 | -0.11726 | 0.0023031 | 0.00057721
51 | 0.98489 | -0.10559 | 0 | 0
52 | 0.98828 | -0.081671 | 0.0013225 | 0.00033145
53 | 0.98223 | -0.12448 | 0.0022454 | 0.00056274
54 | 0.98322 | -0.11744 | 0.0071076 | 0.0017813
55 | 0.98468 | -0.1071 | 0.0027082 | 0.00067873
56 | 0.98831 | -0.081435 | 0.0013859 | 0.00034735
57 | 0.98131 | -0.13104 | 0.0032799 | 0.00082203
58 | 0.97779 | -0.15625 | 0.00061958 | 0.00015528
59 | 0.97761 | -0.15755 | 0.0034221 | 0.00085767
60 | 0.97786 | -0.15573 | 0.0015863 | 0.00039756
61 | 0.97792 | -0.15527 | 0 | 0
62 | 0.97813 | -0.15383 | 0.0011389 | 0.00028543
63 | 0.97826 | -0.15289 | 0 | 0
64 | 0.9838 | -0.11339 | 0.0030737 | 0.00077033
65 | 0.98373 | -0.11386 | 0.0021314 | 0.00053418
66 | 0.98392 | -0.11253 | 0.0017468 | 0.00043778
67 | 0.98372 | -0.11391 | 0.0016612 | 0.00041633
68 | 0.98404 | -0.11169 | 0.0019708 | 0.00049393
69 | 0.9837 | -0.11409 | 0.0015983 | 0.00040058
70 | 0.98404 | -0.11167 | 0.0015264 | 0.00038255
71 | 0.98435 | -0.10948 | 0.0030882 | 0.00077398
72 | 0.98001 | -0.14036 | 0 | 0
73 | 0.98002 | -0.14025 | 0.00061958 | 0.00015528
74 | 0.97842 | -0.15169 | 0.00066237 | 0.00016601
75 | 0.98005 | -0.14007 | 0.00044659 | 0.00011193
76 | 0.99965 | -0.0024437 | 0.00041837 | 0.00010485
77 | 1 | 0 | -0.17545 | -0.044107
78 | 0.98462 | -0.10754 | 0.0010202 | 0.00025568
79 | 0.98435 | -0.10944 | 0.0015395 | 0.00038582
80 | 0.98879 | -0.078051 | 0.0024653 | 0.00061787
81 | 0.98743 | -0.087931 | 0.0018099 | 0.0004536
82 | 0.98698 | -0.091102 | 0.00010392 | 2.6044e-05
83 | 0.99607 | -0.027298 | 0.00082126 | 0.00020583
84 | 0.9867 | -0.093057 | 0 | 0
85 | 0.98651 | -0.09444 | 0 | 0
86 | 0.98572 | -0.099994 | 0.00060115 | 0.00015066
87 | 0.97313 | -0.18994 | 0.0060445 | 0.0015149
88 | 0.97315 | -0.18984 | 0 | 0
89 | 0.97314 | -0.18991 | 0.00090828 | 0.00022764
90 | 0.97637 | -0.16669 | 0.0024961 | 0.00062559
91 | 0.97665 | -0.16466 | 0 | 0
92 | 0.99111 | -0.062129 | 0.0016782 | 0.0004206
93 | 0.99131 | -0.060684 | 0 | 0
94 | 0.99109 | -0.062274 | 0.0051521 | 0.0012912
95 | 0.97919 | -0.14619 | 0.0057919 | 0.0014516
96 | 0.9797 | -0.14254 | 0 | 0
97 | 0.98038 | -0.13768 | 0 | 0
98 | 0.97965 | -0.1429 | 0.0012038 | 0.00030169
99 | 0.98104 | -0.13299 | 0 | 0
100 | 0.98121 | -0.1318 | 0.0030449 | 0.00076313
101 | 0.98094 | -0.13369 | 0.0025917 | 0.00064955
102 | 0.98018 | -0.13911 | 0.0013469 | 0.00033756
103 | 0.98137 | -0.13066 | 0.0053519 | 0.0013413
104 | 0.9809 | -0.13404 | 0.0019279 | 0.00048317
105 | 0.97986 | -0.14171 | 0.00036134 | 9.0559e-05
106 | 0.9794 | -0.14501 | 0.0016899 | 0.00042352
107 | 0.98063 | -0.13621 | 0 | 0
108 | 0.98106 | -0.13312 | 0.00026866 | 6.7332e-05
109 | 0.98298 | -0.11948 | 0 | 0
110 | 0.98337 | -0.11665 | 0.00017676 | 4.43e-05
111 | 0.98143 | -0.13021 | 0 | 0
112 | 0.98531 | -0.10291 | 0.00021757 | 5.4528e-05
113 | 0.98532 | -0.10287 | 0.00037699 | 9.4483e-05
114 | 0.98532 | -0.10285 | 0.00015413 | 3.863e-05
115 | 0.9788 | -0.14903 | 0.00072366 | 0.00018137
116 | 0.97875 | -0.14935 | 0.0014497 | 0.00036333
117 | 0.9788 | -0.14899 | 0.0012471 | 0.00031255
118 | 0.97893 | -0.1481 | 0.00064099 | 0.00016065
119 | 0.98009 | -0.1398 | 0.0019809 | 0.00049646
120 | 0.98068 | -0.13561 | 0.0049152 | 0.0012319
121 | 0.98053 | -0.13666 | 0.0024872 | 0.00062336
122 | 0.9805 | -0.13686 | 0.00079729 | 0.00019982
123 | 0.99162 | -0.058499 | 0 | 0
124 | 0.99236 | -0.053257 | 0.0012048 | 0.00030194
125 | 0.99287 | -0.049706 | 0 | 0
126 | 0.9933 | -0.046622 | 0.0012428 | 0.00031149
127 | 0.99353 | -0.045033 | 0.0012799 | 0.00032078
128 | 0.98041 | -0.1375 | 0.00078354 | 0.00019637
129 | 0.98039 | -0.13767 | 0.0026644 | 0.00066777
130 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00071525 | -0.00017926 | 0.00071527 | 0.000179 | 1.573e-08 | -2.6218e-07 | 0.0010871 | 0.001087 | 0.0010871 | 0.979 | -0.14754 | 0.97903 | -0.14738 | 0.40264
1 | -0.0017492 | -0.00043813 | 0.0017493 | 0.00043796 | 6.8406e-08 | -1.6875e-07 | 0.0026585 | 0.0026585 | 0.0026585 | 0.97903 | -0.14738 | 0.97907 | -0.1471 | 0.98464
2 | 0.005276 | 0.001321 | -0.0052755 | -0.001321 | 4.5609e-07 | 3.246e-08 | 0.0080181 | 0.0080182 | 0.0080182 | 0.97907 | -0.1471 | 0.97898 | -0.14772 | 2.9697
3 | -0.0070252 | -0.0017589 | 0.0070263 | 0.0017592 | 1.025e-06 | 2.1299e-07 | 0.010677 | 0.010677 | 0.010677 | 0.97907 | -0.1471 | 0.97921 | -0.14604 | 3.9543
4 | 0.0018544 | 0.00046449 | -0.0018543 | -0.00046468 | 9.1223e-08 | -1.9628e-07 | 0.0028185 | 0.0028186 | 0.0028186 | 0.97898 | -0.14772 | 0.97893 | -0.14808 | 1.0439
5 | 0.0034211 | 0.00085647 | -0.0034207 | -0.00085664 | 4.7447e-07 | -1.7107e-07 | 0.0051997 | 0.0051998 | 0.0051998 | 0.97898 | -0.14772 | 0.97884 | -0.14873 | 1.9259
6 | 0.0091768 | 0.0022992 | -0.0091732 | -0.0022982 | 3.6089e-06 | 1.0141e-06 | 0.013945 | 0.013945 | 0.013945 | 0.97921 | -0.14604 | 0.97882 | -0.14888 | 5.1648
7 | -0.016203 | -0.0040583 | 0.016206 | 0.0040595 | 3.2785e-06 | 1.1519e-06 | 0.024621 | 0.024621 | 0.024621 | 0.97921 | -0.14604 | 0.97942 | -0.14458 | 9.119
8 | 0.00064099 | 0.0001606 | -0.00064099 | -0.00016065 | 2.1144e-09 | -4.406e-08 | 0.00097432 | 0.00097434 | 0.00097434 | 0.97893 | -0.14808 | 0.97893 | -0.1481 | 0.36087
9 | 0.0012471 | 0.00031232 | -0.0012471 | -0.00031255 | 4.5012e-08 | -2.3495e-07 | 0.0018958 | 0.0018959 | 0.0018959 | 0.97884 | -0.14873 | 0.9788 | -0.14899 | 0.70218
10 | 0.0021735 | 0.00054432 | -0.0021734 | -0.00054445 | 8.9612e-08 | -1.3089e-07 | 0.003304 | 0.0033041 | 0.0033041 | 0.97884 | -0.14873 | 0.9788 | -0.14903 | 1.2237
11 | 0.0074365 | 0.0018629 | -0.0074336 | -0.0018622 | 2.8821e-06 | 6.5442e-07 | 0.011305 | 0.011305 | 0.011305 | 0.97882 | -0.14888 | 0.97842 | -0.15169 | 4.187
12 | -0.022 | -0.0055112 | 0.022006 | 0.0055135 | 6.2157e-06 | 2.2784e-06 | 0.033423 | 0.033423 | 0.033423 | 0.97942 | -0.14458 | 0.9797 | -0.14254 | 12.3788
13 | 0.0057932 | 0.0014518 | -0.0057919 | -0.0014516 | 1.289e-06 | 1.6027e-07 | 0.0088015 | 0.0088016 | 0.0088016 | 0.97942 | -0.14458 | 0.97919 | -0.14619 | 3.2599
14 | 0.13665 | 0.034438 | -0.13641 | -0.034346 | 0.00023868 | 9.1329e-05 | 0.20465 | 0.20465 | 0.20465 | 0.99387 | -0.0425 | 0.99208 | -0.054999 | 37.8987
15 | -0.13716 | -0.034568 | 0.13738 | 0.034649 | 0.00021342 | 8.1663e-05 | 0.20543 | 0.20543 | 0.20543 | 0.99387 | -0.0425 | 0.99546 | -0.031402 | 38.0425
16 | 0.13429 | 0.033816 | -0.13424 | -0.033796 | 5.2407e-05 | 2.005e-05 | 0.20148 | 0.20148 | 0.20148 | 0.99208 | -0.054999 | 0.99168 | -0.057793 | 37.3109
17 | 0.012187 | 0.0030553 | -0.012176 | -0.0030516 | 1.1441e-05 | 3.6829e-06 | 0.018218 | 0.018218 | 0.018218 | 0.99546 | -0.031402 | 0.9945 | -0.038185 | 6.7473
18 | -0.14956 | -0.037705 | 0.14972 | 0.037763 | 0.00015204 | 5.8222e-05 | 0.22365 | 0.22365 | 0.22365 | 0.99546 | -0.031402 | 0.99651 | -0.024153 | 41.4161
19 | 0.13315 | 0.033524 | -0.13301 | -0.033468 | 0.00014557 | 5.5689e-05 | 0.19985 | 0.19985 | 0.19985 | 0.99168 | -0.057793 | 0.99056 | -0.065627 | 37.0097
20 | 0.011345 | 0.0028435 | -0.011342 | -0.0028423 | 3.7292e-06 | 1.1653e-06 | 0.016975 | 0.016976 | 0.016976 | 0.9945 | -0.038185 | 0.99416 | -0.040559 | 6.2872
21 | -0.15018 | -0.037878 | 0.15028 | 0.037918 | 0.00010431 | 3.9945e-05 | 0.22433 | 0.22433 | 0.22433 | 0.99651 | -0.024153 | 0.99722 | -0.019203 | 41.5429
22 | 0.13205 | 0.033227 | -0.13195 | -0.033191 | 9.326e-05 | 3.5674e-05 | 0.19841 | 0.19841 | 0.19841 | 0.99056 | -0.065627 | 0.98984 | -0.070692 | 36.7418
23 | 0.011342 | 0.0028423 | -0.011337 | -0.0028408 | 4.8329e-06 | 1.5105e-06 | 0.016976 | 0.016976 | 0.016976 | 0.99416 | -0.040559 | 0.99373 | -0.043639 | 6.2873
24 | -0.15079 | -0.038044 | 0.15109 | 0.038162 | 0.00030645 | 0.00011736 | 0.22509 | 0.22509 | 0.22509 | 0.99722 | -0.019203 | 0.99931 | -0.0047483 | 41.6827
25 | 0.1308 | 0.032903 | -0.13067 | -0.032852 | 0.00013411 | 5.1296e-05 | 0.19668 | 0.19668 | 0.19668 | 0.98984 | -0.070692 | 0.98879 | -0.078051 | 36.4219
26 | 0.010578 | 0.0026506 | -0.010576 | -0.00265 | 2.0406e-06 | 6.16e-07 | 0.015839 | 0.015839 | 0.015839 | 0.99373 | -0.043639 | 0.99353 | -0.045033 | 5.8664
27 | -0.15172 | -0.038319 | 0.15182 | 0.038358 | 0.00010136 | 3.8818e-05 | 0.22602 | 0.22602 | 0.22602 | 0.99931 | -0.0047483 | 1 | 0 | 41.8561
28 | 0.019809 | 0.0049876 | -0.019803 | -0.0049854 | 5.9047e-06 | 2.1293e-06 | 0.02954 | 0.02954 | 0.02954 | 0.99813 | -0.012972 | 0.99783 | -0.015106 | 10.9407
29 | -0.020392 | -0.0051335 | 0.020401 | 0.0051368 | 8.9733e-06 | 3.2479e-06 | 0.030408 | 0.030408 | 0.030408 | 0.99813 | -0.012972 | 0.99859 | -0.0098227 | 11.2622
30 | 0.019241 | 0.0048446 | -0.019231 | -0.0048409 | 1.0289e-05 | 3.696e-06 | 0.028702 | 0.028702 | 0.028702 | 0.99783 | -0.015106 | 0.99728 | -0.018935 | 10.6303
31 | -0.020706 | -0.0052133 | 0.020706 | 0.0052135 | 6.6586e-07 | 2.4144e-07 | 0.030863 | 0.030863 | 0.030863 | 0.99859 | -0.0098227 | 0.99862 | -0.0095925 | 11.4306
32 | 0.018589 | 0.0046801 | -0.018582 | -0.0046774 | 7.4896e-06 | 2.6772e-06 | 0.027744 | 0.027744 | 0.027744 | 0.99728 | -0.018935 | 0.99686 | -0.02182 | 10.2756
33 | 0.00064177 | 0.00016077 | -0.00064177 | -0.00016084 | 3.1762e-09 | -7.1209e-08 | 0.00095755 | 0.00095758 | 0.00095758 | 0.99728 | -0.018935 | 0.99727 | -0.018971 | 0.35466
34 | -0.020706 | -0.0052135 | 0.020713 | 0.0052159 | 6.7053e-06 | 2.4313e-06 | 0.030863 | 0.030863 | 0.030863 | 0.99862 | -0.0095925 | 0.99895 | -0.0072755 | 11.4306
35 | 0.0011849 | 0.00029667 | -0.0011848 | -0.00029694 | 4.3112e-08 | -2.7137e-07 | 0.0017686 | 0.0017687 | 0.0017687 | 0.99686 | -0.02182 | 0.99682 | -0.022083 | 0.65506
36 | 0.017397 | 0.0043807 | -0.017391 | -0.0043787 | 5.6714e-06 | 2.0057e-06 | 0.025976 | 0.025976 | 0.025976 | 0.99686 | -0.02182 | 0.99653 | -0.024153 | 9.6206
37 | -0.021673 | -0.0054564 | 0.021677 | 0.0054579 | 4.1858e-06 | 1.5257e-06 | 0.032292 | 0.032292 | 0.032292 | 0.99895 | -0.0072755 | 0.99915 | -0.0058932 | 11.9598
38 | 0.016315 | 0.0041091 | -0.016308 | -0.0041066 | 7.1704e-06 | 2.5059e-06 | 0.024369 | 0.024369 | 0.024369 | 0.99653 | -0.024153 | 0.99607 | -0.027298 | 9.0257
39 | -0.02239 | -0.0056366 | 0.022401 | 0.0056406 | 1.0793e-05 | 3.9476e-06 | 0.033354 | 0.033354 | 0.033354 | 0.99915 | -0.0058932 | 0.99965 | -0.0024437 | 12.3533
40 | -0.00062941 | -0.00015774 | 0.00062941 | 0.00015765 | 4.2605e-09 | -9.2548e-08 | 0.00095571 | 0.00095567 | 0.00095571 | 0.97998 | -0.14059 | 0.97998 | -0.14054 | 0.35397
41 | -0.001129 | -0.00028287 | 0.0011291 | 0.00028268 | 2.9459e-08 | -1.9108e-07 | 0.0017143 | 0.0017142 | 0.0017143 | 0.97998 | -0.14054 | 0.98001 | -0.14036 | 0.63493
42 | 0.0032473 | 0.00081365 | -0.003247 | -0.00081377 | 2.7665e-07 | -1.2445e-07 | 0.0049247 | 0.0049247 | 0.0049247 | 0.98117 | -0.13211 | 0.98108 | -0.13272 | 1.824
43 | -0.0082555 | -0.0020688 | 0.008259 | 0.0020697 | 3.5541e-06 | 9.0784e-07 | 0.01252 | 0.01252 | 0.01252 | 0.98117 | -0.13211 | 0.9816 | -0.129 | 4.637
44 | -0.025413 | -0.0063699 | 0.025433 | 0.0063773 | 1.9948e-05 | 7.3997e-06 | 0.038524 | 0.038524 | 0.038524 | 0.9816 | -0.129 | 0.9824 | -0.12333 | 14.2682
45 | 0.017154 | 0.0043001 | -0.017147 | -0.0042976 | 7.1717e-06 | 2.5436e-06 | 0.026004 | 0.026004 | 0.026004 | 0.9816 | -0.129 | 0.98118 | -0.13202 | 9.6312
46 | 0.018563 | 0.004653 | -0.018559 | -0.0046519 | 3.2787e-06 | 1.1769e-06 | 0.028117 | 0.028117 | 0.028117 | 0.9824 | -0.12333 | 0.98222 | -0.12461 | 10.4136
47 | -0.043996 | -0.01103 | 0.04406 | 0.011055 | 6.3898e-05 | 2.4284e-05 | 0.066641 | 0.066641 | 0.066641 | 0.9824 | -0.12333 | 0.98387 | -0.11286 | 24.6817
48 | 0.013906 | 0.0034854 | -0.013903 | -0.0034842 | 3.7724e-06 | 1.2793e-06 | 0.02109 | 0.02109 | 0.02109 | 0.98118 | -0.13202 | 0.9809 | -0.13398 | 7.8111
49 | 0.015881 | 0.0039806 | -0.015876 | -0.0039789 | 4.8917e-06 | 1.7101e-06 | 0.024059 | 0.024059 | 0.024059 | 0.98222 | -0.12461 | 0.98191 | -0.12683 | 8.9108
50 | -0.0451 | -0.011315 | 0.045109 | 0.011319 | 8.6702e-06 | 3.2968e-06 | 0.068215 | 0.068215 | 0.068215 | 0.98387 | -0.11286 | 0.98406 | -0.11148 | 25.2647
51 | 0.012927 | 0.0032395 | -0.012926 | -0.0032393 | 6.8932e-07 | 2.2886e-07 | 0.019609 | 0.019609 | 0.019609 | 0.9809 | -0.13398 | 0.98085 | -0.13436 | 7.2627
52 | 0.012926 | 0.0032395 | -0.01292 | -0.0032374 | 6.0461e-06 | 2.0062e-06 | 0.019588 | 0.019588 | 0.019588 | 0.98191 | -0.12683 | 0.98143 | -0.13021 | 7.2549
53 | -0.04833 | -0.012126 | 0.048369 | 0.012141 | 3.95e-05 | 1.5042e-05 | 0.073085 | 0.073085 | 0.073085 | 0.98406 | -0.11148 | 0.98489 | -0.10559 | 27.0684
54 | 0.011651 | 0.0029198 | -0.011649 | -0.0029192 | 2.0065e-06 | 6.4183e-07 | 0.017675 | 0.017676 | 0.017676 | 0.98085 | -0.13436 | 0.98068 | -0.13561 | 6.5465
55 | -0.050269 | -0.012612 | 0.050329 | 0.012635 | 5.963e-05 | 2.2724e-05 | 0.076032 | 0.076032 | 0.076032 | 0.98387 | -0.11281 | 0.98508 | -0.10427 | 28.1601
56 | 0.046695 | 0.011716 | -0.046676 | -0.011709 | 1.8792e-05 | 7.1511e-06 | 0.070626 | 0.070626 | 0.070626 | 0.98387 | -0.11281 | 0.98347 | -0.11572 | 26.1579
57 | -0.054573 | -0.013699 | 0.054653 | 0.013729 | 7.9543e-05 | 3.0354e-05 | 0.082443 | 0.082443 | 0.082443 | 0.98508 | -0.10427 | 0.98656 | -0.093794 | 30.5345
58 | 0.037263 | 0.0093502 | -0.037251 | -0.0093457 | 1.1811e-05 | 4.467e-06 | 0.056384 | 0.056384 | 0.056384 | 0.98347 | -0.11572 | 0.98314 | -0.118 | 20.8831
59 | 0.0094129 | 0.0023591 | -0.0094109 | -0.0023586 | 2.0069e-06 | 5.7072e-07 | 0.014242 | 0.014242 | 0.014242 | 0.98347 | -0.11572 | 0.98325 | -0.11726 | 5.2748
60 | 0.070567 | 0.017721 | -0.070451 | -0.017677 | 0.00011553 | 4.4228e-05 | 0.10645 | 0.10645 | 0.10645 | 0.98656 | -0.093794 | 0.98489 | -0.10559 | 39.425
61 | -0.12522 | -0.03145 | 0.12543 | 0.031531 | 0.00021141 | 8.0826e-05 | 0.18889 | 0.18889 | 0.18889 | 0.98656 | -0.093794 | 0.98828 | -0.081671 | 34.9797
62 | 0.034362 | 0.0086215 | -0.034331 | -0.0086099 | 3.0877e-05 | 1.1644e-05 | 0.052011 | 0.052011 | 0.052011 | 0.98314 | -0.118 | 0.98223 | -0.12448 | 19.2633
63 | 0.0071078 | 0.0017814 | -0.0071076 | -0.0017813 | 1.7946e-07 | 3.7498e-08 | 0.010757 | 0.010757 | 0.010757 | 0.98325 | -0.11726 | 0.98322 | -0.11744 | 3.9839
64 | 0.022082 | 0.0055357 | -0.022077 | -0.005534 | 4.6089e-06 | 1.6882e-06 | 0.033363 | 0.033363 | 0.033363 | 0.98489 | -0.10559 | 0.98468 | -0.1071 | 12.3566
65 | -0.12675 | -0.031862 | 0.12676 | 0.031864 | 4.1604e-06 | 1.5908e-06 | 0.19088 | 0.19088 | 0.19088 | 0.98828 | -0.081671 | 0.98831 | -0.081435 | 35.3484
66 | 0.032085 | 0.0080471 | -0.032056 | -0.0080362 | 2.915e-05 | 1.0962e-05 | 0.048609 | 0.048609 | 0.048609 | 0.98223 | -0.12448 | 0.98131 | -0.13104 | 18.0035
67 | 0.019369 | 0.0048553 | -0.019368 | -0.0048548 | 1.1909e-06 | 4.2972e-07 | 0.02927 | 0.02927 | 0.02927 | 0.98468 | -0.1071 | 0.98462 | -0.10754 | 10.8409
68 | -0.12814 | -0.032211 | 0.1282 | 0.032234 | 6.0424e-05 | 2.3107e-05 | 0.19297 | 0.19297 | 0.19297 | 0.98831 | -0.081435 | 0.98879 | -0.078051 | 35.7349
69 | 0.028776 | 0.0072141 | -0.02875 | -0.0072042 | 2.6437e-05 | 9.8872e-06 | 0.043636 | 0.043636 | 0.043636 | 0.98131 | -0.13104 | 0.98038 | -0.13768 | 16.1615
70 | 0.0034228 | 0.00085745 | -0.0034221 | -0.00085767 | 6.1737e-07 | -2.1986e-07 | 0.0052087 | 0.0052088 | 0.0052088 | 0.97779 | -0.15625 | 0.97761 | -0.15755 | 1.9292
71 | -0.0040423 | -0.0010127 | 0.0040426 | 0.0010127 | 2.9417e-07 | -4.3128e-08 | 0.0061516 | 0.0061515 | 0.0061516 | 0.97779 | -0.15625 | 0.97786 | -0.15573 | 2.2784
72 | -0.0056289 | -0.0014103 | 0.0056293 | 0.0014103 | 3.5157e-07 | 3.8874e-08 | 0.0085654 | 0.0085654 | 0.0085654 | 0.97786 | -0.15573 | 0.97792 | -0.15527 | 3.1724
73 | -0.0056293 | -0.0014103 | 0.0056304 | 0.0014104 | 1.1203e-06 | 1.2379e-07 | 0.0085654 | 0.0085652 | 0.0085654 | 0.97792 | -0.15527 | 0.97813 | -0.15383 | 3.1724
74 | -0.0067693 | -0.0016958 | 0.0067701 | 0.001696 | 8.8102e-07 | 1.7172e-07 | 0.010298 | 0.010298 | 0.010298 | 0.97813 | -0.15383 | 0.97826 | -0.15289 | 3.814
75 | -0.0067701 | -0.001696 | 0.0067713 | 0.0016962 | 1.1299e-06 | 2.2015e-07 | 0.010298 | 0.010298 | 0.010298 | 0.97826 | -0.15289 | 0.97842 | -0.15169 | 3.814
76 | 0.0053913 | 0.001351 | -0.0053909 | -0.0013509 | 3.5047e-07 | 2.7551e-08 | 0.0081544 | 0.0081544 | 0.0081544 | 0.9838 | -0.11339 | 0.98373 | -0.11386 | 3.0202
77 | -0.0084649 | -0.0021213 | 0.008466 | 0.0021216 | 1.0105e-06 | 2.632e-07 | 0.012803 | 0.012803 | 0.012803 | 0.9838 | -0.11339 | 0.98392 | -0.11253 | 4.742
78 | 0.0032596 | 0.00081677 | -0.0032595 | -0.00081678 | 2.32e-08 | -1.0494e-08 | 0.0049304 | 0.0049304 | 0.0049304 | 0.98373 | -0.11386 | 0.98372 | -0.11391 | 1.8261
79 | -0.010213 | -0.0025594 | 0.010214 | 0.0025597 | 1.1757e-06 | 3.5186e-07 | 0.015445 | 0.015445 | 0.015445 | 0.98392 | -0.11253 | 0.98404 | -0.11169 | 5.7204
80 | 0.0015984 | 0.00040046 | -0.0015983 | -0.00040058 | 3.9613e-08 | -1.2264e-07 | 0.0024177 | 0.0024178 | 0.0024178 | 0.98372 | -0.11391 | 0.9837 | -0.11409 | 0.89546
81 | -0.012185 | -0.0030536 | 0.012185 | 0.0030537 | 4.2962e-08 | 1.3948e-08 | 0.018425 | 0.018425 | 0.018425 | 0.98404 | -0.11169 | 0.98404 | -0.11167 | 6.8241
82 | -0.013711 | -0.0034362 | 0.013715 | 0.0034376 | 4.1561e-06 | 1.4016e-06 | 0.020733 | 0.020733 | 0.020733 | 0.98404 | -0.11167 | 0.98435 | -0.10948 | 7.679
83 | -0.016804 | -0.0042116 | 0.016804 | 0.0042116 | 9.4658e-08 | 3.3418e-08 | 0.025402 | 0.025402 | 0.025402 | 0.98435 | -0.10948 | 0.98435 | -0.10944 | 9.408
84 | -0.0011291 | -0.00028268 | 0.0011291 | 0.00028257 | 1.6604e-08 | -1.0771e-07 | 0.0017142 | 0.0017142 | 0.0017142 | 0.98001 | -0.14036 | 0.98002 | -0.14025 | 0.63491
85 | -0.0017487 | -0.00043785 | 0.0017487 | 0.00043775 | 4.3541e-08 | -1.0799e-07 | 0.0026549 | 0.0026549 | 0.0026549 | 0.98002 | -0.14025 | 0.98005 | -0.14007 | 0.98331
86 | -0.0021953 | -0.00054967 | 0.0021954 | 0.00054956 | 8.2032e-08 | -1.1758e-07 | 0.003333 | 0.0033329 | 0.003333 | 0.98005 | -0.14007 | 0.98009 | -0.1398 | 1.2344
87 | -0.022819 | -0.0057454 | 0.022827 | 0.0057483 | 7.7939e-06 | 2.8558e-06 | 0.033976 | 0.033976 | 0.033976 | 0.99965 | -0.0024437 | 1 | 0 | 12.5839
88 | 0.018348 | 0.0045992 | -0.018343 | -0.0045974 | 4.8134e-06 | 1.7237e-06 | 0.027729 | 0.027729 | 0.027729 | 0.98462 | -0.10754 | 0.98435 | -0.10944 | 10.2699
89 | 0.013547 | 0.0034021 | -0.013541 | -0.0034001 | 5.9684e-06 | 2.0022e-06 | 0.020417 | 0.020417 | 0.020417 | 0.98743 | -0.087931 | 0.98698 | -0.091102 | 7.5619
90 | -0.015357 | -0.0038557 | 0.015487 | 0.0039008 | 0.00013033 | 4.5096e-05 | 0.023144 | 0.023143 | 0.023144 | 0.98743 | -0.087931 | 0.99607 | -0.027298 | 8.572
91 | 0.013437 | 0.0033741 | -0.013433 | -0.0033728 | 3.6499e-06 | 1.2218e-06 | 0.02026 | 0.020261 | 0.020261 | 0.98698 | -0.091102 | 0.9867 | -0.093057 | 7.5039
92 | 0.013433 | 0.0033728 | -0.013431 | -0.003372 | 2.5804e-06 | 8.6382e-07 | 0.020261 | 0.020261 | 0.020261 | 0.9867 | -0.093057 | 0.98651 | -0.09444 | 7.5039
93 | 0.013431 | 0.003372 | -0.01342 | -0.0033685 | 1.0356e-05 | 3.4674e-06 | 0.020261 | 0.020261 | 0.020261 | 0.98651 | -0.09444 | 0.98572 | -0.099994 | 7.504
94 | 0.012819 | 0.0032178 | -0.012814 | -0.0032162 | 5.0824e-06 | 1.6777e-06 | 0.019353 | 0.019353 | 0.019353 | 0.98572 | -0.099994 | 0.98532 | -0.10285 | 7.1679
95 | -0.0060445 | -0.0015149 | 0.0060446 | 0.0015149 | 8.835e-08 | 1.3389e-08 | 0.0092426 | 0.0092426 | 0.0092426 | 0.97313 | -0.18994 | 0.97315 | -0.18984 | 3.4232
96 | 0.00090829 | 0.00022755 | -0.00090828 | -0.00022764 | 8.8888e-09 | -8.8335e-08 | 0.0013888 | 0.0013888 | 0.0013888 | 0.97315 | -0.18984 | 0.97314 | -0.18991 | 0.51439
97 | -0.0069529 | -0.0017425 | 0.0069752 | 0.0017471 | 2.2299e-05 | 4.6349e-06 | 0.010631 | 0.01063 | 0.010631 | 0.97315 | -0.18984 | 0.97637 | -0.16669 | 3.9376
98 | -0.0094713 | -0.0023727 | 0.009474 | 0.0023735 | 2.6675e-06 | 7.6929e-07 | 0.014434 | 0.014434 | 0.014434 | 0.97637 | -0.16669 | 0.97665 | -0.16466 | 5.346
99 | -0.009474 | -0.0023735 | 0.0094998 | 0.0023809 | 2.5794e-05 | 7.4309e-06 | 0.014434 | 0.014433 | 0.014434 | 0.97665 | -0.16466 | 0.9794 | -0.14501 | 5.346
100 | -0.0068304 | -0.0017118 | 0.0068318 | 0.0017121 | 1.3658e-06 | 2.5704e-07 | 0.010255 | 0.010255 | 0.010255 | 0.99111 | -0.062129 | 0.99131 | -0.060684 | 3.7981
101 | 0.0051522 | 0.0012912 | -0.0051521 | -0.0012912 | 1.0363e-07 | 4.0907e-09 | 0.0077354 | 0.0077354 | 0.0077354 | 0.99111 | -0.062129 | 0.99109 | -0.062274 | 2.8649
102 | -0.0068318 | -0.0017121 | 0.0068339 | 0.0017125 | 2.0664e-06 | 3.8866e-07 | 0.010255 | 0.010255 | 0.010255 | 0.99131 | -0.060684 | 0.99162 | -0.058499 | 3.7981
103 | -0.02321 | -0.0058149 | 0.023225 | 0.0058206 | 1.5604e-05 | 5.7481e-06 | 0.035251 | 0.035251 | 0.035251 | 0.9797 | -0.14254 | 0.98038 | -0.13768 | 13.056
104 | 0.0012038 | 0.00030135 | -0.0012038 | -0.00030169 | 6.0493e-08 | -3.4188e-07 | 0.0018283 | 0.0018284 | 0.0018284 | 0.9797 | -0.14254 | 0.97965 | -0.1429 | 0.6772
105 | 0.0055247 | 0.0013836 | -0.0055236 | -0.0013835 | 1.0959e-06 | 1.0659e-07 | 0.008385 | 0.0083851 | 0.0083851 | 0.98038 | -0.13768 | 0.98018 | -0.13911 | 3.1056
106 | -0.0045201 | -0.0011325 | 0.0045209 | 0.0011325 | 7.4326e-07 | -3.4166e-08 | 0.0068559 | 0.0068558 | 0.0068559 | 0.98104 | -0.13299 | 0.98121 | -0.1318 | 2.5392
107 | 0.0045201 | 0.0011325 | -0.0045197 | -0.0011325 | 4.4221e-07 | -2.0271e-08 | 0.0068559 | 0.0068559 | 0.0068559 | 0.98104 | -0.13299 | 0.98094 | -0.13369 | 2.5392
108 | -0.0075658 | -0.0018956 | 0.007567 | 0.0018959 | 1.188e-06 | 2.7422e-07 | 0.011473 | 0.011473 | 0.011473 | 0.98121 | -0.1318 | 0.98137 | -0.13066 | 4.2494
109 | 0.001928 | 0.00048298 | -0.0019279 | -0.00048317 | 9.348e-08 | -1.8515e-07 | 0.0029245 | 0.0029246 | 0.0029246 | 0.98094 | -0.13369 | 0.9809 | -0.13404 | 1.0832
110 | 0.0041767 | 0.001046 | -0.0041763 | -0.001046 | 3.9462e-07 | -4.6487e-08 | 0.0063404 | 0.0063404 | 0.0063404 | 0.98018 | -0.13911 | 0.98009 | -0.1398 | 2.3483
111 | -0.012919 | -0.0032372 | 0.01292 | 0.0032374 | 8.0335e-07 | 2.6658e-07 | 0.019588 | 0.019588 | 0.019588 | 0.98137 | -0.13066 | 0.98143 | -0.13021 | 7.2549
112 | 0.011195 | 0.002806 | -0.01119 | -0.0028044 | 5.1088e-06 | 1.6083e-06 | 0.017001 | 0.017001 | 0.017001 | 0.97986 | -0.14171 | 0.9794 | -0.14501 | 6.2965
113 | -0.011556 | -0.0028966 | 0.011565 | 0.0028994 | 8.8149e-06 | 2.8121e-06 | 0.017549 | 0.017549 | 0.017549 | 0.97986 | -0.14171 | 0.98063 | -0.13621 | 6.4997
114 | -0.011565 | -0.0028994 | 0.01157 | 0.002901 | 4.9524e-06 | 1.5795e-06 | 0.017549 | 0.017549 | 0.017549 | 0.98063 | -0.13621 | 0.98106 | -0.13312 | 6.4997
115 | -0.011839 | -0.0029683 | 0.011861 | 0.0029755 | 2.2401e-05 | 7.2071e-06 | 0.017956 | 0.017956 | 0.017956 | 0.98106 | -0.13312 | 0.98298 | -0.11948 | 6.6505
116 | -0.011861 | -0.0029755 | 0.011866 | 0.002977 | 4.6517e-06 | 1.4959e-06 | 0.017956 | 0.017956 | 0.017956 | 0.98298 | -0.11948 | 0.98337 | -0.11665 | 6.6503
117 | -0.012042 | -0.0030213 | 0.012065 | 0.0030288 | 2.3096e-05 | 7.4662e-06 | 0.018223 | 0.018223 | 0.018223 | 0.98337 | -0.11665 | 0.98532 | -0.10285 | 6.7494
118 | -0.00021757 | -5.4528e-05 | 0.00021757 | 5.4335e-05 | 1.0267e-09 | -1.9376e-07 | 0.00032857 | 0.00032851 | 0.00032857 | 0.98531 | -0.10291 | 0.98532 | -0.10287 | 0.12169
119 | -0.00059456 | -0.00014882 | 0.00059456 | 0.00014877 | 1.9403e-09 | -4.8385e-08 | 0.00089783 | 0.00089782 | 0.00089783 | 0.98532 | -0.10287 | 0.98532 | -0.10285 | 0.33253
120 | 0.0014498 | 0.00036308 | -0.0014497 | -0.00036333 | 6.5688e-08 | -2.4711e-07 | 0.0022039 | 0.002204 | 0.002204 | 0.9788 | -0.14903 | 0.97875 | -0.14935 | 0.8163
121 | 0.006734 | 0.0016873 | -0.006733 | -0.0016871 | 9.8563e-07 | 1.8822e-07 | 0.010218 | 0.010218 | 0.010218 | 0.98068 | -0.13561 | 0.98053 | -0.13666 | 3.7843
122 | 0.0042457 | 0.0010638 | -0.0042456 | -0.0010638 | 1.1605e-07 | -1.1871e-08 | 0.0064431 | 0.0064431 | 0.0064431 | 0.98053 | -0.13666 | 0.9805 | -0.13686 | 2.3863
123 | 0.0034483 | 0.00086398 | -0.003448 | -0.00086409 | 3.0322e-07 | -1.0715e-07 | 0.0052331 | 0.0052332 | 0.0052332 | 0.9805 | -0.13686 | 0.98041 | -0.1375 | 1.9382
124 | -0.0068339 | -0.0017125 | 0.0068388 | 0.0017134 | 4.9591e-06 | 9.3167e-07 | 0.010255 | 0.010254 | 0.010255 | 0.99162 | -0.058499 | 0.99236 | -0.053257 | 3.7981
125 | -0.0080436 | -0.0020154 | 0.0080475 | 0.0020163 | 3.9531e-06 | 9.5747e-07 | 0.012061 | 0.012061 | 0.012061 | 0.99236 | -0.053257 | 0.99287 | -0.049706 | 4.467
126 | -0.0080475 | -0.0020163 | 0.008051 | 0.0020172 | 3.434e-06 | 8.3127e-07 | 0.012061 | 0.012061 | 0.012061 | 0.99287 | -0.049706 | 0.9933 | -0.046622 | 4.4669
127 | -0.0092938 | -0.0023286 | 0.0092959 | 0.0023292 | 2.0445e-06 | 5.6749e-07 | 0.013922 | 0.013922 | 0.013922 | 0.9933 | -0.046622 | 0.99353 | -0.045033 | 5.1564
128 | 0.0026645 | 0.00066771 | -0.0026644 | -0.00066777 | 6.2733e-08 | -5.3391e-08 | 0.004044 | 0.004044 | 0.004044 | 0.98041 | -0.1375 | 0.98039 | -0.13767 | 1.4978

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.17596 | 0.044235

## res_load
| p_mw | q_mvar
0 | 0.00071525 | 0.00017926
1 | 0.0010339 | 0.00025913
2 | 0.0012133 | 0.00030408
3 | 0.0017367 | 0.00043526
4 | 0.00051878 | 0.00013002
5 | 0.0021163 | 0.0005304
6 | 0.001084 | 0.00027167
7 | 0.00083033 | 0.0002081
8 | 0.00045845 | 0.0001149
9 | 0.00096299 | 0.00024135
10 | 0.00050603 | 0.00012682
11 | 0.0011493 | 0.00028804
12 | 0.00075897 | 0.00019021
13 | 0.00062891 | 0.00015762
14 | 0.00058231 | 0.00014594
15 | 0.00056214 | 0.00014089
16 | 0.00030519 | 7.6488e-05
17 | 0.00064177 | 0.00016084
18 | 0.00095933 | 0.00024043
19 | 0.0011848 | 0.00029694
20 | 0.0010758 | 0.00026961
21 | 0.00071325 | 0.00017876
22 | 0.00062941 | 0.00015774
23 | 0.00049963 | 0.00012522
24 | 0.0050082 | 0.0012552
25 | 0.003247 | 0.00081377
26 | 0.0032405 | 0.00081214
27 | 0.0026784 | 0.00067126
28 | 0.0010408 | 0.00026086
29 | 0.00097611 | 0.00024464
30 | 0.0029504 | 0.00073943
31 | 0.0032206 | 0.00080715
32 | 0.0012747 | 0.00031947
33 | 0.0035745 | 0.00089585
34 | 0.0042441 | 0.0010637
35 | 0.0028896 | 0.0007242
36 | 0.0023031 | 0.00057721
37 | 0.0013225 | 0.00033145
38 | 0.0022454 | 0.00056274
39 | 0.0071076 | 0.0017813
40 | 0.0027082 | 0.00067873
41 | 0.0013859 | 0.00034735
42 | 0.0032799 | 0.00082203
43 | 0.00061958 | 0.00015528
44 | 0.0034221 | 0.00085767
45 | 0.0015863 | 0.00039756
46 | 0.0011389 | 0.00028543
47 | 0.0030737 | 0.00077033
48 | 0.0021314 | 0.00053418
49 | 0.0017468 | 0.00043778
50 | 0.0016612 | 0.00041633
51 | 0.0019708 | 0.00049393
52 | 0.0015983 | 0.00040058
53 | 0.0015264 | 0.00038255
54 | 0.0030882 | 0.00077398
55 | 0.00061958 | 0.00015528
56 | 0.00066237 | 0.00016601
57 | 0.00044659 | 0.00011193
58 | 0.00041837 | 0.00010485
59 | 0.00051291 | 0.00012855
60 | 0.0010202 | 0.00025568
61 | 0.0015395 | 0.00038582
62 | 0.0024653 | 0.00061787
63 | 0.0018099 | 0.0004536
64 | 0.00010392 | 2.6044e-05
65 | 0.00082126 | 0.00020583
66 | 0.00060115 | 0.00015066
67 | 0.0060445 | 0.0015149
68 | 0.00090828 | 0.00022764
69 | 0.0024961 | 0.00062559
70 | 0.0016782 | 0.0004206
71 | 0.0051521 | 0.0012912
72 | 0.0057919 | 0.0014516
73 | 0.0012038 | 0.00030169
74 | 0.0030449 | 0.00076313
75 | 0.0025917 | 0.00064955
76 | 0.0013469 | 0.00033756
77 | 0.0053519 | 0.0013413
78 | 0.0019279 | 0.00048317
79 | 0.00036134 | 9.0559e-05
80 | 0.0016899 | 0.00042352
81 | 0.00026866 | 6.7332e-05
82 | 0.00017676 | 4.43e-05
83 | 0.00021757 | 5.4528e-05
84 | 0.00037699 | 9.4483e-05
85 | 0.00015413 | 3.863e-05
86 | 0.00072366 | 0.00018137
87 | 0.0014497 | 0.00036333
88 | 0.0012471 | 0.00031255
89 | 0.00064099 | 0.00016065
90 | 0.0019809 | 0.00049646
91 | 0.0049152 | 0.0012319
92 | 0.0024872 | 0.00062336
93 | 0.00079729 | 0.00019982
94 | 0.0012048 | 0.00030194
95 | 0.0012428 | 0.00031149
96 | 0.0012799 | 0.00032078
97 | 0.00078354 | 0.00019637
98 | 0.0026644 | 0.00066777

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1