## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4163-10_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4163-10_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4163-10_0_4_node_47 | 0.4 | n |  | TRUE
3 | bus_LV_4163-10_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_4163-10_0_4_node_57 | 0.4 | n |  | TRUE
5 | bus_LV_4163-10_0_4_node_45 | 0.4 | n |  | TRUE
6 | bus_LV_4163-10_0_4_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_4163-10_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_4163-10_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_4163-10_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_4163-10_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_4163-10_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_4163-10_0_4_node_52 | 0.4 | n |  | TRUE
13 | bus_LV_4163-10_0_4_node_51 | 0.4 | n |  | TRUE
14 | bus_LV_4163-10_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_4163-10_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_4163-10_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_4163-10_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_4163-10_0_4_node_56 | 0.4 | n |  | TRUE
19 | bus_LV_4163-10_0_4_node_46 | 0.4 | n |  | TRUE
20 | bus_LV_4163-10_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_4163-10_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_4163-10_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_4163-10_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_4163-10_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_4163-10_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_4163-10_0_4_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_4163-10_0_4_node_49 | 0.4 | n |  | TRUE
28 | bus_LV_4163-10_0_4_node_70 | 0.4 | n |  | TRUE
29 | bus_LV_4163-10_0_4_node_72 | 0.4 | n |  | TRUE
30 | bus_LV_4163-10_0_4_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_4163-10_0_4_node_48 | 0.4 | n |  | TRUE
32 | bus_LV_4163-10_0_4_node_69 | 0.4 | n |  | TRUE
33 | bus_LV_4163-10_0_4_node_71 | 0.4 | n |  | TRUE
34 | bus_LV_4163-10_0_4_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_4163-10_0_4_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_4163-10_0_4_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_4163-10_0_4_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_4163-10_0_4_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_4163-10_0_4_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_4163-10_0_4_node_39 | 0.4 | n |  | TRUE
41 | bus_LV_4163-10_0_4_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_4163-10_0_4_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_4163-10_0_4_node_55 | 0.4 | n |  | TRUE
44 | bus_LV_4163-10_0_4_node_63 | 0.4 | n |  | TRUE
45 | bus_LV_4163-10_0_4_node_66 | 0.4 | n |  | TRUE
46 | bus_LV_4163-10_0_4_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_4163-10_0_4_node_41 | 0.4 | n |  | TRUE
48 | bus_LV_4163-10_0_4_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_4163-10_0_4_node_27 | 0.4 | n |  | TRUE
50 | bus_LV_4163-10_0_4_node_54 | 0.4 | n |  | TRUE
51 | bus_LV_4163-10_0_4_node_58 | 0.4 | n |  | TRUE
52 | bus_LV_4163-10_0_4_node_26 | 0.4 | n |  | TRUE
53 | bus_LV_4163-10_0_4_node_28 | 0.4 | n |  | TRUE
54 | bus_LV_4163-10_0_4_node_30 | 0.4 | n |  | TRUE
55 | bus_LV_4163-10_0_4_node_33 | 0.4 | n |  | TRUE
56 | bus_LV_4163-10_0_4_node_62 | 0.4 | n |  | TRUE
57 | bus_LV_4163-10_0_4_node_75 | 0.4 | n |  | TRUE
58 | bus_LV_4163-10_0_4_node_34 | 0.4 | n |  | TRUE
59 | bus_LV_4163-10_0_4_node_35 | 0.4 | n |  | TRUE
60 | bus_LV_4163-10_0_4_node_38 | 0.4 | n |  | TRUE
61 | bus_LV_4163-10_0_4_node_59 | 0.4 | n |  | TRUE
62 | bus_LV_4163-10_0_4_node_36 | 0.4 | n |  | TRUE
63 | bus_LV_4163-10_0_4_node_37 | 0.4 | n |  | TRUE
64 | bus_LV_4163-10_0_4_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_4163-10_0_4_node_60 | 0.4 | n |  | TRUE
66 | bus_LV_4163-10_0_4_node_64 | 0.4 | n |  | TRUE
67 | bus_LV_4163-10_0_4_node_65 | 0.4 | n |  | TRUE
68 | bus_LV_4163-10_0_4_node_43 | 0.4 | n |  | TRUE
69 | bus_LV_4163-10_0_4_node_44 | 0.4 | n |  | TRUE
70 | bus_LV_4163-10_0_4_node_53 | 0.4 | n |  | TRUE
71 | bus_LV_4163-10_0_4_node_76 | 0.4 | n |  | TRUE
72 | bus_LV_4163-10_0_4_node_74 | 0.4 | n |  | TRUE
73 | bus_LV_4163-10_0_4_node_68 | 0.4 | n |  | TRUE
74 | bus_LV_4163-10_0_4_node_73 | 0.4 | n |  | TRUE
75 | bus_MV_304_0_node_10 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4163-10_0_4_load_0 | 0 | 0.0003269 | 8.1929e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4163-10_0_4_load_1 | 1 | 0.00081636 | 0.0002046 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4163-10_0_4_load_47 | 2 | 0.0043332 | 0.001086 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4163-10_0_4_load_2 | 3 | 0.00042305 | 0.00010603 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4163-10_0_4_load_57 | 4 | 0.0036173 | 0.00090658 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4163-10_0_4_load_3 | 6 | 0.00051149 | 0.00012819 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4163-10_0_4_load_4 | 7 | 0.0018602 | 0.00046622 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4163-10_0_4_load_5 | 8 | 0.0034693 | 0.0008695 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4163-10_0_4_load_6 | 9 | 0.0014945 | 0.00037455 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4163-10_0_4_load_7 | 10 | 0.0015322 | 0.00038402 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4163-10_0_4_load_8 | 11 | 0.0014941 | 0.00037446 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4163-10_0_4_load_52 | 12 | 0.0021679 | 0.00054333 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4163-10_0_4_load_51 | 13 | 0.0023025 | 0.00057707 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4163-10_0_4_load_9 | 14 | 0.0052917 | 0.0013262 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4163-10_0_4_load_10 | 15 | 0.001211 | 0.00030351 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4163-10_0_4_load_11 | 16 | 0.0021384 | 0.00053593 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4163-10_0_4_load_12 | 17 | 0.0016772 | 0.00042034 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4163-10_0_4_load_56 | 18 | 0.0031029 | 0.00077767 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4163-10_0_4_load_13 | 20 | 0.0049602 | 0.0012431 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4163-10_0_4_load_14 | 21 | 0.002218 | 0.00055588 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4163-10_0_4_load_16 | 23 | 0.0013192 | 0.00033061 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4163-10_0_4_load_17 | 24 | 0.0028329 | 0.00071 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4163-10_0_4_load_31 | 26 | 0.00094709 | 0.00023736 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4163-10_0_4_load_49 | 27 | 0.0014631 | 0.00036668 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4163-10_0_4_load_72 | 29 | 0.00407 | 0.0010201 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4163-10_0_4_load_32 | 30 | 0.0027799 | 0.00069671 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4163-10_0_4_load_48 | 31 | 0.0020446 | 0.00051242 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4163-10_0_4_load_69 | 32 | 0.0027591 | 0.0006915 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4163-10_0_4_load_71 | 33 | 0.0020598 | 0.00051623 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4163-10_0_4_load_19 | 34 | 0.0023901 | 0.00059901 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4163-10_0_4_load_22 | 37 | 0.0040616 | 0.0010179 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4163-10_0_4_load_24 | 38 | 0.0028922 | 0.00072487 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4163-10_0_4_load_25 | 39 | 0.003085 | 0.00077316 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4163-10_0_4_load_29 | 42 | 0.0029705 | 0.00074448 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4163-10_0_4_load_55 | 43 | 0.0021077 | 0.00052823 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4163-10_0_4_load_63 | 44 | 0.0034198 | 0.00085708 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4163-10_0_4_load_66 | 45 | 0.0097363 | 0.0024401 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4163-10_0_4_load_40 | 46 | 0.0010377 | 0.00026007 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4163-10_0_4_load_41 | 47 | 0.0028216 | 0.00070716 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4163-10_0_4_load_42 | 48 | 0.0021102 | 0.00052887 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4163-10_0_4_load_27 | 49 | 0.00076929 | 0.0001928 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4163-10_0_4_load_54 | 50 | 0.0037848 | 0.00094855 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4163-10_0_4_load_58 | 51 | 0.0036698 | 0.00091975 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4163-10_0_4_load_26 | 52 | 0.00263 | 0.00065914 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4163-10_0_4_load_28 | 53 | 0.0033976 | 0.00085151 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4163-10_0_4_load_30 | 54 | 0.0011446 | 0.00028687 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4163-10_0_4_load_33 | 55 | 0.0025024 | 0.00062715 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4163-10_0_4_load_62 | 56 | 0.0027597 | 0.00069165 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4163-10_0_4_load_75 | 57 | 0.0022149 | 0.00055509 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4163-10_0_4_load_34 | 58 | 0.0022185 | 0.00055601 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4163-10_0_4_load_35 | 59 | 0.0022307 | 0.00055906 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4163-10_0_4_load_38 | 60 | 0.0016817 | 0.00042148 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4163-10_0_4_load_59 | 61 | 0.0011347 | 0.00028437 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4163-10_0_4_load_36 | 62 | 0.0040966 | 0.0010267 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4163-10_0_4_load_37 | 63 | 0.0021741 | 0.00054489 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4163-10_0_4_load_50 | 64 | 0.0020806 | 0.00052144 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4163-10_0_4_load_60 | 65 | 0.0010826 | 0.00027132 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4163-10_0_4_load_64 | 66 | 0.00091017 | 0.00022811 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4163-10_0_4_load_65 | 67 | 0.0010693 | 0.00026799 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4163-10_0_4_load_43 | 68 | 0.003215 | 0.00080576 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4163-10_0_4_load_44 | 69 | 0.0065829 | 0.0016498 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4163-10_0_4_load_53 | 70 | 0.0041092 | 0.0010299 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4163-10_0_4_load_76 | 71 | 0.0017807 | 0.0004463 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4163-10_0_4_load_74 | 72 | 0.0017168 | 0.00043027 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4163-10_0_4_load_68 | 73 | 0.0028126 | 0.00070491 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4163-10_0_4_load_73 | 74 | 0.0029241 | 0.00073286 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4163-10_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0027775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_4163-10_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.28792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_4163-10_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.011097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_4163-10_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.036103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_4163-10_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.026991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_4163-10_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.0016379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_4163-10_0_4_line_6 | NAYY 4x150 SE | 4 | 51 | 0.031611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_4163-10_0_4_line_7 | NAYY 4x150 SE | 5 | 68 | 0.012427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_4163-10_0_4_line_8 | NAYY 4x150 SE | 6 | 7 | 0.023594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_4163-10_0_4_line_9 | NAYY 4x150 SE | 8 | 9 | 0.0019042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_4163-10_0_4_line_10 | NAYY 4x150 SE | 9 | 10 | 0.019857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_4163-10_0_4_line_11 | NAYY 4x150 SE | 10 | 11 | 0.01855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_4163-10_0_4_line_12 | NAYY 4x150 SE | 11 | 12 | 0.018747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_4163-10_0_4_line_13 | NAYY 4x150 SE | 12 | 13 | 0.0011158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_4163-10_0_4_line_14 | NAYY 4x150 SE | 13 | 54 | 0.0021398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_4163-10_0_4_line_15 | NAYY 4x150 SE | 14 | 15 | 0.0092384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_4163-10_0_4_line_16 | NAYY 4x150 SE | 14 | 16 | 0.011913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_4163-10_0_4_line_17 | NAYY 4x150 SE | 15 | 17 | 0.0087494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_4163-10_0_4_line_18 | NAYY 4x150 SE | 17 | 18 | 0.020802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_4163-10_0_4_line_19 | NAYY 4x150 SE | 18 | 19 | 0.0067103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_4163-10_0_4_line_20 | NAYY 4x150 SE | 19 | 70 | 0.014461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_4163-10_0_4_line_21 | NAYY 4x150 SE | 19 | 69 | 0.025279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_4163-10_0_4_line_22 | NAYY 4x150 SE | 20 | 21 | 0.019443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_4163-10_0_4_line_23 | NAYY 4x150 SE | 20 | 22 | 0.02255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_4163-10_0_4_line_24 | NAYY 4x150 SE | 21 | 23 | 0.0060053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_4163-10_0_4_line_25 | NAYY 4x150 SE | 22 | 24 | 0.011839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_4163-10_0_4_line_26 | NAYY 4x150 SE | 22 | 25 | 0.028547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_4163-10_0_4_line_27 | NAYY 4x150 SE | 23 | 26 | 0.021555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_4163-10_0_4_line_28 | NAYY 4x150 SE | 24 | 27 | 0.024914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
29 | LV_4163-10_0_4_line_29 | NAYY 4x150 SE | 25 | 28 | 0.049694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_4163-10_0_4_line_30 | NAYY 4x150 SE | 25 | 29 | 0.017638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_4163-10_0_4_line_31 | NAYY 4x150 SE | 26 | 30 | 0.012085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_4163-10_0_4_line_32 | NAYY 4x150 SE | 27 | 31 | 0.015453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_4163-10_0_4_line_33 | NAYY 4x150 SE | 28 | 32 | 0.017176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_4163-10_0_4_line_34 | NAYY 4x150 SE | 29 | 33 | 0.029238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_4163-10_0_4_line_35 | NAYY 4x150 SE | 30 | 55 | 0.0024526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_4163-10_0_4_line_36 | NAYY 4x150 SE | 31 | 46 | 0.0076333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_4163-10_0_4_line_37 | NAYY 4x150 SE | 32 | 73 | 0.026871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_4163-10_0_4_line_38 | NAYY 4x150 SE | 33 | 74 | 0.0011241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_4163-10_0_4_line_39 | NAYY 4x150 SE | 34 | 35 | 0.01575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_4163-10_0_4_line_40 | NAYY 4x150 SE | 34 | 36 | 0.025018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_4163-10_0_4_line_41 | NAYY 4x150 SE | 35 | 37 | 0.0073796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_4163-10_0_4_line_42 | NAYY 4x150 SE | 36 | 38 | 0.021519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_4163-10_0_4_line_43 | NAYY 4x150 SE | 36 | 39 | 0.013606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_4163-10_0_4_line_44 | NAYY 4x150 SE | 37 | 40 | 0.029936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_4163-10_0_4_line_45 | NAYY 4x150 SE | 38 | 44 | 0.032387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_4163-10_0_4_line_46 | NAYY 4x150 SE | 39 | 45 | 0.027932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_4163-10_0_4_line_47 | NAYY 4x150 SE | 40 | 46 | 0.015949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_4163-10_0_4_line_48 | NAYY 4x150 SE | 40 | 47 | 0.035031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_4163-10_0_4_line_49 | NAYY 4x150 SE | 40 | 48 | 0.042106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_4163-10_0_4_line_50 | NAYY 4x150 SE | 41 | 42 | 0.015163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_4163-10_0_4_line_51 | NAYY 4x150 SE | 41 | 43 | 0.024337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_4163-10_0_4_line_52 | NAYY 4x150 SE | 42 | 49 | 0.011028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_4163-10_0_4_line_53 | NAYY 4x150 SE | 43 | 50 | 0.038705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
54 | LV_4163-10_0_4_line_54 | NAYY 4x150 SE | 44 | 51 | 0.02802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_4163-10_0_4_line_55 | NAYY 4x150 SE | 47 | 64 | 0.0093411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_4163-10_0_4_line_56 | NAYY 4x150 SE | 48 | 66 | 0.025144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_4163-10_0_4_line_57 | NAYY 4x150 SE | 49 | 52 | 0.017766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_4163-10_0_4_line_58 | NAYY 4x150 SE | 50 | 70 | 0.02194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
59 | LV_4163-10_0_4_line_59 | NAYY 4x150 SE | 52 | 53 | 0.0012264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_4163-10_0_4_line_60 | NAYY 4x150 SE | 53 | 54 | 0.022584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_4163-10_0_4_line_61 | NAYY 4x150 SE | 55 | 56 | 0.0058651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_4163-10_0_4_line_62 | NAYY 4x150 SE | 56 | 57 | 0.061917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_4163-10_0_4_line_63 | NAYY 4x150 SE | 57 | 71 | 0.020163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_4163-10_0_4_line_64 | NAYY 4x150 SE | 58 | 59 | 0.020494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_4163-10_0_4_line_65 | NAYY 4x150 SE | 59 | 60 | 0.0025264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_4163-10_0_4_line_66 | NAYY 4x150 SE | 60 | 61 | 0.0086947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_4163-10_0_4_line_67 | NAYY 4x150 SE | 61 | 65 | 0.0080645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_4163-10_0_4_line_68 | NAYY 4x150 SE | 62 | 63 | 0.016607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_4163-10_0_4_line_69 | NAYY 4x150 SE | 63 | 64 | 0.010916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_4163-10_0_4_line_70 | NAYY 4x150 SE | 65 | 71 | 0.04647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_4163-10_0_4_line_71 | NAYY 4x150 SE | 66 | 67 | 0.022131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_4163-10_0_4_line_72 | NAYY 4x150 SE | 67 | 72 | 0.0029057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_4163-10_0_4_line_73 | NAYY 4x150 SE | 68 | 69 | 0.026981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4163-10_0_4_trafo_29 | 0.25 MVA 20/0.4 kV | 75 | 42 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2644954.1776 | 1262245.1531 | 2644956.8537 | 1262244.4096
1 | 2644674.2871 | 1262312.6733 | 2644954.1776 | 1262245.1531
2 | 2644956.8537 | 1262244.4096 | 2644959.192 | 1262243.76 | 2644967.4333 | 1262241.0678
3 | 2644674.2871 | 1262312.6733 | 2644672.3225 | 1262302.0852 | 2644665.8128 | 1262285.2242 | 2644662.2928 | 1262278.8744
4 | 2644676.7407 | 1262339.523 | 2644676.4113 | 1262331.2702 | 2644675.4987 | 1262321.4341 | 2644675.0806 | 1262316.95 | 2644674.2871 | 1262312.6733
5 | 2644968.9903 | 1262240.5592 | 2644967.4333 | 1262241.0678
6 | 2644644.5494 | 1262252.7773 | 2644657.8527 | 1262270.865 | 2644662.2928 | 1262278.8744
7 | 2644676.7407 | 1262339.523 | 2644670.7407 | 1262339.9669 | 2644667.2399 | 1262345.3373
8 | 2644992.0998 | 1262236.7161 | 2644977.6198 | 1262237.7401 | 2644968.9903 | 1262240.5592
9 | 2644541.5988 | 1262370.5405 | 2644542.5647 | 1262368.8995
10 | 2644552.637 | 1262351.7867 | 2644542.5647 | 1262368.8995
11 | 2644562.0466 | 1262335.8 | 2644552.637 | 1262351.7867
12 | 2644562.0466 | 1262335.8 | 2644564.0402 | 1262332.4129 | 2644569.8653 | 1262321.1821 | 2644570.5428 | 1262319.126
13 | 2644570.5428 | 1262319.126 | 2644570.892 | 1262318.0663
14 | 2644571.5617 | 1262316.034 | 2644570.892 | 1262318.0663
15 | 2644608.2512 | 1262369.0211 | 2644603.5357 | 1262376.9655
16 | 2644597.4399 | 1262387.2006 | 2644603.2211 | 1262377.4955 | 2644603.5357 | 1262376.9655
17 | 2644608.2512 | 1262369.0211 | 2644612.717 | 1262361.4973
18 | 2644623.0951 | 1262343.4815 | 2644621.8546 | 1262346.1026 | 2644612.717 | 1262361.4973
19 | 2644625.9657 | 1262337.4163 | 2644623.0951 | 1262343.4815
20 | 2644625.9657 | 1262337.4163 | 2644628.2191 | 1262324.3128 | 2644628.3136 | 1262323.1513
21 | 2644625.9657 | 1262337.4163 | 2644648.0268 | 1262349.7582
22 | 2644473.4786 | 1262213.2518 | 2644475.7971 | 1262193.9479
23 | 2644478.9526 | 1262171.6255 | 2644477.2885 | 1262181.5311 | 2644475.7971 | 1262193.9479
24 | 2644472.7625 | 1262219.2143 | 2644473.4786 | 1262213.2518
25 | 2644478.9526 | 1262171.6255 | 2644487.2495 | 1262180.0709
26 | 2644478.9526 | 1262171.6255 | 2644470.2043 | 1262165.8334 | 2644454.1222 | 1262157.4845
27 | 2644469.8422 | 1262240.569 | 2644471.7673 | 1262227.5 | 2644472.7625 | 1262219.2143
28 | 2644487.2495 | 1262180.0709 | 2644493.6439 | 1262186.5798 | 2644505.8063 | 1262195.1885 | 2644506.5673 | 1262195.6484
29 | 2644405.9464 | 1262147.1156 | 2644426.3927 | 1262148.1586 | 2644440.1771 | 1262151.4867 | 2644454.1222 | 1262157.4845
30 | 2644454.1222 | 1262157.4845 | 2644460.8389 | 1262141.1757
31 | 2644469.8422 | 1262240.569 | 2644468.0812 | 1262252.5246
32 | 2644520.1664 | 1262202.9188 | 2644514.5434 | 1262200.469 | 2644506.5673 | 1262195.6484
33 | 2644405.9464 | 1262147.1156 | 2644408.1775 | 1262136.9362 | 2644408.7269 | 1262130.2032
34 | 2644471.9732 | 1262114.1408 | 2644460.8389 | 1262141.1757
35 | 2644468.0812 | 1262252.5246 | 2644467.7237 | 1262254.9511
36 | 2644520.1664 | 1262202.9188 | 2644527.1644 | 1262205.9676
37 | 2644409.2385 | 1262103.3724 | 2644409.4709 | 1262108.1477 | 2644409.5631 | 1262119.9568 | 2644408.7269 | 1262130.2032
38 | 2644472.4012 | 1262113.1014 | 2644471.9732 | 1262114.1408
39 | 2644578.2109 | 1262215.4254 | 2644583.0478 | 1262206.3887 | 2644585.2658 | 1262201.3558
40 | 2644601.2893 | 1262184.077 | 2644590.452 | 1262189.5881 | 2644585.2658 | 1262201.3558
41 | 2644578.2109 | 1262215.4254 | 2644570.8451 | 1262215.8775
42 | 2644601.2893 | 1262184.077 | 2644601.9585 | 1262189.2524 | 2644606.3653 | 1262199.2927 | 2644609.2108 | 1262203.8066
43 | 2644601.2893 | 1262184.077 | 2644600.7767 | 1262180.1259 | 2644601.9572 | 1262170.5767
44 | 2644541.7862 | 1262212.3379 | 2644553.0682 | 1262216.8038 | 2644560.785 | 1262216.495 | 2644570.8451 | 1262215.8775
45 | 2644627.9477 | 1262230.2048 | 2644613.2814 | 1262210.2637 | 2644609.2108 | 1262203.8066
46 | 2644601.9572 | 1262170.5767 | 2644602.301 | 1262167.7953 | 2644606.8669 | 1262156.744 | 2644613.9816 | 1262145.6583
47 | 2644541.7862 | 1262212.3379 | 2644527.1644 | 1262205.9676
48 | 2644541.7862 | 1262212.3379 | 2644531.0023 | 1262245.6677
49 | 2644541.7862 | 1262212.3379 | 2644555.3579 | 1262172.4793
50 | 2644593.4478 | 1262251.8994 | 2644588.5117 | 1262266.2359
51 | 2644593.4478 | 1262251.8994 | 2644601.887 | 1262254.6872 | 2644611.4194 | 1262266.8448
52 | 2644584.9216 | 1262276.6629 | 2644588.5117 | 1262266.2359
53 | 2644611.4194 | 1262266.8448 | 2644617.2957 | 1262274.3394 | 2644624.3636 | 1262289.1366 | 2644628.0498 | 1262299.8164 | 2644628.1884 | 1262301.2951
54 | 2644644.5494 | 1262252.7773 | 2644627.9477 | 1262230.2048
55 | 2644531.0023 | 1262245.6677 | 2644528.1268 | 1262254.5552
56 | 2644555.3579 | 1262172.4793 | 2644558.1035 | 1262164.4156 | 2644564.3795 | 1262149.02
57 | 2644579.1379 | 1262293.4613 | 2644584.9216 | 1262276.6629
58 | 2644628.3136 | 1262323.1513 | 2644629.2072 | 1262312.1672 | 2644628.1884 | 1262301.2951
59 | 2644579.1379 | 1262293.4613 | 2644578.7387 | 1262294.6209
60 | 2644571.5617 | 1262316.034 | 2644575.9176 | 1262302.8146 | 2644578.7387 | 1262294.6209
61 | 2644466.869 | 1262260.7535 | 2644467.7237 | 1262254.9511
62 | 2644466.869 | 1262260.7535 | 2644422.8106 | 1262304.2569
63 | 2644422.8106 | 1262304.2569 | 2644426.3597 | 1262324.1055
64 | 2644492.9763 | 1262328.6943 | 2644485.2983 | 1262334.6111 | 2644476.3271 | 1262340.625
65 | 2644474.2286 | 1262342.0318 | 2644476.3271 | 1262340.625
66 | 2644474.2286 | 1262342.0318 | 2644469.519 | 1262345.1889 | 2644467.5442 | 1262347.4801
67 | 2644462.2793 | 1262353.5889 | 2644467.5442 | 1262347.4801
68 | 2644524.7664 | 1262264.941 | 2644519.6542 | 1262280.7414
69 | 2644524.7664 | 1262264.941 | 2644528.1268 | 1262254.5552
70 | 2644462.2793 | 1262353.5889 | 2644426.3597 | 1262324.1055
71 | 2644564.3795 | 1262149.02 | 2644572.7338 | 1262128.5261
72 | 2644573.8307 | 1262125.8354 | 2644572.7338 | 1262128.5261
73 | 2644667.2399 | 1262345.3373 | 2644659.994 | 1262356.4531 | 2644648.0268 | 1262349.7582

## bus_geodata
| x | y | coords
0 | 2644954.1776 | 1262245.1531
1 | 2644956.8537 | 1262244.4096
2 | 2644674.2871 | 1262312.6733
3 | 2644967.4333 | 1262241.0678
4 | 2644662.2928 | 1262278.8744
5 | 2644676.7407 | 1262339.523
6 | 2644968.9903 | 1262240.5592
7 | 2644992.0998 | 1262236.7161
8 | 2644541.5988 | 1262370.5405
9 | 2644542.5647 | 1262368.8995
10 | 2644552.637 | 1262351.7867
11 | 2644562.0466 | 1262335.8
12 | 2644570.5428 | 1262319.126
13 | 2644570.892 | 1262318.0663
14 | 2644603.5357 | 1262376.9655
15 | 2644608.2512 | 1262369.0211
16 | 2644597.4399 | 1262387.2006
17 | 2644612.717 | 1262361.4973
18 | 2644623.0951 | 1262343.4815
19 | 2644625.9657 | 1262337.4163
20 | 2644475.7971 | 1262193.9479
21 | 2644473.4786 | 1262213.2518
22 | 2644478.9526 | 1262171.6255
23 | 2644472.7625 | 1262219.2143
24 | 2644487.2495 | 1262180.0709
25 | 2644454.1222 | 1262157.4845
26 | 2644469.8422 | 1262240.569
27 | 2644506.5673 | 1262195.6484
28 | 2644405.9464 | 1262147.1156
29 | 2644460.8389 | 1262141.1757
30 | 2644468.0812 | 1262252.5246
31 | 2644520.1664 | 1262202.9188
32 | 2644408.7269 | 1262130.2032
33 | 2644471.9732 | 1262114.1408
34 | 2644585.2658 | 1262201.3558
35 | 2644578.2109 | 1262215.4254
36 | 2644601.2893 | 1262184.077
37 | 2644570.8451 | 1262215.8775
38 | 2644609.2108 | 1262203.8066
39 | 2644601.9572 | 1262170.5767
40 | 2644541.7862 | 1262212.3379
41 | 2644593.4478 | 1262251.8994
42 | 2644588.5117 | 1262266.2359
43 | 2644611.4194 | 1262266.8448
44 | 2644627.9477 | 1262230.2048
45 | 2644613.9816 | 1262145.6583
46 | 2644527.1644 | 1262205.9676
47 | 2644531.0023 | 1262245.6677
48 | 2644555.3579 | 1262172.4793
49 | 2644584.9216 | 1262276.6629
50 | 2644628.1884 | 1262301.2951
51 | 2644644.5494 | 1262252.7773
52 | 2644579.1379 | 1262293.4613
53 | 2644578.7387 | 1262294.6209
54 | 2644571.5617 | 1262316.034
55 | 2644467.7237 | 1262254.9511
56 | 2644466.869 | 1262260.7535
57 | 2644422.8106 | 1262304.2569
58 | 2644492.9763 | 1262328.6943
59 | 2644476.3271 | 1262340.625
60 | 2644474.2286 | 1262342.0318
61 | 2644467.5443 | 1262347.4801
62 | 2644519.6542 | 1262280.7414
63 | 2644524.7664 | 1262264.941
64 | 2644528.1268 | 1262254.5552
65 | 2644462.2793 | 1262353.5889
66 | 2644564.3795 | 1262149.02
67 | 2644572.7338 | 1262128.5261
68 | 2644667.2399 | 1262345.3373
69 | 2644648.0268 | 1262349.7582
70 | 2644628.3136 | 1262323.1513
71 | 2644426.3597 | 1262324.1055
72 | 2644573.8307 | 1262125.8354
73 | 2644409.2385 | 1262103.3724
74 | 2644472.4012 | 1262113.1014
75 | 2644593.4478 | 1262251.8994

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1