## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4181-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4181-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4181-5_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4181-5_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4181-5_0_4_node_82 | 0.4 | n |  | TRUE
5 | bus_LV_4181-5_0_4_node_95 | 0.4 | n |  | TRUE
6 | bus_LV_4181-5_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_4181-5_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_4181-5_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_4181-5_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_4181-5_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_4181-5_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_4181-5_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_4181-5_0_4_node_19 | 0.4 | n |  | TRUE
14 | bus_LV_4181-5_0_4_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_4181-5_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_4181-5_0_4_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_4181-5_0_4_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_4181-5_0_4_node_81 | 0.4 | n |  | TRUE
19 | bus_LV_4181-5_0_4_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_4181-5_0_4_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_4181-5_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_4181-5_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_4181-5_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_4181-5_0_4_node_28 | 0.4 | n |  | TRUE
25 | bus_LV_4181-5_0_4_node_49 | 0.4 | n |  | TRUE
26 | bus_LV_4181-5_0_4_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_4181-5_0_4_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_4181-5_0_4_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_4181-5_0_4_node_38 | 0.4 | n |  | TRUE
30 | bus_LV_4181-5_0_4_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_4181-5_0_4_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_4181-5_0_4_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_4181-5_0_4_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_4181-5_0_4_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_4181-5_0_4_node_50 | 0.4 | n |  | TRUE
36 | bus_LV_4181-5_0_4_node_52 | 0.4 | n |  | TRUE
37 | bus_LV_4181-5_0_4_node_48 | 0.4 | n |  | TRUE
38 | bus_LV_4181-5_0_4_node_79 | 0.4 | n |  | TRUE
39 | bus_LV_4181-5_0_4_node_39 | 0.4 | n |  | TRUE
40 | bus_LV_4181-5_0_4_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_4181-5_0_4_node_40 | 0.4 | n |  | TRUE
42 | bus_LV_4181-5_0_4_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_4181-5_0_4_node_32 | 0.4 | n |  | TRUE
44 | bus_LV_4181-5_0_4_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_4181-5_0_4_node_34 | 0.4 | n |  | TRUE
46 | bus_LV_4181-5_0_4_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_4181-5_0_4_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_4181-5_0_4_node_53 | 0.4 | n |  | TRUE
49 | bus_LV_4181-5_0_4_node_47 | 0.4 | n |  | TRUE
50 | bus_LV_4181-5_0_4_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_4181-5_0_4_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_4181-5_0_4_node_44 | 0.4 | n |  | TRUE
53 | bus_LV_4181-5_0_4_node_45 | 0.4 | n |  | TRUE
54 | bus_LV_4181-5_0_4_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_4181-5_0_4_node_51 | 0.4 | n |  | TRUE
56 | bus_LV_4181-5_0_4_node_54 | 0.4 | n |  | TRUE
57 | bus_LV_4181-5_0_4_node_62 | 0.4 | n |  | TRUE
58 | bus_LV_4181-5_0_4_node_55 | 0.4 | n |  | TRUE
59 | bus_LV_4181-5_0_4_node_63 | 0.4 | n |  | TRUE
60 | bus_LV_4181-5_0_4_node_64 | 0.4 | n |  | TRUE
61 | bus_LV_4181-5_0_4_node_60 | 0.4 | n |  | TRUE
62 | bus_LV_4181-5_0_4_node_78 | 0.4 | n |  | TRUE
63 | bus_LV_4181-5_0_4_node_58 | 0.4 | n |  | TRUE
64 | bus_LV_4181-5_0_4_node_56 | 0.4 | n |  | TRUE
65 | bus_LV_4181-5_0_4_node_57 | 0.4 | n |  | TRUE
66 | bus_LV_4181-5_0_4_node_59 | 0.4 | n |  | TRUE
67 | bus_LV_4181-5_0_4_node_61 | 0.4 | n |  | TRUE
68 | bus_LV_4181-5_0_4_node_65 | 0.4 | n |  | TRUE
69 | bus_LV_4181-5_0_4_node_66 | 0.4 | n |  | TRUE
70 | bus_LV_4181-5_0_4_node_80 | 0.4 | n |  | TRUE
71 | bus_LV_4181-5_0_4_node_67 | 0.4 | n |  | TRUE
72 | bus_LV_4181-5_0_4_node_68 | 0.4 | n |  | TRUE
73 | bus_LV_4181-5_0_4_node_69 | 0.4 | n |  | TRUE
74 | bus_LV_4181-5_0_4_node_70 | 0.4 | n |  | TRUE
75 | bus_LV_4181-5_0_4_node_72 | 0.4 | n |  | TRUE
76 | bus_LV_4181-5_0_4_node_73 | 0.4 | n |  | TRUE
77 | bus_LV_4181-5_0_4_node_71 | 0.4 | n |  | TRUE
78 | bus_LV_4181-5_0_4_node_75 | 0.4 | n |  | TRUE
79 | bus_LV_4181-5_0_4_node_74 | 0.4 | n |  | TRUE
80 | bus_LV_4181-5_0_4_node_101 | 0.4 | n |  | TRUE
81 | bus_LV_4181-5_0_4_node_98 | 0.4 | n |  | TRUE
82 | bus_LV_4181-5_0_4_node_102 | 0.4 | n |  | TRUE
83 | bus_LV_4181-5_0_4_node_99 | 0.4 | n |  | TRUE
84 | bus_LV_4181-5_0_4_node_76 | 0.4 | n |  | TRUE
85 | bus_LV_4181-5_0_4_node_77 | 0.4 | n |  | TRUE
86 | bus_LV_4181-5_0_4_node_83 | 0.4 | n |  | TRUE
87 | bus_LV_4181-5_0_4_node_89 | 0.4 | n |  | TRUE
88 | bus_LV_4181-5_0_4_node_88 | 0.4 | n |  | TRUE
89 | bus_LV_4181-5_0_4_node_86 | 0.4 | n |  | TRUE
90 | bus_LV_4181-5_0_4_node_105 | 0.4 | n |  | TRUE
91 | bus_LV_4181-5_0_4_node_84 | 0.4 | n |  | TRUE
92 | bus_LV_4181-5_0_4_node_85 | 0.4 | n |  | TRUE
93 | bus_LV_4181-5_0_4_node_87 | 0.4 | n |  | TRUE
94 | bus_LV_4181-5_0_4_node_94 | 0.4 | n |  | TRUE
95 | bus_LV_4181-5_0_4_node_92 | 0.4 | n |  | TRUE
96 | bus_LV_4181-5_0_4_node_106 | 0.4 | n |  | TRUE
97 | bus_LV_4181-5_0_4_node_90 | 0.4 | n |  | TRUE
98 | bus_LV_4181-5_0_4_node_91 | 0.4 | n |  | TRUE
99 | bus_LV_4181-5_0_4_node_93 | 0.4 | n |  | TRUE
100 | bus_LV_4181-5_0_4_node_96 | 0.4 | n |  | TRUE
101 | bus_LV_4181-5_0_4_node_97 | 0.4 | n |  | TRUE
102 | bus_LV_4181-5_0_4_node_111 | 0.4 | n |  | TRUE
103 | bus_LV_4181-5_0_4_node_120 | 0.4 | n |  | TRUE
104 | bus_LV_4181-5_0_4_node_121 | 0.4 | n |  | TRUE
105 | bus_LV_4181-5_0_4_node_100 | 0.4 | n |  | TRUE
106 | bus_LV_4181-5_0_4_node_118 | 0.4 | n |  | TRUE
107 | bus_LV_4181-5_0_4_node_119 | 0.4 | n |  | TRUE
108 | bus_LV_4181-5_0_4_node_103 | 0.4 | n |  | TRUE
109 | bus_LV_4181-5_0_4_node_104 | 0.4 | n |  | TRUE
110 | bus_LV_4181-5_0_4_node_134 | 0.4 | n |  | TRUE
111 | bus_LV_4181-5_0_4_node_133 | 0.4 | n |  | TRUE
112 | bus_LV_4181-5_0_4_node_146 | 0.4 | n |  | TRUE
113 | bus_LV_4181-5_0_4_node_145 | 0.4 | n |  | TRUE
114 | bus_LV_4181-5_0_4_node_107 | 0.4 | n |  | TRUE
115 | bus_LV_4181-5_0_4_node_108 | 0.4 | n |  | TRUE
116 | bus_LV_4181-5_0_4_node_109 | 0.4 | n |  | TRUE
117 | bus_LV_4181-5_0_4_node_110 | 0.4 | n |  | TRUE
118 | bus_LV_4181-5_0_4_node_131 | 0.4 | n |  | TRUE
119 | bus_LV_4181-5_0_4_node_122 | 0.4 | n |  | TRUE
120 | bus_LV_4181-5_0_4_node_135 | 0.4 | n |  | TRUE
121 | bus_LV_4181-5_0_4_node_112 | 0.4 | n |  | TRUE
122 | bus_LV_4181-5_0_4_node_113 | 0.4 | n |  | TRUE
123 | bus_LV_4181-5_0_4_node_114 | 0.4 | n |  | TRUE
124 | bus_LV_4181-5_0_4_node_115 | 0.4 | n |  | TRUE
125 | bus_LV_4181-5_0_4_node_117 | 0.4 | n |  | TRUE
126 | bus_LV_4181-5_0_4_node_136 | 0.4 | n |  | TRUE
127 | bus_LV_4181-5_0_4_node_116 | 0.4 | n |  | TRUE
128 | bus_LV_4181-5_0_4_node_142 | 0.4 | n |  | TRUE
129 | bus_LV_4181-5_0_4_node_127 | 0.4 | n |  | TRUE
130 | bus_LV_4181-5_0_4_node_132 | 0.4 | n |  | TRUE
131 | bus_LV_4181-5_0_4_node_137 | 0.4 | n |  | TRUE
132 | bus_LV_4181-5_0_4_node_130 | 0.4 | n |  | TRUE
133 | bus_LV_4181-5_0_4_node_141 | 0.4 | n |  | TRUE
134 | bus_LV_4181-5_0_4_node_125 | 0.4 | n |  | TRUE
135 | bus_LV_4181-5_0_4_node_126 | 0.4 | n |  | TRUE
136 | bus_LV_4181-5_0_4_node_123 | 0.4 | n |  | TRUE
137 | bus_LV_4181-5_0_4_node_124 | 0.4 | n |  | TRUE
138 | bus_LV_4181-5_0_4_node_128 | 0.4 | n |  | TRUE
139 | bus_LV_4181-5_0_4_node_129 | 0.4 | n |  | TRUE
140 | bus_LV_4181-5_0_4_node_140 | 0.4 | n |  | TRUE
141 | bus_LV_4181-5_0_4_node_139 | 0.4 | n |  | TRUE
142 | bus_LV_4181-5_0_4_node_138 | 0.4 | n |  | TRUE
143 | bus_LV_4181-5_0_4_node_143 | 0.4 | n |  | TRUE
144 | bus_LV_4181-5_0_4_node_147 | 0.4 | n |  | TRUE
145 | bus_MV_304_0_node_222 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4181-5_0_4_load_0 | 0 | 0.0059426 | 0.0014893 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4181-5_0_4_load_1 | 1 | 0.0043393 | 0.0010875 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4181-5_0_4_load_2 | 2 | 0.0098061 | 0.0024576 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4181-5_0_4_load_3 | 3 | 0.00099235 | 0.00024871 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4181-5_0_4_load_95 | 5 | 0.00070157 | 0.00017583 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4181-5_0_4_load_4 | 6 | 0.0030177 | 0.0007563 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4181-5_0_4_load_7 | 9 | 0.00054784 | 0.0001373 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4181-5_0_4_load_8 | 10 | 0.0045309 | 0.0011356 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4181-5_0_4_load_10 | 12 | 0.0014902 | 0.00037347 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4181-5_0_4_load_19 | 13 | 0.00050483 | 0.00012652 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4181-5_0_4_load_26 | 14 | 0.0021232 | 0.00053213 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4181-5_0_4_load_11 | 15 | 0.0010706 | 0.00026831 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4181-5_0_4_load_15 | 16 | 0.0090265 | 0.0022623 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4181-5_0_4_load_29 | 17 | 0.0011436 | 0.00028661 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4181-5_0_4_load_24 | 19 | 0.0038272 | 0.00095919 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4181-5_0_4_load_17 | 20 | 0.0008787 | 0.00022022 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4181-5_0_4_load_12 | 21 | 0.0022982 | 0.00057598 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4181-5_0_4_load_16 | 23 | 0.0020836 | 0.00052221 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4181-5_0_4_load_49 | 25 | 0.0020754 | 0.00052014 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4181-5_0_4_load_20 | 27 | 0.0018106 | 0.00045377 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4181-5_0_4_load_21 | 28 | 0.0022854 | 0.00057277 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4181-5_0_4_load_38 | 29 | 0.0026479 | 0.00066362 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4181-5_0_4_load_22 | 30 | 0.0023345 | 0.00058507 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4181-5_0_4_load_30 | 31 | 0.00057149 | 0.00014323 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4181-5_0_4_load_31 | 32 | 0.0014756 | 0.00036981 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4181-5_0_4_load_23 | 33 | 0.00084476 | 0.00021172 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4181-5_0_4_load_27 | 34 | 0.0015474 | 0.00038781 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4181-5_0_4_load_52 | 36 | 0.00073561 | 0.00018436 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4181-5_0_4_load_48 | 37 | 0.0032239 | 0.00080798 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4181-5_0_4_load_41 | 40 | 0.00071868 | 0.00018012 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4181-5_0_4_load_40 | 41 | 0.0013235 | 0.0003317 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4181-5_0_4_load_35 | 42 | 0.0011565 | 0.00028985 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4181-5_0_4_load_32 | 43 | 0.0011146 | 0.00027935 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4181-5_0_4_load_33 | 44 | 0.0013252 | 0.00033213 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4181-5_0_4_load_36 | 46 | 0.001494 | 0.00037443 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4181-5_0_4_load_37 | 47 | 0.0010346 | 0.00025929 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4181-5_0_4_load_53 | 48 | 0.0005746 | 0.00014401 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4181-5_0_4_load_47 | 49 | 0.0014151 | 0.00035465 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4181-5_0_4_load_42 | 50 | 0.0010236 | 0.00025653 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4181-5_0_4_load_44 | 52 | 0.0013348 | 0.00033454 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4181-5_0_4_load_46 | 54 | 0.00059817 | 0.00014992 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4181-5_0_4_load_51 | 55 | 0.0031442 | 0.000788 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4181-5_0_4_load_54 | 56 | 0.005295 | 0.0013271 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4181-5_0_4_load_62 | 57 | 0.0015065 | 0.00037756 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4181-5_0_4_load_63 | 59 | 0.0064254 | 0.0016104 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4181-5_0_4_load_64 | 60 | 0.00084556 | 0.00021192 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4181-5_0_4_load_60 | 61 | 0.0014335 | 0.00035927 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4181-5_0_4_load_58 | 63 | 0.0016887 | 0.00042322 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4181-5_0_4_load_56 | 64 | 0.0017644 | 0.00044221 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4181-5_0_4_load_57 | 65 | 0.0024171 | 0.00060579 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4181-5_0_4_load_59 | 66 | 0.0018404 | 0.00046124 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4181-5_0_4_load_61 | 67 | 0.0016301 | 0.00040855 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4181-5_0_4_load_65 | 68 | 0.0012484 | 0.00031288 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4181-5_0_4_load_67 | 71 | 0.0024091 | 0.00060377 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4181-5_0_4_load_68 | 72 | 0.0021984 | 0.00055097 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4181-5_0_4_load_69 | 73 | 0.0010885 | 0.0002728 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4181-5_0_4_load_70 | 74 | 0.0015032 | 0.00037673 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4181-5_0_4_load_72 | 75 | 0.0022524 | 0.00056451 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4181-5_0_4_load_75 | 78 | 0.001328 | 0.00033283 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4181-5_0_4_load_74 | 79 | 0.00091469 | 0.00022924 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4181-5_0_4_load_101 | 80 | 0.0017232 | 0.00043188 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4181-5_0_4_load_98 | 81 | 0.00077032 | 0.00019306 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4181-5_0_4_load_102 | 82 | 0.0015311 | 0.00038373 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4181-5_0_4_load_99 | 83 | 0.00056809 | 0.00014238 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4181-5_0_4_load_76 | 84 | 0.0024341 | 0.00061004 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4181-5_0_4_load_77 | 85 | 0.00092438 | 0.00023167 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4181-5_0_4_load_83 | 86 | 0.0015059 | 0.0003774 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4181-5_0_4_load_89 | 87 | 0.0018602 | 0.00046621 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4181-5_0_4_load_88 | 88 | 0.0038258 | 0.00095883 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4181-5_0_4_load_86 | 89 | 0.0012513 | 0.00031361 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4181-5_0_4_load_105 | 90 | 0.0017832 | 0.00044691 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4181-5_0_4_load_84 | 91 | 0.0032364 | 0.00081112 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4181-5_0_4_load_85 | 92 | 0.0033475 | 0.00083896 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4181-5_0_4_load_87 | 93 | 0.0033483 | 0.00083915 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4181-5_0_4_load_94 | 94 | 0.0030368 | 0.00076108 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4181-5_0_4_load_92 | 95 | 0.0017925 | 0.00044924 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4181-5_0_4_load_106 | 96 | 0.00093158 | 0.00023348 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4181-5_0_4_load_90 | 97 | 0.0016492 | 0.00041332 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4181-5_0_4_load_91 | 98 | 0.0016928 | 0.00042426 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4181-5_0_4_load_93 | 99 | 0.0020471 | 0.00051306 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4181-5_0_4_load_96 | 100 | 0.0018913 | 0.00047401 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4181-5_0_4_load_97 | 101 | 0.0017295 | 0.00043346 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4181-5_0_4_load_121 | 104 | 0.00079713 | 0.00019978 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4181-5_0_4_load_100 | 105 | 0.00093716 | 0.00023488 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4181-5_0_4_load_118 | 106 | 0.0010258 | 0.00025708 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4181-5_0_4_load_119 | 107 | 0.0012509 | 0.0003135 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4181-5_0_4_load_103 | 108 | 0.00095884 | 0.00024031 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4181-5_0_4_load_104 | 109 | 0.0014572 | 0.00036521 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4181-5_0_4_load_134 | 110 | 0.00093201 | 0.00023358 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4181-5_0_4_load_146 | 112 | 0.00093143 | 0.00023344 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4181-5_0_4_load_107 | 114 | 0.0018699 | 0.00046864 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4181-5_0_4_load_109 | 116 | 0.0016323 | 0.00040909 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4181-5_0_4_load_110 | 117 | 0.0014084 | 0.00035298 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4181-5_0_4_load_131 | 118 | 0.00034739 | 8.7063e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4181-5_0_4_load_122 | 119 | 0.0013643 | 0.00034192 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4181-5_0_4_load_135 | 120 | 0.0013353 | 0.00033467 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4181-5_0_4_load_112 | 121 | 0.00059108 | 0.00014814 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4181-5_0_4_load_113 | 122 | 0.0002775 | 6.9549e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4181-5_0_4_load_115 | 124 | 0.00051066 | 0.00012798 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4181-5_0_4_load_142 | 128 | 0.00093207 | 0.0002336 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4181-5_0_4_load_132 | 130 | 0.00060311 | 0.00015115 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4181-5_0_4_load_137 | 131 | 0.001564 | 0.00039198 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4181-5_0_4_load_130 | 132 | 0.00070485 | 0.00017665 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4181-5_0_4_load_141 | 133 | 0.00093166 | 0.0002335 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4181-5_0_4_load_126 | 135 | 0.0023789 | 0.0005962 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4181-5_0_4_load_123 | 136 | 0.00048265 | 0.00012096 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4181-5_0_4_load_124 | 137 | 0.0014961 | 0.00037495 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4181-5_0_4_load_128 | 138 | 0.00090758 | 0.00022746 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4181-5_0_4_load_129 | 139 | 0.0011633 | 0.00029156 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4181-5_0_4_load_140 | 140 | 0.0014196 | 0.00035578 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4181-5_0_4_load_139 | 141 | 0.0015081 | 0.00037796 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4181-5_0_4_load_138 | 142 | 0.0010978 | 0.00027514 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4181-5_0_4_load_147 | 144 | 0.0016445 | 0.00041216 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 58 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4181-5_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0091822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_4181-5_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.0090777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_4181-5_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.00027718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_4181-5_0_4_line_3 | NAYY 4x150 SE | 3 | 4 | 0.011203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_4181-5_0_4_line_4 | NAYY 4x150 SE | 4 | 5 | 0.0095913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_4181-5_0_4_line_5 | NAYY 4x150 SE | 5 | 70 | 0.015418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_4181-5_0_4_line_6 | NAYY 4x150 SE | 6 | 7 | 0.021715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_4181-5_0_4_line_7 | NAYY 4x150 SE | 6 | 8 | 0.01865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_4181-5_0_4_line_8 | NAYY 4x150 SE | 7 | 9 | 0.020569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_4181-5_0_4_line_9 | NAYY 4x150 SE | 7 | 10 | 0.012358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_4181-5_0_4_line_10 | NAYY 4x150 SE | 8 | 11 | 0.006922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_4181-5_0_4_line_11 | NAYY 4x150 SE | 9 | 12 | 0.010809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_4181-5_0_4_line_12 | NAYY 4x150 SE | 10 | 13 | 0.0020555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_4181-5_0_4_line_13 | NAYY 4x150 SE | 11 | 14 | 0.018398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_4181-5_0_4_line_14 | NAYY 4x150 SE | 12 | 15 | 0.0016494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_4181-5_0_4_line_15 | NAYY 4x150 SE | 13 | 16 | 0.016895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_4181-5_0_4_line_16 | NAYY 4x150 SE | 14 | 19 | 0.009142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_4181-5_0_4_line_17 | NAYY 4x150 SE | 15 | 20 | 0.0017355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_4181-5_0_4_line_18 | NAYY 4x150 SE | 17 | 18 | 0.013496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_4181-5_0_4_line_19 | NAYY 4x150 SE | 18 | 38 | 0.0046 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_4181-5_0_4_line_20 | NAYY 4x150 SE | 19 | 33 | 0.0026733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_4181-5_0_4_line_21 | NAYY 4x150 SE | 21 | 22 | 0.050211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_4181-5_0_4_line_22 | NAYY 4x150 SE | 22 | 23 | 0.0079115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_4181-5_0_4_line_23 | NAYY 4x150 SE | 23 | 24 | 0.021002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_4181-5_0_4_line_24 | NAYY 4x150 SE | 24 | 25 | 0.013907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_4181-5_0_4_line_25 | NAYY 4x150 SE | 24 | 26 | 0.008511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_4181-5_0_4_line_26 | NAYY 4x150 SE | 25 | 37 | 0.015322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_4181-5_0_4_line_27 | NAYY 4x150 SE | 26 | 34 | 0.0060934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_4181-5_0_4_line_28 | NAYY 4x150 SE | 26 | 33 | 0.015923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_4181-5_0_4_line_29 | NAYY 4x150 SE | 27 | 28 | 0.011293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_4181-5_0_4_line_30 | NAYY 4x150 SE | 27 | 29 | 0.056727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_4181-5_0_4_line_31 | NAYY 4x150 SE | 28 | 30 | 0.029063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_4181-5_0_4_line_32 | NAYY 4x150 SE | 30 | 31 | 0.016991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_4181-5_0_4_line_33 | NAYY 4x150 SE | 31 | 32 | 0.010425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_4181-5_0_4_line_34 | NAYY 4x150 SE | 32 | 39 | 0.014146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_4181-5_0_4_line_35 | NAYY 4x150 SE | 34 | 35 | 0.015272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_4181-5_0_4_line_36 | NAYY 4x150 SE | 35 | 36 | 0.012791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_4181-5_0_4_line_37 | NAYY 4x150 SE | 36 | 57 | 0.016537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_4181-5_0_4_line_38 | NAYY 4x150 SE | 37 | 40 | 0.0090363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_4181-5_0_4_line_39 | NAYY 4x150 SE | 38 | 62 | 0.010147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_4181-5_0_4_line_40 | NAYY 4x150 SE | 38 | 59 | 0.016318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_4181-5_0_4_line_41 | NAYY 4x150 SE | 39 | 40 | 0.011091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_4181-5_0_4_line_42 | NAYY 4x150 SE | 39 | 41 | 0.037556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_4181-5_0_4_line_43 | NAYY 4x150 SE | 39 | 42 | 0.019961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_4181-5_0_4_line_44 | NAYY 4x150 SE | 42 | 44 | 0.029165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_4181-5_0_4_line_45 | NAYY 4x150 SE | 43 | 44 | 0.0048855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_4181-5_0_4_line_46 | NAYY 4x150 SE | 43 | 45 | 0.015505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_4181-5_0_4_line_47 | NAYY 4x150 SE | 45 | 46 | 0.02085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_4181-5_0_4_line_48 | NAYY 4x150 SE | 45 | 47 | 0.033014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_4181-5_0_4_line_49 | NAYY 4x150 SE | 47 | 48 | 0.021357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_4181-5_0_4_line_50 | NAYY 4x150 SE | 48 | 49 | 0.0057841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_4181-5_0_4_line_51 | NAYY 4x150 SE | 49 | 53 | 0.0026678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_4181-5_0_4_line_52 | NAYY 4x150 SE | 50 | 51 | 0.024992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_4181-5_0_4_line_53 | NAYY 4x150 SE | 51 | 52 | 0.013172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_4181-5_0_4_line_54 | NAYY 4x150 SE | 51 | 53 | 0.048829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_4181-5_0_4_line_55 | NAYY 4x150 SE | 53 | 54 | 0.026233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_4181-5_0_4_line_56 | NAYY 4x150 SE | 55 | 56 | 0.018329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_4181-5_0_4_line_57 | NAYY 4x150 SE | 56 | 58 | 0.015977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_4181-5_0_4_line_58 | NAYY 4x150 SE | 57 | 59 | 0.0070595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_4181-5_0_4_line_59 | NAYY 4x150 SE | 58 | 60 | 0.022009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
60 | LV_4181-5_0_4_line_60 | NAYY 4x150 SE | 58 | 61 | 0.010454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_4181-5_0_4_line_61 | NAYY 4x150 SE | 60 | 62 | 0.018694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
62 | LV_4181-5_0_4_line_62 | NAYY 4x150 SE | 61 | 63 | 0.0050253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_4181-5_0_4_line_63 | NAYY 4x150 SE | 62 | 70 | 0.026159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_4181-5_0_4_line_64 | NAYY 4x150 SE | 63 | 64 | 0.00082286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_4181-5_0_4_line_65 | NAYY 4x150 SE | 64 | 65 | 0.011646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_4181-5_0_4_line_66 | NAYY 4x150 SE | 65 | 66 | 0.0070333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_4181-5_0_4_line_67 | NAYY 4x150 SE | 66 | 67 | 0.0012184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_4181-5_0_4_line_68 | NAYY 4x150 SE | 67 | 68 | 0.021854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_4181-5_0_4_line_69 | NAYY 4x150 SE | 68 | 69 | 0.0020941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_4181-5_0_4_line_70 | NAYY 4x150 SE | 69 | 71 | 0.012017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_4181-5_0_4_line_71 | NAYY 4x150 SE | 69 | 72 | 0.02404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_4181-5_0_4_line_72 | NAYY 4x150 SE | 70 | 88 | 0.0077693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_4181-5_0_4_line_73 | NAYY 4x150 SE | 71 | 73 | 0.0055316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_4181-5_0_4_line_74 | NAYY 4x150 SE | 73 | 74 | 0.008291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_4181-5_0_4_line_75 | NAYY 4x150 SE | 74 | 77 | 0.020989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_4181-5_0_4_line_76 | NAYY 4x150 SE | 75 | 76 | 0.024387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_4181-5_0_4_line_77 | NAYY 4x150 SE | 76 | 80 | 0.0073262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_4181-5_0_4_line_78 | NAYY 4x150 SE | 76 | 81 | 0.02094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_4181-5_0_4_line_79 | NAYY 4x150 SE | 77 | 78 | 0.012611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_4181-5_0_4_line_80 | NAYY 4x150 SE | 78 | 79 | 0.00039737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_4181-5_0_4_line_81 | NAYY 4x150 SE | 79 | 84 | 0.01027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_4181-5_0_4_line_82 | NAYY 4x150 SE | 80 | 82 | 0.026355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_4181-5_0_4_line_83 | NAYY 4x150 SE | 81 | 83 | 0.014601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_4181-5_0_4_line_84 | NAYY 4x150 SE | 83 | 105 | 0.0056137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_4181-5_0_4_line_85 | NAYY 4x150 SE | 85 | 86 | 0.015379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_4181-5_0_4_line_86 | NAYY 4x150 SE | 86 | 87 | 0.023751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_4181-5_0_4_line_87 | NAYY 4x150 SE | 87 | 90 | 0.028182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_4181-5_0_4_line_88 | NAYY 4x150 SE | 88 | 89 | 0.0070442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_4181-5_0_4_line_89 | NAYY 4x150 SE | 89 | 91 | 0.011693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_4181-5_0_4_line_90 | NAYY 4x150 SE | 90 | 96 | 0.02291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_4181-5_0_4_line_91 | NAYY 4x150 SE | 91 | 92 | 0.00030472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_4181-5_0_4_line_92 | NAYY 4x150 SE | 92 | 93 | 0.011485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_4181-5_0_4_line_93 | NAYY 4x150 SE | 93 | 94 | 0.013014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_4181-5_0_4_line_94 | NAYY 4x150 SE | 94 | 95 | 0.00037133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_4181-5_0_4_line_95 | NAYY 4x150 SE | 95 | 97 | 0.0083629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_4181-5_0_4_line_96 | NAYY 4x150 SE | 96 | 112 | 0.0082451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_4181-5_0_4_line_97 | NAYY 4x150 SE | 97 | 98 | 0.0036623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_4181-5_0_4_line_98 | NAYY 4x150 SE | 98 | 99 | 0.010819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_4181-5_0_4_line_99 | NAYY 4x150 SE | 99 | 100 | 0.0031473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_4181-5_0_4_line_100 | NAYY 4x150 SE | 100 | 101 | 0.014826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_4181-5_0_4_line_101 | NAYY 4x150 SE | 101 | 102 | 0.012528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_4181-5_0_4_line_102 | NAYY 4x150 SE | 102 | 103 | 0.010124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_4181-5_0_4_line_103 | NAYY 4x150 SE | 102 | 104 | 0.021804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_4181-5_0_4_line_104 | NAYY 4x150 SE | 103 | 120 | 0.018447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_4181-5_0_4_line_105 | NAYY 4x150 SE | 103 | 107 | 0.014168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_4181-5_0_4_line_106 | NAYY 4x150 SE | 104 | 119 | 0.00051147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_4181-5_0_4_line_107 | NAYY 4x150 SE | 105 | 106 | 0.0031135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_4181-5_0_4_line_108 | NAYY 4x150 SE | 106 | 107 | 0.006459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_4181-5_0_4_line_109 | NAYY 4x150 SE | 108 | 109 | 0.0063258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_4181-5_0_4_line_110 | NAYY 4x150 SE | 109 | 110 | 0.015901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_4181-5_0_4_line_111 | NAYY 4x150 SE | 110 | 111 | 0.010659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_4181-5_0_4_line_112 | NAYY 4x150 SE | 111 | 132 | 0.021881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_4181-5_0_4_line_113 | NAYY 4x150 SE | 111 | 127 | 0.023278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_4181-5_0_4_line_114 | NAYY 4x150 SE | 112 | 113 | 0.007806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_4181-5_0_4_line_115 | NAYY 4x150 SE | 113 | 143 | 0.021437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_4181-5_0_4_line_116 | NAYY 4x150 SE | 114 | 115 | 0.046408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_4181-5_0_4_line_117 | NAYY 4x150 SE | 115 | 116 | 0.019175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_4181-5_0_4_line_118 | NAYY 4x150 SE | 115 | 117 | 0.035151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_4181-5_0_4_line_119 | NAYY 4x150 SE | 116 | 118 | 0.0032487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_4181-5_0_4_line_120 | NAYY 4x150 SE | 117 | 119 | 0.014386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_4181-5_0_4_line_121 | NAYY 4x150 SE | 120 | 135 | 0.0050561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_4181-5_0_4_line_122 | NAYY 4x150 SE | 121 | 122 | 0.0073173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_4181-5_0_4_line_123 | NAYY 4x150 SE | 121 | 123 | 0.029196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_4181-5_0_4_line_124 | NAYY 4x150 SE | 122 | 124 | 0.0091395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_4181-5_0_4_line_125 | NAYY 4x150 SE | 123 | 125 | 0.001838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_4181-5_0_4_line_126 | NAYY 4x150 SE | 124 | 126 | 0.0075206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_4181-5_0_4_line_127 | NAYY 4x150 SE | 125 | 129 | 0.010916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_4181-5_0_4_line_128 | NAYY 4x150 SE | 125 | 130 | 0.027468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_4181-5_0_4_line_129 | NAYY 4x150 SE | 126 | 131 | 0.017936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_4181-5_0_4_line_130 | NAYY 4x150 SE | 127 | 128 | 0.016088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_4181-5_0_4_line_131 | NAYY 4x150 SE | 128 | 133 | 0.022342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_4181-5_0_4_line_132 | NAYY 4x150 SE | 129 | 134 | 0.027606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_4181-5_0_4_line_133 | NAYY 4x150 SE | 131 | 140 | 0.013272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_4181-5_0_4_line_134 | NAYY 4x150 SE | 132 | 139 | 0.013974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_4181-5_0_4_line_135 | NAYY 4x150 SE | 133 | 143 | 0.0092882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_4181-5_0_4_line_136 | NAYY 4x150 SE | 133 | 144 | 0.041146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_4181-5_0_4_line_137 | NAYY 4x150 SE | 134 | 138 | 0.017533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_4181-5_0_4_line_138 | NAYY 4x150 SE | 134 | 136 | 0.023259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_4181-5_0_4_line_139 | NAYY 4x150 SE | 135 | 137 | 0.011483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_4181-5_0_4_line_140 | NAYY 4x150 SE | 136 | 137 | 0.005893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_4181-5_0_4_line_141 | NAYY 4x150 SE | 138 | 139 | 0.0038726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_4181-5_0_4_line_142 | NAYY 4x150 SE | 140 | 141 | 0.027729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_4181-5_0_4_line_143 | NAYY 4x150 SE | 141 | 142 | 0.0074296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4181-5_0_4_trafo_55 | 0.25 MVA 20/0.4 kV | 145 | 58 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2640123.8808 | 1258602.3861 | 2640114.7118 | 1258602.8776
1 | 2640114.7118 | 1258602.8776 | 2640110.893 | 1258603.0823 | 2640105.6407 | 1258603.1934
2 | 2640105.6407 | 1258603.1934 | 2640105.3636 | 1258603.1992
3 | 2640094.1633 | 1258603.436 | 2640105.3636 | 1258603.1992
4 | 2640094.1633 | 1258603.436 | 2640088.1286 | 1258601.8274 | 2640085.3757 | 1258602.0422 | 2640084.7974 | 1258602.1278
5 | 2640070.9777 | 1258608.7273 | 2640077.7412 | 1258605.1261 | 2640080.5105 | 1258603.6104 | 2640082.7875 | 1258602.425 | 2640084.7974 | 1258602.1278
6 | 2640195.865 | 1258692.8094 | 2640187.1057 | 1258683.9327 | 2640180.4016 | 1258677.5676
7 | 2640164.7228 | 1258667.5918 | 2640178.2002 | 1258675.4775 | 2640180.4016 | 1258677.5676
8 | 2640195.865 | 1258692.8094 | 2640209.4125 | 1258708.2862
9 | 2640195.865 | 1258692.8094 | 2640186.228 | 1258700.5456
10 | 2640158.7388 | 1258664.0821 | 2640164.7228 | 1258667.5918
11 | 2640216.5317 | 1258716.4193 | 2640209.4125 | 1258708.2862
12 | 2640184.6344 | 1258701.8437 | 2640185.1932 | 1258701.3762 | 2640186.228 | 1258700.5456
13 | 2640158.7388 | 1258664.0821 | 2640155.0859 | 1258669.1831 | 2640148.3274 | 1258676.4868 | 2640146.9349 | 1258678.1552
14 | 2640216.5317 | 1258716.4193 | 2640217.6181 | 1258717.6603
15 | 2640171.6746 | 1258712.6832 | 2640184.6344 | 1258701.8437
16 | 2640146.9349 | 1258678.1552 | 2640141.0769 | 1258685.1737
17 | 2640217.6181 | 1258717.6603 | 2640218.7612 | 1258718.9662
18 | 2640100.0552 | 1258637.266 | 2640106.2079 | 1258641.4884 | 2640111.59 | 1258644.2168
19 | 2640100.0552 | 1258637.266 | 2640096.1367 | 1258634.8378
20 | 2640141.0769 | 1258685.1737 | 2640139.3639 | 1258687.2261
21 | 2640153.7165 | 1258727.7033 | 2640186.8571 | 1258765.4235
22 | 2640153.7165 | 1258727.7033 | 2640148.4951 | 1258721.7596
23 | 2640134.6343 | 1258705.9812 | 2640148.4951 | 1258721.7596
24 | 2640134.6343 | 1258705.9812 | 2640123.5891 | 1258714.4314
25 | 2640134.6343 | 1258705.9812 | 2640129.1607 | 1258699.4507
26 | 2640123.5891 | 1258714.4314 | 2640111.4199 | 1258723.7416
27 | 2640129.1607 | 1258699.4507 | 2640125.2498 | 1258694.7779
28 | 2640129.1607 | 1258699.4507 | 2640139.3639 | 1258687.2261
29 | 2640139.0389 | 1258791.3572 | 2640139.4943 | 1258791.8848 | 2640146.5169 | 1258799.8198
30 | 2640146.5169 | 1258799.8198 | 2640104.9511 | 1258838.4227
31 | 2640139.0389 | 1258791.3572 | 2640120.0472 | 1258769.3572
32 | 2640120.0472 | 1258769.3572 | 2640108.9442 | 1258756.4955
33 | 2640108.9442 | 1258756.4955 | 2640102.1318 | 1258748.604
34 | 2640095.7732 | 1258736.3725 | 2640097.6403 | 1258743.4011 | 2640102.1318 | 1258748.604
35 | 2640115.962 | 1258682.683 | 2640119.1183 | 1258687.4521 | 2640125.2498 | 1258694.7779
36 | 2640115.962 | 1258682.683 | 2640109.7166 | 1258673.2453 | 2640108.9795 | 1258671.9686
37 | 2640108.9795 | 1258671.9686 | 2640101.4612 | 1258658.9461 | 2640101.027 | 1258657.5108
38 | 2640104.2431 | 1258729.2323 | 2640111.4199 | 1258723.7416
39 | 2640096.1367 | 1258634.8378 | 2640088.4172 | 1258628.2254
40 | 2640096.1367 | 1258634.8378 | 2640096.2634 | 1258641.7323 | 2640097.4871 | 1258645.8101 | 2640098.9827 | 1258650.7537
41 | 2640095.7732 | 1258736.3725 | 2640099.6573 | 1258732.7407 | 2640104.2431 | 1258729.2323
42 | 2640095.7732 | 1258736.3725 | 2640089.9722 | 1258734.7765 | 2640070.7778 | 1258709.7497
43 | 2640095.7732 | 1258736.3725 | 2640088.3879 | 1258739.4246 | 2640078.9027 | 1258746.7262
44 | 2640055.7923 | 1258764.5162 | 2640078.9027 | 1258746.7262
45 | 2640051.921 | 1258767.4963 | 2640055.7923 | 1258764.5162
46 | 2640039.6345 | 1258776.9543 | 2640051.921 | 1258767.4963
47 | 2640039.6345 | 1258776.9543 | 2640054.8343 | 1258791.2255
48 | 2640039.6345 | 1258776.9543 | 2640017.3184 | 1258752.6247
49 | 2640002.8823 | 1258736.8861 | 2640017.3184 | 1258752.6247
50 | 2640002.8823 | 1258736.8861 | 2639998.9725 | 1258732.6235
51 | 2639997.1692 | 1258730.6575 | 2639998.9725 | 1258732.6235
52 | 2639958.4425 | 1258708.8922 | 2639952.5155 | 1258704.7271 | 2639937.113 | 1258695.909
53 | 2639958.4425 | 1258708.8922 | 2639948.6474 | 1258717.6995
54 | 2639958.4425 | 1258708.8922 | 2639969.4946 | 1258713.1697 | 2639977.3477 | 1258713.3895 | 2639982.1522 | 1258711.8765 | 2639983.1223 | 1258713.3285 | 2639990.6741 | 1258723.5754 | 2639997.1692 | 1258730.6575
55 | 2639997.1692 | 1258730.6575 | 2639981.2063 | 1258751.4753
56 | 2640076.5913 | 1258673.774 | 2640076.4027 | 1258673.6868 | 2640062.5994 | 1258661.9452
57 | 2640054.1279 | 1258649.1302 | 2640056.586 | 1258656.83 | 2640062.5994 | 1258661.9452
58 | 2640098.9827 | 1258650.7537 | 2640101.027 | 1258657.5108
59 | 2640054.1279 | 1258649.1302 | 2640070.0597 | 1258641.8996 | 2640073.9394 | 1258639.594
60 | 2640054.1279 | 1258649.1302 | 2640052.3812 | 1258649.9301 | 2640044.1986 | 1258652.3509
61 | 2640088.4172 | 1258628.2254 | 2640084.3038 | 1258633.4345 | 2640073.9394 | 1258639.594
62 | 2640044.1986 | 1258652.3509 | 2640039.3798 | 1258653.7765
63 | 2640070.9777 | 1258608.7273 | 2640080.6972 | 1258620.5679 | 2640088.4172 | 1258628.2254
64 | 2640038.5907 | 1258654.0099 | 2640039.3798 | 1258653.7765
65 | 2640038.5907 | 1258654.0099 | 2640033.9361 | 1258655.387 | 2640027.9355 | 1258658.5691
66 | 2640027.9355 | 1258658.5691 | 2640025.0545 | 1258660.0969 | 2640021.3185 | 1258660.6187
67 | 2640021.3185 | 1258660.6187 | 2640020.1118 | 1258660.7873
68 | 2639998.3615 | 1258662.1959 | 2640001.0841 | 1258662.2143 | 2640009.4887 | 1258662.2711 | 2640020.1118 | 1258660.7873
69 | 2639996.2674 | 1258662.1817 | 2639998.3615 | 1258662.1959
70 | 2639996.2674 | 1258662.1817 | 2639984.2785 | 1258663.0067
71 | 2639996.2674 | 1258662.1817 | 2639996.9624 | 1258653.0356 | 2639992.6024 | 1258638.8223
72 | 2640070.9777 | 1258608.7273 | 2640065.9071 | 1258602.8408
73 | 2639978.7568 | 1258662.8916 | 2639982.7302 | 1258663.1132 | 2639984.2785 | 1258663.0067
74 | 2639978.7568 | 1258662.8916 | 2639970.4787 | 1258662.4298
75 | 2639949.5571 | 1258662.8003 | 2639959.3709 | 1258661.8103 | 2639970.4787 | 1258662.4298
76 | 2639954.9883 | 1258579.5904 | 2639960.3401 | 1258586.3311 | 2639970.0915 | 1258598.7376
77 | 2639954.9883 | 1258579.5904 | 2639950.4314 | 1258573.8538
78 | 2639954.9883 | 1258579.5904 | 2639970.3008 | 1258565.3078
79 | 2639949.5571 | 1258662.8003 | 2639942.5163 | 1258652.3373
80 | 2639942.5163 | 1258652.3373 | 2639942.2944 | 1258652.0076
81 | 2639942.2944 | 1258652.0076 | 2639936.5607 | 1258643.487
82 | 2639934.0388 | 1258553.2174 | 2639950.4314 | 1258573.8538
83 | 2639970.3008 | 1258565.3078 | 2639980.9779 | 1258555.3489
84 | 2639980.9779 | 1258555.3489 | 2639980.9779 | 1258555.3489 | 2639979.454 | 1258549.946
85 | 2639917.0733 | 1258617.992 | 2639907.1243 | 1258606.2648
86 | 2639891.7595 | 1258588.1537 | 2639907.1243 | 1258606.2648
87 | 2639873.5278 | 1258566.6634 | 2639891.7595 | 1258588.1537
88 | 2640065.9071 | 1258602.8408 | 2640062.8177 | 1258599.2544 | 2640061.3103 | 1258597.5032
89 | 2640052.9433 | 1258589.3978 | 2640057.6868 | 1258593.2933 | 2640061.3103 | 1258597.5032
90 | 2639858.7067 | 1258549.1933 | 2639873.5278 | 1258566.6634
91 | 2640052.9433 | 1258589.3978 | 2640052.7078 | 1258589.2045
92 | 2640043.832 | 1258581.9154 | 2640052.7078 | 1258589.2045
93 | 2640043.832 | 1258581.9154 | 2640033.7747 | 1258573.6561
94 | 2640033.7747 | 1258573.6561 | 2640033.4877 | 1258573.4204
95 | 2640027.0445 | 1258568.0902 | 2640027.4755 | 1258568.4831 | 2640033.4877 | 1258573.4204
96 | 2639853.3728 | 1258542.906 | 2639858.7067 | 1258549.1933
97 | 2640027.0445 | 1258568.0902 | 2640024.3377 | 1258565.6233
98 | 2640016.3418 | 1258558.3358 | 2640024.3377 | 1258565.6233
99 | 2640016.3418 | 1258558.3358 | 2640014.0156 | 1258556.2158
100 | 2640014.0156 | 1258556.2158 | 2640003.058 | 1258546.229
101 | 2639993.7985 | 1258537.7899 | 2640003.058 | 1258546.229
102 | 2639993.7985 | 1258537.7899 | 2639987.1865 | 1258530.1066
103 | 2639993.7985 | 1258537.7899 | 2640001.2751 | 1258527.9558 | 2640003.6353 | 1258518.8049
104 | 2639987.1865 | 1258530.1066 | 2639975.1518 | 1258516.126
105 | 2639987.1865 | 1258530.1066 | 2639980.0635 | 1258536.7076 | 2639977.9646 | 1258540.5405 | 2639977.9626 | 1258540.6276
106 | 2640003.6353 | 1258518.8049 | 2640003.763 | 1258518.3097
107 | 2639978.4907 | 1258546.9852 | 2639979.454 | 1258549.946 | 2639979.454 | 1258549.946
108 | 2639978.4907 | 1258546.9852 | 2639977.8588 | 1258545.0429 | 2639977.9626 | 1258540.6276
109 | 2639912.8881 | 1258525.0137 | 2639916.5145 | 1258530.1968
110 | 2639903.7724 | 1258511.9848 | 2639912.8881 | 1258525.0137
111 | 2639897.6619 | 1258503.2511 | 2639903.7724 | 1258511.9848
112 | 2639897.6619 | 1258503.2511 | 2639907.6503 | 1258502.1176 | 2639917.019 | 1258498.9674 | 2639918.6086 | 1258497.847
113 | 2639883.274 | 1258484.9416 | 2639893.2343 | 1258496.9281 | 2639897.6619 | 1258503.2511
114 | 2639848.3229 | 1258536.9536 | 2639853.3728 | 1258542.906
115 | 2639848.3229 | 1258536.9536 | 2639848.1896 | 1258526.5121 | 2639849.4467 | 1258515.5908
116 | 2640004.9124 | 1258469.3731 | 2640002.5295 | 1258453.8685 | 2640001.2084 | 1258441.8624 | 2640001.9659 | 1258425.7007 | 2640002.2506 | 1258423.2534
117 | 2640004.9124 | 1258469.3731 | 2639989.1362 | 1258465.7752 | 2639986.1424 | 1258465.7938
118 | 2640004.9124 | 1258469.3731 | 2640006.5676 | 1258475.4218 | 2640007.6983 | 1258483.246 | 2640006.6459 | 1258496.1923 | 2640006.0014 | 1258504.1515
119 | 2639982.8937 | 1258465.814 | 2639986.1424 | 1258465.7938
120 | 2640006.0014 | 1258504.1515 | 2640005.3546 | 1258512.1391 | 2640003.763 | 1258518.3097
121 | 2639975.1518 | 1258516.126 | 2639971.8532 | 1258512.294
122 | 2639897.6697 | 1258432.1184 | 2639895.4461 | 1258430.4636 | 2639892.5184 | 1258426.9865
123 | 2639921.0912 | 1258449.5495 | 2639897.6697 | 1258432.1184
124 | 2639887.105 | 1258419.686 | 2639888.1395 | 1258421.7861 | 2639892.5184 | 1258426.9865
125 | 2639922.5689 | 1258450.6491 | 2639921.0912 | 1258449.5495
126 | 2639883.7816 | 1258412.9396 | 2639887.105 | 1258419.686
127 | 2639922.5689 | 1258450.6491 | 2639930.4254 | 1258458.2518
128 | 2639922.5689 | 1258450.6491 | 2639938.6189 | 1258428.3583
129 | 2639883.7816 | 1258412.9396 | 2639882.7205 | 1258405.9609 | 2639881.4958 | 1258396.4016 | 2639881.7016 | 1258395.1795
130 | 2639883.274 | 1258484.9416 | 2639869.0563 | 1258492.4707
131 | 2639852.7592 | 1258506.9134 | 2639853.7747 | 1258504.2342 | 2639862.023 | 1258496.1953 | 2639869.0563 | 1258492.4707
132 | 2639948.5201 | 1258479.0993 | 2639935.5556 | 1258463.2232 | 2639930.4254 | 1258458.2518
133 | 2639881.7016 | 1258395.1795 | 2639883.906 | 1258382.0915
134 | 2639918.6086 | 1258497.847 | 2639922.7376 | 1258494.9365 | 2639930.0581 | 1258489.8349
135 | 2639849.4467 | 1258515.5908 | 2639850.4746 | 1258512.9403 | 2639852.7592 | 1258506.9134
136 | 2639852.7592 | 1258506.9134 | 2639818.4035 | 1258484.2715
137 | 2639948.5201 | 1258479.0993 | 2639937.1963 | 1258484.8603 | 2639933.2353 | 1258487.6207
138 | 2639948.5201 | 1258479.0993 | 2639961.3214 | 1258498.518
139 | 2639964.5649 | 1258503.4381 | 2639965.6601 | 1258505.0996 | 2639971.8532 | 1258512.294
140 | 2639961.3214 | 1258498.518 | 2639964.5649 | 1258503.4381
141 | 2639933.2353 | 1258487.6207 | 2639930.0581 | 1258489.8349
142 | 2639883.906 | 1258382.0915 | 2639886.0974 | 1258369.0803 | 2639886.8168 | 1258354.5639
143 | 2639886.984 | 1258347.1378 | 2639886.9524 | 1258351.8297 | 2639886.8168 | 1258354.5639

## bus_geodata
| x | y | coords
0 | 2640123.8808 | 1258602.3861
1 | 2640114.7118 | 1258602.8776
2 | 2640105.6407 | 1258603.1934
3 | 2640105.3636 | 1258603.1992
4 | 2640094.1633 | 1258603.436
5 | 2640084.7974 | 1258602.1278
6 | 2640180.4016 | 1258677.5676
7 | 2640195.865 | 1258692.8094
8 | 2640164.7228 | 1258667.5918
9 | 2640209.4125 | 1258708.2862
10 | 2640186.228 | 1258700.5456
11 | 2640158.7388 | 1258664.0821
12 | 2640216.5317 | 1258716.4193
13 | 2640184.6344 | 1258701.8437
14 | 2640146.9349 | 1258678.1552
15 | 2640217.6181 | 1258717.6603
16 | 2640171.6746 | 1258712.6832
17 | 2640111.59 | 1258644.2168
18 | 2640100.0552 | 1258637.266
19 | 2640141.0769 | 1258685.1737
20 | 2640218.7612 | 1258718.9662
21 | 2640186.8571 | 1258765.4235
22 | 2640153.7165 | 1258727.7033
23 | 2640148.4951 | 1258721.7596
24 | 2640134.6343 | 1258705.9812
25 | 2640123.5891 | 1258714.4314
26 | 2640129.1607 | 1258699.4507
27 | 2640146.5169 | 1258799.8198
28 | 2640139.0389 | 1258791.3572
29 | 2640104.9511 | 1258838.4227
30 | 2640120.0472 | 1258769.3572
31 | 2640108.9442 | 1258756.4955
32 | 2640102.1318 | 1258748.604
33 | 2640139.3639 | 1258687.2261
34 | 2640125.2498 | 1258694.7779
35 | 2640115.962 | 1258682.683
36 | 2640108.9795 | 1258671.9686
37 | 2640111.4199 | 1258723.7416
38 | 2640096.1367 | 1258634.8378
39 | 2640095.7732 | 1258736.3725
40 | 2640104.2431 | 1258729.2323
41 | 2640070.7778 | 1258709.7497
42 | 2640078.9027 | 1258746.7262
43 | 2640051.921 | 1258767.4963
44 | 2640055.7923 | 1258764.5162
45 | 2640039.6345 | 1258776.9543
46 | 2640054.8343 | 1258791.2255
47 | 2640017.3184 | 1258752.6247
48 | 2640002.8823 | 1258736.8861
49 | 2639998.9725 | 1258732.6235
50 | 2639937.113 | 1258695.909
51 | 2639958.4425 | 1258708.8922
52 | 2639948.6474 | 1258717.6995
53 | 2639997.1692 | 1258730.6575
54 | 2639981.2063 | 1258751.4753
55 | 2640076.5913 | 1258673.774
56 | 2640062.5994 | 1258661.9452
57 | 2640101.027 | 1258657.5108
58 | 2640054.1279 | 1258649.1302
59 | 2640098.9827 | 1258650.7537
60 | 2640073.9394 | 1258639.594
61 | 2640044.1986 | 1258652.3509
62 | 2640088.4172 | 1258628.2254
63 | 2640039.3798 | 1258653.7765
64 | 2640038.5907 | 1258654.0099
65 | 2640027.9355 | 1258658.5691
66 | 2640021.3185 | 1258660.6187
67 | 2640020.1118 | 1258660.7873
68 | 2639998.3615 | 1258662.1959
69 | 2639996.2674 | 1258662.1817
70 | 2640070.9777 | 1258608.7273
71 | 2639984.2785 | 1258663.0067
72 | 2639992.6024 | 1258638.8223
73 | 2639978.7568 | 1258662.8916
74 | 2639970.4787 | 1258662.4298
75 | 2639970.0915 | 1258598.7376
76 | 2639954.9883 | 1258579.5904
77 | 2639949.5571 | 1258662.8003
78 | 2639942.5163 | 1258652.3373
79 | 2639942.2944 | 1258652.0076
80 | 2639950.4314 | 1258573.8538
81 | 2639970.3008 | 1258565.3078
82 | 2639934.0388 | 1258553.2174
83 | 2639980.9779 | 1258555.3489
84 | 2639936.5607 | 1258643.487
85 | 2639917.0733 | 1258617.992
86 | 2639907.1243 | 1258606.2648
87 | 2639891.7595 | 1258588.1537
88 | 2640065.9071 | 1258602.8408
89 | 2640061.3103 | 1258597.5032
90 | 2639873.5278 | 1258566.6634
91 | 2640052.9433 | 1258589.3978
92 | 2640052.7078 | 1258589.2045
93 | 2640043.832 | 1258581.9154
94 | 2640033.7747 | 1258573.6561
95 | 2640033.4877 | 1258573.4204
96 | 2639858.7067 | 1258549.1933
97 | 2640027.0445 | 1258568.0902
98 | 2640024.3377 | 1258565.6233
99 | 2640016.3418 | 1258558.3358
100 | 2640014.0156 | 1258556.2158
101 | 2640003.058 | 1258546.229
102 | 2639993.7985 | 1258537.7899
103 | 2639987.1865 | 1258530.1066
104 | 2640003.6353 | 1258518.8049
105 | 2639979.454 | 1258549.946
106 | 2639978.4907 | 1258546.9852
107 | 2639977.9626 | 1258540.6276
108 | 2639916.5145 | 1258530.1968
109 | 2639912.8881 | 1258525.0137
110 | 2639903.7724 | 1258511.9848
111 | 2639897.6619 | 1258503.2511
112 | 2639853.3728 | 1258542.906
113 | 2639848.3229 | 1258536.9536
114 | 2640002.2506 | 1258423.2534
115 | 2640004.9124 | 1258469.3731
116 | 2639986.1424 | 1258465.7938
117 | 2640006.0014 | 1258504.1515
118 | 2639982.8937 | 1258465.814
119 | 2640003.763 | 1258518.3097
120 | 2639975.1518 | 1258516.126
121 | 2639897.6697 | 1258432.1184
122 | 2639892.5184 | 1258426.9865
123 | 2639921.0912 | 1258449.5495
124 | 2639887.105 | 1258419.686
125 | 2639922.5689 | 1258450.6491
126 | 2639883.7816 | 1258412.9396
127 | 2639883.274 | 1258484.9416
128 | 2639869.0563 | 1258492.4707
129 | 2639930.4254 | 1258458.2518
130 | 2639938.6189 | 1258428.3583
131 | 2639881.7016 | 1258395.1795
132 | 2639918.6086 | 1258497.847
133 | 2639852.7592 | 1258506.9134
134 | 2639948.5201 | 1258479.0993
135 | 2639971.8532 | 1258512.294
136 | 2639961.3214 | 1258498.518
137 | 2639964.5649 | 1258503.4381
138 | 2639933.2353 | 1258487.6207
139 | 2639930.0581 | 1258489.8349
140 | 2639883.906 | 1258382.0915
141 | 2639886.8168 | 1258354.5639
142 | 2639886.984 | 1258347.1378
143 | 2639849.4467 | 1258515.5908
144 | 2639818.4035 | 1258484.2715
145 | 2640088.4172 | 1258628.2254

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1