## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5566-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5566-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5566-3_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5566-3_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5566-3_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_5566-3_0_4_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_5566-3_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_5566-3_0_4_node_74 | 0.4 | n |  | TRUE
8 | bus_LV_5566-3_0_4_node_72 | 0.4 | n |  | TRUE
9 | bus_LV_5566-3_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_5566-3_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_5566-3_0_4_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_5566-3_0_4_node_71 | 0.4 | n |  | TRUE
13 | bus_LV_5566-3_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_5566-3_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_5566-3_0_4_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_5566-3_0_4_node_87 | 0.4 | n |  | TRUE
17 | bus_LV_5566-3_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_5566-3_0_4_node_69 | 0.4 | n |  | TRUE
19 | bus_LV_5566-3_0_4_node_68 | 0.4 | n |  | TRUE
20 | bus_LV_5566-3_0_4_node_88 | 0.4 | n |  | TRUE
21 | bus_LV_5566-3_0_4_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_5566-3_0_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_5566-3_0_4_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_5566-3_0_4_node_73 | 0.4 | n |  | TRUE
25 | bus_LV_5566-3_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_5566-3_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_5566-3_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_5566-3_0_4_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_5566-3_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_5566-3_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_5566-3_0_4_node_79 | 0.4 | n |  | TRUE
32 | bus_LV_5566-3_0_4_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_5566-3_0_4_node_53 | 0.4 | n |  | TRUE
34 | bus_LV_5566-3_0_4_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_5566-3_0_4_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_5566-3_0_4_node_80 | 0.4 | n |  | TRUE
37 | bus_LV_5566-3_0_4_node_81 | 0.4 | n |  | TRUE
38 | bus_LV_5566-3_0_4_node_82 | 0.4 | n |  | TRUE
39 | bus_LV_5566-3_0_4_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_5566-3_0_4_node_42 | 0.4 | n |  | TRUE
41 | bus_LV_5566-3_0_4_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_5566-3_0_4_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_5566-3_0_4_node_32 | 0.4 | n |  | TRUE
44 | bus_LV_5566-3_0_4_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_5566-3_0_4_node_78 | 0.4 | n |  | TRUE
46 | bus_LV_5566-3_0_4_node_76 | 0.4 | n |  | TRUE
47 | bus_LV_5566-3_0_4_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_5566-3_0_4_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_5566-3_0_4_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_5566-3_0_4_node_75 | 0.4 | n |  | TRUE
51 | bus_LV_5566-3_0_4_node_70 | 0.4 | n |  | TRUE
52 | bus_LV_5566-3_0_4_node_67 | 0.4 | n |  | TRUE
53 | bus_LV_5566-3_0_4_node_33 | 0.4 | n |  | TRUE
54 | bus_LV_5566-3_0_4_node_35 | 0.4 | n |  | TRUE
55 | bus_LV_5566-3_0_4_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_5566-3_0_4_node_89 | 0.4 | n |  | TRUE
57 | bus_LV_5566-3_0_4_node_50 | 0.4 | n |  | TRUE
58 | bus_LV_5566-3_0_4_node_84 | 0.4 | n |  | TRUE
59 | bus_LV_5566-3_0_4_node_83 | 0.4 | n |  | TRUE
60 | bus_LV_5566-3_0_4_node_43 | 0.4 | n |  | TRUE
61 | bus_LV_5566-3_0_4_node_48 | 0.4 | n |  | TRUE
62 | bus_LV_5566-3_0_4_node_86 | 0.4 | n |  | TRUE
63 | bus_LV_5566-3_0_4_node_85 | 0.4 | n |  | TRUE
64 | bus_LV_5566-3_0_4_node_39 | 0.4 | n |  | TRUE
65 | bus_LV_5566-3_0_4_node_40 | 0.4 | n |  | TRUE
66 | bus_LV_5566-3_0_4_node_41 | 0.4 | n |  | TRUE
67 | bus_LV_5566-3_0_4_node_61 | 0.4 | n |  | TRUE
68 | bus_LV_5566-3_0_4_node_59 | 0.4 | n |  | TRUE
69 | bus_LV_5566-3_0_4_node_44 | 0.4 | n |  | TRUE
70 | bus_LV_5566-3_0_4_node_45 | 0.4 | n |  | TRUE
71 | bus_LV_5566-3_0_4_node_47 | 0.4 | n |  | TRUE
72 | bus_LV_5566-3_0_4_node_57 | 0.4 | n |  | TRUE
73 | bus_LV_5566-3_0_4_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_5566-3_0_4_node_62 | 0.4 | n |  | TRUE
75 | bus_LV_5566-3_0_4_node_49 | 0.4 | n |  | TRUE
76 | bus_LV_5566-3_0_4_node_51 | 0.4 | n |  | TRUE
77 | bus_LV_5566-3_0_4_node_54 | 0.4 | n |  | TRUE
78 | bus_LV_5566-3_0_4_node_52 | 0.4 | n |  | TRUE
79 | bus_LV_5566-3_0_4_node_65 | 0.4 | n |  | TRUE
80 | bus_LV_5566-3_0_4_node_55 | 0.4 | n |  | TRUE
81 | bus_LV_5566-3_0_4_node_66 | 0.4 | n |  | TRUE
82 | bus_LV_5566-3_0_4_node_56 | 0.4 | n |  | TRUE
83 | bus_LV_5566-3_0_4_node_77 | 0.4 | n |  | TRUE
84 | bus_LV_5566-3_0_4_node_58 | 0.4 | n |  | TRUE
85 | bus_LV_5566-3_0_4_node_60 | 0.4 | n |  | TRUE
86 | bus_LV_5566-3_0_4_node_63 | 0.4 | n |  | TRUE
87 | bus_MV_338_0_node_98 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5566-3_0_4_load_0 | 0 | 0.0052169 | 0.0013075 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5566-3_0_4_load_1 | 1 | 0.0039652 | 0.00099378 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5566-3_0_4_load_3 | 3 | 0.0037161 | 0.00093135 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5566-3_0_4_load_5 | 4 | 0.0059896 | 0.0015011 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5566-3_0_4_load_74 | 7 | 0.0034637 | 0.00086809 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5566-3_0_4_load_72 | 8 | 0.014425 | 0.0036153 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5566-3_0_4_load_9 | 9 | 0.0098215 | 0.0024615 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5566-3_0_4_load_6 | 10 | 0.0077598 | 0.0019448 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5566-3_0_4_load_71 | 12 | 0.010159 | 0.0025462 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5566-3_0_4_load_10 | 14 | 0.0033536 | 0.0008405 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5566-3_0_4_load_87 | 16 | 0.0044172 | 0.0011071 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5566-3_0_4_load_69 | 18 | 0.010754 | 0.0026953 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5566-3_0_4_load_68 | 19 | 0.0018575 | 0.00046553 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5566-3_0_4_load_88 | 20 | 0.0093985 | 0.0023555 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5566-3_0_4_load_23 | 21 | 0.012041 | 0.0030178 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5566-3_0_4_load_20 | 22 | 0.0017775 | 0.00044547 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5566-3_0_4_load_21 | 23 | 0.0017632 | 0.00044191 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5566-3_0_4_load_14 | 26 | 0.0013286 | 0.00033297 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5566-3_0_4_load_15 | 27 | 0.00089675 | 0.00022475 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5566-3_0_4_load_17 | 29 | 0.0019316 | 0.00048411 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5566-3_0_4_load_18 | 30 | 0.00090412 | 0.00022659 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5566-3_0_4_load_79 | 31 | 0.0029851 | 0.00074814 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5566-3_0_4_load_28 | 32 | 0.0012931 | 0.00032407 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5566-3_0_4_load_53 | 33 | 0.0018561 | 0.00046519 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5566-3_0_4_load_80 | 36 | 0.00098133 | 0.00024594 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5566-3_0_4_load_81 | 37 | 4.27e-05 | 1.0702e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5566-3_0_4_load_82 | 38 | 0.00039341 | 9.8598e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5566-3_0_4_load_27 | 39 | 0.0015171 | 0.00038022 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5566-3_0_4_load_42 | 40 | 0.0012249 | 0.00030699 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5566-3_0_4_load_37 | 42 | 0.0027331 | 0.00068498 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5566-3_0_4_load_32 | 43 | 0.0047887 | 0.0012001 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5566-3_0_4_load_26 | 44 | 0.0042455 | 0.001064 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5566-3_0_4_load_78 | 45 | 0.0051138 | 0.0012816 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5566-3_0_4_load_76 | 46 | 0.0015469 | 0.00038769 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5566-3_0_4_load_30 | 48 | 0.0014137 | 0.00035431 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5566-3_0_4_load_31 | 49 | 0.0014417 | 0.00036134 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5566-3_0_4_load_75 | 50 | 0.0017488 | 0.0004383 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5566-3_0_4_load_70 | 51 | 0.0022749 | 0.00057015 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5566-3_0_4_load_67 | 52 | 0.0017278 | 0.00043304 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5566-3_0_4_load_89 | 56 | 0.0016682 | 0.00041809 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5566-3_0_4_load_83 | 59 | 0.0010248 | 0.00025684 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5566-3_0_4_load_43 | 60 | 0.00079521 | 0.0001993 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5566-3_0_4_load_48 | 61 | 0.0013011 | 0.00032608 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5566-3_0_4_load_86 | 62 | 0.0024195 | 0.00060639 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5566-3_0_4_load_85 | 63 | 0.0021652 | 0.00054266 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5566-3_0_4_load_39 | 64 | 0.0018527 | 0.00046432 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5566-3_0_4_load_40 | 65 | 0.0027358 | 0.00068566 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5566-3_0_4_load_41 | 66 | 0.0010209 | 0.00025586 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5566-3_0_4_load_44 | 69 | 0.0016878 | 0.00042299 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5566-3_0_4_load_45 | 70 | 0.0022456 | 0.00056279 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5566-3_0_4_load_62 | 74 | 0.0037488 | 0.00093954 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5566-3_0_4_load_54 | 77 | 0.0062261 | 0.0015604 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5566-3_0_4_load_65 | 79 | 0.0018067 | 0.00045281 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5566-3_0_4_load_55 | 80 | 0.0092954 | 0.0023296 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5566-3_0_4_load_66 | 81 | 0.0044615 | 0.0011182 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5566-3_0_4_load_56 | 82 | 0.0027983 | 0.00070133 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5566-3_0_4_load_77 | 83 | 0.0016409 | 0.00041125 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5566-3_0_4_load_58 | 84 | 0.0019848 | 0.00049743 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5566-3_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.010494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_5566-3_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.010386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_5566-3_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0026329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_5566-3_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.015178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_5566-3_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.020641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_5566-3_0_4_line_5 | NAYY 4x150 SE | 5 | 9 | 0.011349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_5566-3_0_4_line_6 | NAYY 4x150 SE | 5 | 10 | 0.011354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_5566-3_0_4_line_7 | NAYY 4x150 SE | 6 | 7 | 0.0087617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_5566-3_0_4_line_8 | NAYY 4x150 SE | 6 | 8 | 0.0089633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_5566-3_0_4_line_9 | NAYY 4x150 SE | 7 | 11 | 0.0073814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_5566-3_0_4_line_10 | NAYY 4x150 SE | 8 | 12 | 0.0071911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_5566-3_0_4_line_11 | NAYY 4x150 SE | 9 | 15 | 0.012775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_5566-3_0_4_line_12 | NAYY 4x150 SE | 10 | 13 | 0.0085934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_5566-3_0_4_line_13 | NAYY 4x150 SE | 11 | 20 | 0.014718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_5566-3_0_4_line_14 | NAYY 4x150 SE | 12 | 86 | 0.013418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_5566-3_0_4_line_15 | NAYY 4x150 SE | 13 | 14 | 0.019764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_5566-3_0_4_line_16 | NAYY 4x150 SE | 14 | 16 | 0.0093634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_5566-3_0_4_line_17 | NAYY 4x150 SE | 15 | 21 | 0.0012392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_5566-3_0_4_line_18 | NAYY 4x150 SE | 16 | 20 | 0.011223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_5566-3_0_4_line_19 | NAYY 4x150 SE | 17 | 18 | 0.020594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_5566-3_0_4_line_20 | NAYY 4x150 SE | 17 | 19 | 0.025666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_5566-3_0_4_line_21 | NAYY 4x150 SE | 18 | 24 | 0.035889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_5566-3_0_4_line_22 | NAYY 4x150 SE | 19 | 25 | 0.0069456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_5566-3_0_4_line_23 | NAYY 4x150 SE | 22 | 23 | 0.016876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_5566-3_0_4_line_24 | NAYY 4x150 SE | 23 | 25 | 0.003555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_5566-3_0_4_line_25 | NAYY 4x150 SE | 24 | 59 | 0.026271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_5566-3_0_4_line_26 | NAYY 4x150 SE | 24 | 86 | 0.009191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_5566-3_0_4_line_27 | NAYY 4x150 SE | 26 | 27 | 0.010545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_5566-3_0_4_line_28 | NAYY 4x150 SE | 26 | 28 | 0.021454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_5566-3_0_4_line_29 | NAYY 4x150 SE | 27 | 29 | 0.01824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_5566-3_0_4_line_30 | NAYY 4x150 SE | 28 | 30 | 0.0097948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_5566-3_0_4_line_31 | NAYY 4x150 SE | 28 | 31 | 0.17198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_5566-3_0_4_line_32 | NAYY 4x150 SE | 29 | 32 | 0.017898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_5566-3_0_4_line_33 | NAYY 4x150 SE | 30 | 33 | 0.0088653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_5566-3_0_4_line_34 | NAYY 4x150 SE | 31 | 36 | 0.022556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_5566-3_0_4_line_35 | NAYY 4x150 SE | 31 | 37 | 0.46708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_5566-3_0_4_line_36 | NAYY 4x150 SE | 32 | 39 | 0.0060496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_5566-3_0_4_line_37 | NAYY 4x150 SE | 33 | 34 | 0.01695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_5566-3_0_4_line_38 | NAYY 4x150 SE | 34 | 35 | 0.014019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_5566-3_0_4_line_39 | NAYY 4x150 SE | 35 | 40 | 0.0069272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_5566-3_0_4_line_40 | NAYY 4x150 SE | 37 | 38 | 0.17102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_5566-3_0_4_line_41 | NAYY 4x150 SE | 39 | 47 | 0.011157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_5566-3_0_4_line_42 | NAYY 4x150 SE | 40 | 60 | 0.016677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_5566-3_0_4_line_43 | NAYY 4x150 SE | 41 | 42 | 0.0064443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_5566-3_0_4_line_44 | NAYY 4x150 SE | 41 | 43 | 0.026645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_5566-3_0_4_line_45 | NAYY 4x150 SE | 42 | 60 | 0.033739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_5566-3_0_4_line_46 | NAYY 4x150 SE | 43 | 53 | 0.024536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_5566-3_0_4_line_47 | NAYY 4x150 SE | 44 | 45 | 0.01274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_5566-3_0_4_line_48 | NAYY 4x150 SE | 45 | 46 | 0.0003667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_5566-3_0_4_line_49 | NAYY 4x150 SE | 46 | 83 | 0.012912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_5566-3_0_4_line_50 | NAYY 4x150 SE | 47 | 48 | 0.0092735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_5566-3_0_4_line_51 | NAYY 4x150 SE | 47 | 49 | 0.0099259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_5566-3_0_4_line_52 | NAYY 4x150 SE | 48 | 50 | 0.0013986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_5566-3_0_4_line_53 | NAYY 4x150 SE | 49 | 51 | 0.011692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_5566-3_0_4_line_54 | NAYY 4x150 SE | 51 | 52 | 0.016692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_5566-3_0_4_line_55 | NAYY 4x150 SE | 52 | 78 | 0.015799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_5566-3_0_4_line_56 | NAYY 4x150 SE | 53 | 54 | 0.006816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_5566-3_0_4_line_57 | NAYY 4x150 SE | 53 | 55 | 0.003687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_5566-3_0_4_line_58 | NAYY 4x150 SE | 54 | 56 | 0.020258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_5566-3_0_4_line_59 | NAYY 4x150 SE | 54 | 57 | 0.004131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_5566-3_0_4_line_60 | NAYY 4x150 SE | 55 | 58 | 0.018344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_5566-3_0_4_line_61 | NAYY 4x150 SE | 55 | 59 | 0.0092155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_5566-3_0_4_line_62 | NAYY 4x150 SE | 57 | 61 | 0.0396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_5566-3_0_4_line_63 | NAYY 4x150 SE | 58 | 62 | 0.015826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_5566-3_0_4_line_64 | NAYY 4x150 SE | 58 | 63 | 0.012907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_5566-3_0_4_line_65 | NAYY 4x150 SE | 61 | 75 | 0.032506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_5566-3_0_4_line_66 | NAYY 4x150 SE | 64 | 65 | 0.00086022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_5566-3_0_4_line_67 | NAYY 4x150 SE | 65 | 66 | 0.014184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_5566-3_0_4_line_68 | NAYY 4x150 SE | 66 | 67 | 0.018123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_5566-3_0_4_line_69 | NAYY 4x150 SE | 67 | 68 | 0.0197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_5566-3_0_4_line_70 | NAYY 4x150 SE | 68 | 74 | 0.005862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_5566-3_0_4_line_71 | NAYY 4x150 SE | 68 | 84 | 0.020729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_5566-3_0_4_line_72 | NAYY 4x150 SE | 69 | 70 | 0.010077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_5566-3_0_4_line_73 | NAYY 4x150 SE | 70 | 71 | 0.018667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_5566-3_0_4_line_74 | NAYY 4x150 SE | 71 | 72 | 0.003764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_5566-3_0_4_line_75 | NAYY 4x150 SE | 72 | 73 | 0.022369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_5566-3_0_4_line_76 | NAYY 4x150 SE | 72 | 74 | 0.0066759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_5566-3_0_4_line_77 | NAYY 4x150 SE | 73 | 83 | 0.010483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_5566-3_0_4_line_78 | NAYY 4x150 SE | 75 | 76 | 0.040663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_5566-3_0_4_line_79 | NAYY 4x150 SE | 76 | 77 | 0.045238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_5566-3_0_4_line_80 | NAYY 4x150 SE | 77 | 80 | 0.018221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_5566-3_0_4_line_81 | NAYY 4x150 SE | 78 | 79 | 0.018251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_5566-3_0_4_line_82 | NAYY 4x150 SE | 79 | 81 | 0.019609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_5566-3_0_4_line_83 | NAYY 4x150 SE | 80 | 82 | 0.0037999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_5566-3_0_4_line_84 | NAYY 4x150 SE | 84 | 85 | 0.017738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_5566-3_0_4_line_85 | NAYY 4x150 SE | 85 | 86 | 0.007996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5566-3_0_4_trafo_73 | 0.25 MVA 20/0.4 kV | 87 | 24 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2545753.8382 | 1193521.9698 | 2545757.8205 | 1193522.993 | 2545763.7165 | 1193525.4374
1 | 2545743.7794 | 1193519.3852 | 2545753.8382 | 1193521.9698
2 | 2545763.7165 | 1193525.4374 | 2545766.1487 | 1193526.4457
3 | 2545743.7794 | 1193519.3852 | 2545745.2077 | 1193510.5116 | 2545739.8976 | 1193507.3308
4 | 2545785.2162 | 1193534.3506 | 2545766.1487 | 1193526.4457
5 | 2545785.2162 | 1193534.3506 | 2545791.8852 | 1193525.1678
6 | 2545785.2162 | 1193534.3506 | 2545779.2 | 1193543.9795
7 | 2545722.3969 | 1193513.8986 | 2545724.3304 | 1193521.1852 | 2545724.2798 | 1193522.4071
8 | 2545722.3969 | 1193513.8986 | 2545718.7529 | 1193505.7095
9 | 2545723.9742 | 1193529.7822 | 2545724.2798 | 1193522.4071
10 | 2545715.8293 | 1193499.1396 | 2545718.7529 | 1193505.7095
11 | 2545799.6974 | 1193515.0971 | 2545798.0578 | 1193516.6684 | 2545791.8852 | 1193525.1678
12 | 2545774.6465 | 1193551.2673 | 2545779.2 | 1193543.9795
13 | 2545723.9742 | 1193529.7822 | 2545732.04 | 1193532.5438 | 2545737.7402 | 1193534.9632
14 | 2545712.4728 | 1193486.1509 | 2545715.7601 | 1193498.9838 | 2545715.8293 | 1193499.1396
15 | 2545774.6465 | 1193551.2673 | 2545756.6462 | 1193543.1067
16 | 2545756.6462 | 1193543.1067 | 2545752.5294 | 1193541.2403 | 2545748.0711 | 1193539.3481
17 | 2545799.6974 | 1193515.0971 | 2545800.7683 | 1193515.7207
18 | 2545737.7402 | 1193534.9632 | 2545748.0711 | 1193539.3481
19 | 2545706.9594 | 1193541.11 | 2545705.518 | 1193534.3081 | 2545703.8743 | 1193520.7661
20 | 2545706.9594 | 1193541.11 | 2545703.2105 | 1193537.8534 | 2545695.2517 | 1193531.7667 | 2545688.3052 | 1193526.3824 | 2545686.697 | 1193525.3855
21 | 2545703.3246 | 1193485.0557 | 2545702.5997 | 1193491.666 | 2545701.8373 | 1193501.6898 | 2545702.8733 | 1193512.5198 | 2545703.8743 | 1193520.7661
22 | 2545680.7938 | 1193521.7259 | 2545686.697 | 1193525.3855
23 | 2545691.2281 | 1193539.1468 | 2545688.3586 | 1193532.2519 | 2545682.8684 | 1193524.6127
24 | 2545680.7938 | 1193521.7259 | 2545682.8684 | 1193524.6127
25 | 2545703.3246 | 1193485.0557 | 2545702.9431 | 1193480.8234 | 2545701.6907 | 1193476.3656 | 2545690.8906 | 1193464.6016 | 2545689.8189 | 1193463.6681
26 | 2545703.3246 | 1193485.0557 | 2545710.3679 | 1193486.0033 | 2545712.4728 | 1193486.1509
27 | 2545564.5547 | 1193473.7006 | 2545560.58 | 1193483.4679
28 | 2545552.4934 | 1193503.3397 | 2545560.58 | 1193483.4679
29 | 2545571.1724 | 1193456.7802 | 2545568.9602 | 1193464.5341 | 2545565.4716 | 1193471.4476 | 2545564.5547 | 1193473.7006
30 | 2545552.4934 | 1193503.3397 | 2545558.8459 | 1193502.9148 | 2545562.2735 | 1193502.8556
31 | 2545552.4934 | 1193503.3397 | 2545426.7745 | 1193620.6984
32 | 2545571.1724 | 1193456.7802 | 2545573.8863 | 1193447.2683 | 2545574.0114 | 1193439.2626
33 | 2545562.2735 | 1193502.8556 | 2545571.1375 | 1193502.7026
34 | 2545426.7745 | 1193620.6984 | 2545421.3684 | 1193617.8464 | 2545406.5075 | 1193610.8072
35 | 2545426.7745 | 1193620.6984 | 2545258.1917 | 1194056.2927
36 | 2545574.0114 | 1193439.2626 | 2545574.0114 | 1193439.2626 | 2545576.1257 | 1193433.5946
37 | 2545578.1961 | 1193517.8691 | 2545575.8728 | 1193509.6412 | 2545571.1375 | 1193502.7026
38 | 2545592.0936 | 1193515.7413 | 2545578.1961 | 1193517.8691
39 | 2545592.0936 | 1193515.7413 | 2545598.8097 | 1193514.0444
40 | 2545258.1917 | 1194056.2927 | 2545126.2024 | 1194165.0412
41 | 2545580.168 | 1193423.1974 | 2545578.6761 | 1193426.7574 | 2545576.1257 | 1193433.5946
42 | 2545598.8097 | 1193514.0444 | 2545605.2865 | 1193512.408 | 2545614.7839 | 1193509.2878
43 | 2545652.7655 | 1193496.1776 | 2545646.695 | 1193498.3404
44 | 2545652.7655 | 1193496.1776 | 2545655.5069 | 1193495.0853 | 2545660.4906 | 1193491.6491 | 2545664.3978 | 1193487.1777 | 2545670.852 | 1193477.4159
45 | 2545614.7839 | 1193509.2878 | 2545629.9977 | 1193504.2895 | 2545646.695 | 1193498.3404
46 | 2545680.1116 | 1193455.161 | 2545676.0748 | 1193460.4785 | 2545674.4781 | 1193469.2647 | 2545671.1791 | 1193476.9213 | 2545670.852 | 1193477.4159
47 | 2545765.3747 | 1193498.482 | 2545766.6605 | 1193499.4215 | 2545776.6077 | 1193504.4538
48 | 2545765.3747 | 1193498.482 | 2545765.0786 | 1193498.2656
49 | 2545765.0786 | 1193498.2656 | 2545754.6531 | 1193490.6478 | 2545754.6531 | 1193490.6478
50 | 2545580.168 | 1193423.1974 | 2545571.9171 | 1193418.9641
51 | 2545580.168 | 1193423.1974 | 2545589.9926 | 1193424.6118
52 | 2545570.6727 | 1193418.3256 | 2545571.9171 | 1193418.9641
53 | 2545589.9926 | 1193424.6118 | 2545600.72 | 1193426.1562 | 2545601.5569 | 1193426.3284
54 | 2545617.9061 | 1193429.6912 | 2545601.5569 | 1193426.3284
55 | 2545632.8912 | 1193434.568 | 2545622.406 | 1193430.6168 | 2545617.9061 | 1193429.6912
56 | 2545680.1116 | 1193455.161 | 2545675.2511 | 1193450.3691
57 | 2545680.1116 | 1193455.161 | 2545682.8701 | 1193457.615
58 | 2545686.7909 | 1193433.6991 | 2545675.2511 | 1193450.3691
59 | 2545672.3434 | 1193447.4273 | 2545675.2511 | 1193450.3691
60 | 2545693.7717 | 1193442.8408 | 2545682.8701 | 1193457.615
61 | 2545682.8701 | 1193457.615 | 2545689.8189 | 1193463.6681
62 | 2545672.3434 | 1193447.4273 | 2545653.3202 | 1193429.8904 | 2545643.9978 | 1193419.8144
63 | 2545693.7717 | 1193442.8408 | 2545705.9367 | 1193453.0026
64 | 2545693.7717 | 1193442.8408 | 2545700.8705 | 1193433.1374 | 2545701.6666 | 1193433.5213
65 | 2545621.0613 | 1193396.7987 | 2545623.5349 | 1193398.9329 | 2545640.0499 | 1193415.5475 | 2545643.9978 | 1193419.8144
66 | 2545733.9066 | 1193426.7447 | 2545733.264 | 1193426.1727
67 | 2545733.9066 | 1193426.7447 | 2545744.5007 | 1193436.1762
68 | 2545737.0651 | 1193451.5299 | 2545745.5387 | 1193437.1003 | 2545744.5007 | 1193436.1762
69 | 2545752.5183 | 1193463.7297 | 2545740.8663 | 1193453.83 | 2545737.0651 | 1193451.5299
70 | 2545752.5183 | 1193463.7297 | 2545758.3803 | 1193463.7492
71 | 2545752.5183 | 1193463.7297 | 2545741.6421 | 1193467.0638 | 2545734.0754 | 1193472.5617
72 | 2545793.7515 | 1193448.606 | 2545787.7902 | 1193451.0688 | 2545784.5515 | 1193452.7009
73 | 2545768.2697 | 1193461.7967 | 2545776.1975 | 1193456.9108 | 2545784.5515 | 1193452.7009
74 | 2545765.0561 | 1193463.7714 | 2545768.2697 | 1193461.7967
75 | 2545765.0561 | 1193463.7714 | 2545750.6855 | 1193480.9451
76 | 2545765.0561 | 1193463.7714 | 2545758.3803 | 1193463.7492
77 | 2545750.6855 | 1193480.9451 | 2545754.6531 | 1193490.6478
78 | 2545586.9068 | 1193374.8641 | 2545595.5889 | 1193379.1541 | 2545605.8795 | 1193385.1526 | 2545615.7689 | 1193392.2999 | 2545621.0613 | 1193396.7987
79 | 2545586.9068 | 1193374.8641 | 2545576.8353 | 1193381.1928 | 2545561.6453 | 1193386.2008 | 2545550.2649 | 1193386.905 | 2545544.7473 | 1193384.6859
80 | 2545544.7473 | 1193384.6859 | 2545527.8424 | 1193377.8869
81 | 2545632.8912 | 1193434.568 | 2545626.13 | 1193449.5269 | 2545625.6779 | 1193451.3056
82 | 2545625.6779 | 1193451.3056 | 2545623.6798 | 1193459.1658 | 2545634.0052 | 1193464.2262
83 | 2545524.3169 | 1193376.469 | 2545527.8424 | 1193377.8869
84 | 2545719.8614 | 1193483.1709 | 2545726.6278 | 1193477.9731 | 2545734.0754 | 1193472.5617
85 | 2545712.4728 | 1193486.1509 | 2545718.6497 | 1193484.0269 | 2545719.8614 | 1193483.1709

## bus_geodata
| x | y | coords
0 | 2545753.8382 | 1193521.9698
1 | 2545763.7165 | 1193525.4374
2 | 2545743.7794 | 1193519.3852
3 | 2545766.1487 | 1193526.4457
4 | 2545739.8976 | 1193507.3308
5 | 2545785.2162 | 1193534.3506
6 | 2545722.3969 | 1193513.8986
7 | 2545724.2798 | 1193522.4071
8 | 2545718.7529 | 1193505.7095
9 | 2545791.8852 | 1193525.1678
10 | 2545779.2 | 1193543.9795
11 | 2545723.9742 | 1193529.7822
12 | 2545715.8294 | 1193499.1396
13 | 2545774.6465 | 1193551.2673
14 | 2545756.6462 | 1193543.1067
15 | 2545799.6974 | 1193515.0971
16 | 2545748.0711 | 1193539.3481
17 | 2545706.9594 | 1193541.11
18 | 2545703.8743 | 1193520.7661
19 | 2545686.697 | 1193525.3855
20 | 2545737.7402 | 1193534.9632
21 | 2545800.7683 | 1193515.7207
22 | 2545691.2281 | 1193539.1468
23 | 2545682.8684 | 1193524.6127
24 | 2545703.3246 | 1193485.0557
25 | 2545680.7938 | 1193521.7259
26 | 2545560.58 | 1193483.4679
27 | 2545564.5547 | 1193473.7006
28 | 2545552.4934 | 1193503.3397
29 | 2545571.1724 | 1193456.7802
30 | 2545562.2735 | 1193502.8556
31 | 2545426.7745 | 1193620.6984
32 | 2545574.0114 | 1193439.2626
33 | 2545571.1375 | 1193502.7026
34 | 2545578.1961 | 1193517.8691
35 | 2545592.0936 | 1193515.7413
36 | 2545406.5075 | 1193610.8072
37 | 2545258.1917 | 1194056.2927
38 | 2545126.2024 | 1194165.0412
39 | 2545576.1257 | 1193433.5946
40 | 2545598.8097 | 1193514.0444
41 | 2545652.7655 | 1193496.1776
42 | 2545646.695 | 1193498.3404
43 | 2545670.852 | 1193477.4159
44 | 2545776.6077 | 1193504.4538
45 | 2545765.3747 | 1193498.482
46 | 2545765.0786 | 1193498.2656
47 | 2545580.168 | 1193423.1974
48 | 2545571.9171 | 1193418.9641
49 | 2545589.9926 | 1193424.6118
50 | 2545570.6727 | 1193418.3256
51 | 2545601.5569 | 1193426.3284
52 | 2545617.9061 | 1193429.6912
53 | 2545680.1116 | 1193455.161
54 | 2545675.2511 | 1193450.3691
55 | 2545682.8701 | 1193457.615
56 | 2545686.7909 | 1193433.6991
57 | 2545672.3434 | 1193447.4273
58 | 2545693.7717 | 1193442.8408
59 | 2545689.8189 | 1193463.6681
60 | 2545614.7839 | 1193509.2878
61 | 2545643.9978 | 1193419.8144
62 | 2545705.9367 | 1193453.0026
63 | 2545701.6666 | 1193433.5213
64 | 2545733.264 | 1193426.1727
65 | 2545733.9066 | 1193426.7447
66 | 2545744.5007 | 1193436.1762
67 | 2545737.0651 | 1193451.5299
68 | 2545752.5183 | 1193463.7297
69 | 2545793.7515 | 1193448.606
70 | 2545784.5515 | 1193452.7009
71 | 2545768.2697 | 1193461.7967
72 | 2545765.0561 | 1193463.7714
73 | 2545750.6855 | 1193480.9451
74 | 2545758.3803 | 1193463.7492
75 | 2545621.0613 | 1193396.7987
76 | 2545586.9068 | 1193374.8641
77 | 2545544.7473 | 1193384.6859
78 | 2545632.8912 | 1193434.568
79 | 2545625.6779 | 1193451.3056
80 | 2545527.8424 | 1193377.8869
81 | 2545634.0052 | 1193464.2262
82 | 2545524.3169 | 1193376.469
83 | 2545754.6531 | 1193490.6478
84 | 2545734.0754 | 1193472.5617
85 | 2545719.8614 | 1193483.1709
86 | 2545712.4728 | 1193486.1509
87 | 2545712.4728 | 1193486.1509

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1