## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6783-2_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6783-2_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6783-2_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_6783-2_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_6783-2_0_3_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_6783-2_0_3_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_6783-2_0_3_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_6783-2_0_3_node_22 | 0.4 | n |  | TRUE
8 | bus_LV_6783-2_0_3_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_6783-2_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_6783-2_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_6783-2_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_6783-2_0_3_node_115 | 0.4 | n |  | TRUE
13 | bus_LV_6783-2_0_3_node_103 | 0.4 | n |  | TRUE
14 | bus_LV_6783-2_0_3_node_109 | 0.4 | n |  | TRUE
15 | bus_LV_6783-2_0_3_node_94 | 0.4 | n |  | TRUE
16 | bus_LV_6783-2_0_3_node_108 | 0.4 | n |  | TRUE
17 | bus_LV_6783-2_0_3_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_6783-2_0_3_node_106 | 0.4 | n |  | TRUE
19 | bus_LV_6783-2_0_3_node_71 | 0.4 | n |  | TRUE
20 | bus_LV_6783-2_0_3_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_6783-2_0_3_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_6783-2_0_3_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_6783-2_0_3_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_6783-2_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_6783-2_0_3_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_6783-2_0_3_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_6783-2_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_6783-2_0_3_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_6783-2_0_3_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_6783-2_0_3_node_87 | 0.4 | n |  | TRUE
31 | bus_LV_6783-2_0_3_node_91 | 0.4 | n |  | TRUE
32 | bus_LV_6783-2_0_3_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_6783-2_0_3_node_99 | 0.4 | n |  | TRUE
34 | bus_LV_6783-2_0_3_node_85 | 0.4 | n |  | TRUE
35 | bus_LV_6783-2_0_3_node_92 | 0.4 | n |  | TRUE
36 | bus_LV_6783-2_0_3_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_6783-2_0_3_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_6783-2_0_3_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_6783-2_0_3_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_6783-2_0_3_node_28 | 0.4 | n |  | TRUE
41 | bus_LV_6783-2_0_3_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_6783-2_0_3_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_6783-2_0_3_node_31 | 0.4 | n |  | TRUE
44 | bus_LV_6783-2_0_3_node_86 | 0.4 | n |  | TRUE
45 | bus_LV_6783-2_0_3_node_84 | 0.4 | n |  | TRUE
46 | bus_LV_6783-2_0_3_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_6783-2_0_3_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_6783-2_0_3_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_6783-2_0_3_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_6783-2_0_3_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_6783-2_0_3_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_6783-2_0_3_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_6783-2_0_3_node_59 | 0.4 | n |  | TRUE
54 | bus_LV_6783-2_0_3_node_77 | 0.4 | n |  | TRUE
55 | bus_LV_6783-2_0_3_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_6783-2_0_3_node_60 | 0.4 | n |  | TRUE
57 | bus_LV_6783-2_0_3_node_76 | 0.4 | n |  | TRUE
58 | bus_LV_6783-2_0_3_node_42 | 0.4 | n |  | TRUE
59 | bus_LV_6783-2_0_3_node_43 | 0.4 | n |  | TRUE
60 | bus_LV_6783-2_0_3_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_6783-2_0_3_node_44 | 0.4 | n |  | TRUE
62 | bus_LV_6783-2_0_3_node_150 | 0.4 | n |  | TRUE
63 | bus_LV_6783-2_0_3_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_6783-2_0_3_node_97 | 0.4 | n |  | TRUE
65 | bus_LV_6783-2_0_3_node_152 | 0.4 | n |  | TRUE
66 | bus_LV_6783-2_0_3_node_148 | 0.4 | n |  | TRUE
67 | bus_LV_6783-2_0_3_node_110 | 0.4 | n |  | TRUE
68 | bus_LV_6783-2_0_3_node_47 | 0.4 | n |  | TRUE
69 | bus_LV_6783-2_0_3_node_48 | 0.4 | n |  | TRUE
70 | bus_LV_6783-2_0_3_node_49 | 0.4 | n |  | TRUE
71 | bus_LV_6783-2_0_3_node_50 | 0.4 | n |  | TRUE
72 | bus_LV_6783-2_0_3_node_51 | 0.4 | n |  | TRUE
73 | bus_LV_6783-2_0_3_node_52 | 0.4 | n |  | TRUE
74 | bus_LV_6783-2_0_3_node_61 | 0.4 | n |  | TRUE
75 | bus_LV_6783-2_0_3_node_75 | 0.4 | n |  | TRUE
76 | bus_LV_6783-2_0_3_node_127 | 0.4 | n |  | TRUE
77 | bus_LV_6783-2_0_3_node_62 | 0.4 | n |  | TRUE
78 | bus_LV_6783-2_0_3_node_74 | 0.4 | n |  | TRUE
79 | bus_LV_6783-2_0_3_node_128 | 0.4 | n |  | TRUE
80 | bus_LV_6783-2_0_3_node_53 | 0.4 | n |  | TRUE
81 | bus_LV_6783-2_0_3_node_54 | 0.4 | n |  | TRUE
82 | bus_LV_6783-2_0_3_node_55 | 0.4 | n |  | TRUE
83 | bus_LV_6783-2_0_3_node_56 | 0.4 | n |  | TRUE
84 | bus_LV_6783-2_0_3_node_57 | 0.4 | n |  | TRUE
85 | bus_LV_6783-2_0_3_node_58 | 0.4 | n |  | TRUE
86 | bus_LV_6783-2_0_3_node_70 | 0.4 | n |  | TRUE
87 | bus_LV_6783-2_0_3_node_72 | 0.4 | n |  | TRUE
88 | bus_LV_6783-2_0_3_node_66 | 0.4 | n |  | TRUE
89 | bus_LV_6783-2_0_3_node_73 | 0.4 | n |  | TRUE
90 | bus_LV_6783-2_0_3_node_107 | 0.4 | n |  | TRUE
91 | bus_LV_6783-2_0_3_node_65 | 0.4 | n |  | TRUE
92 | bus_LV_6783-2_0_3_node_63 | 0.4 | n |  | TRUE
93 | bus_LV_6783-2_0_3_node_67 | 0.4 | n |  | TRUE
94 | bus_LV_6783-2_0_3_node_68 | 0.4 | n |  | TRUE
95 | bus_LV_6783-2_0_3_node_64 | 0.4 | n |  | TRUE
96 | bus_LV_6783-2_0_3_node_93 | 0.4 | n |  | TRUE
97 | bus_LV_6783-2_0_3_node_69 | 0.4 | n |  | TRUE
98 | bus_LV_6783-2_0_3_node_90 | 0.4 | n |  | TRUE
99 | bus_LV_6783-2_0_3_node_129 | 0.4 | n |  | TRUE
100 | bus_LV_6783-2_0_3_node_83 | 0.4 | n |  | TRUE
101 | bus_LV_6783-2_0_3_node_88 | 0.4 | n |  | TRUE
102 | bus_LV_6783-2_0_3_node_78 | 0.4 | n |  | TRUE
103 | bus_LV_6783-2_0_3_node_80 | 0.4 | n |  | TRUE
104 | bus_LV_6783-2_0_3_node_79 | 0.4 | n |  | TRUE
105 | bus_LV_6783-2_0_3_node_81 | 0.4 | n |  | TRUE
106 | bus_LV_6783-2_0_3_node_82 | 0.4 | n |  | TRUE
107 | bus_LV_6783-2_0_3_node_153 | 0.4 | n |  | TRUE
108 | bus_LV_6783-2_0_3_node_111 | 0.4 | n |  | TRUE
109 | bus_LV_6783-2_0_3_node_112 | 0.4 | n |  | TRUE
110 | bus_LV_6783-2_0_3_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_6783-2_0_3_node_98 | 0.4 | n |  | TRUE
112 | bus_LV_6783-2_0_3_node_130 | 0.4 | n |  | TRUE
113 | bus_LV_6783-2_0_3_node_95 | 0.4 | n |  | TRUE
114 | bus_LV_6783-2_0_3_node_96 | 0.4 | n |  | TRUE
115 | bus_LV_6783-2_0_3_node_105 | 0.4 | n |  | TRUE
116 | bus_LV_6783-2_0_3_node_102 | 0.4 | n |  | TRUE
117 | bus_LV_6783-2_0_3_node_113 | 0.4 | n |  | TRUE
118 | bus_LV_6783-2_0_3_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_6783-2_0_3_node_100 | 0.4 | n |  | TRUE
120 | bus_LV_6783-2_0_3_node_101 | 0.4 | n |  | TRUE
121 | bus_LV_6783-2_0_3_node_118 | 0.4 | n |  | TRUE
122 | bus_LV_6783-2_0_3_node_116 | 0.4 | n |  | TRUE
123 | bus_LV_6783-2_0_3_node_117 | 0.4 | n |  | TRUE
124 | bus_LV_6783-2_0_3_node_114 | 0.4 | n |  | TRUE
125 | bus_LV_6783-2_0_3_node_119 | 0.4 | n |  | TRUE
126 | bus_LV_6783-2_0_3_node_126 | 0.4 | n |  | TRUE
127 | bus_LV_6783-2_0_3_node_120 | 0.4 | n |  | TRUE
128 | bus_LV_6783-2_0_3_node_121 | 0.4 | n |  | TRUE
129 | bus_LV_6783-2_0_3_node_154 | 0.4 | n |  | TRUE
130 | bus_LV_6783-2_0_3_node_122 | 0.4 | n |  | TRUE
131 | bus_LV_6783-2_0_3_node_124 | 0.4 | n |  | TRUE
132 | bus_LV_6783-2_0_3_node_123 | 0.4 | n |  | TRUE
133 | bus_LV_6783-2_0_3_node_125 | 0.4 | n |  | TRUE
134 | bus_LV_6783-2_0_3_node_132 | 0.4 | n |  | TRUE
135 | bus_LV_6783-2_0_3_node_131 | 0.4 | n |  | TRUE
136 | bus_LV_6783-2_0_3_node_133 | 0.4 | n |  | TRUE
137 | bus_LV_6783-2_0_3_node_134 | 0.4 | n |  | TRUE
138 | bus_LV_6783-2_0_3_node_135 | 0.4 | n |  | TRUE
139 | bus_LV_6783-2_0_3_node_151 | 0.4 | n |  | TRUE
140 | bus_LV_6783-2_0_3_node_149 | 0.4 | n |  | TRUE
141 | bus_LV_6783-2_0_3_node_136 | 0.4 | n |  | TRUE
142 | bus_LV_6783-2_0_3_node_137 | 0.4 | n |  | TRUE
143 | bus_LV_6783-2_0_3_node_138 | 0.4 | n |  | TRUE
144 | bus_LV_6783-2_0_3_node_139 | 0.4 | n |  | TRUE
145 | bus_LV_6783-2_0_3_node_142 | 0.4 | n |  | TRUE
146 | bus_LV_6783-2_0_3_node_144 | 0.4 | n |  | TRUE
147 | bus_LV_6783-2_0_3_node_140 | 0.4 | n |  | TRUE
148 | bus_LV_6783-2_0_3_node_141 | 0.4 | n |  | TRUE
149 | bus_LV_6783-2_0_3_node_145 | 0.4 | n |  | TRUE
150 | bus_LV_6783-2_0_3_node_146 | 0.4 | n |  | TRUE
151 | bus_LV_6783-2_0_3_node_147 | 0.4 | n |  | TRUE
152 | bus_MV_344_1_node_15 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6783-2_0_3_load_0 | 0 | 0.0058065 | 0.0014552 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6783-2_0_3_load_1 | 1 | 0.023542 | 0.0059001 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6783-2_0_3_load_3 | 2 | 0.033372 | 0.0083637 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6783-2_0_3_load_13 | 4 | 0.0017567 | 0.00044028 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6783-2_0_3_load_25 | 5 | 0.00055464 | 0.00013901 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6783-2_0_3_load_14 | 6 | 0.0016259 | 0.0004075 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6783-2_0_3_load_22 | 7 | 0.00017407 | 4.3627e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6783-2_0_3_load_5 | 9 | 0.00014653 | 3.6724e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6783-2_0_3_load_6 | 10 | 0.0019167 | 0.00048036 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6783-2_0_3_load_7 | 11 | 0.003497 | 0.00087644 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6783-2_0_3_load_115 | 12 | 0.00014823 | 3.715e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6783-2_0_3_load_103 | 13 | 0.00014138 | 3.5434e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6783-2_0_3_load_109 | 14 | 6.5429e-05 | 1.6398e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6783-2_0_3_load_94 | 15 | 0.00016049 | 4.0223e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6783-2_0_3_load_108 | 16 | 0.00019608 | 4.9143e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6783-2_0_3_load_8 | 17 | 0.00059976 | 0.00015032 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6783-2_0_3_load_106 | 18 | 0.00052453 | 0.00013146 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6783-2_0_3_load_9 | 20 | 0.00016039 | 4.0198e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6783-2_0_3_load_10 | 21 | 0.00030425 | 7.6252e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6783-2_0_3_load_11 | 22 | 0.00029703 | 7.4443e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6783-2_0_3_load_12 | 23 | 0.0010039 | 0.00025161 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6783-2_0_3_load_20 | 27 | 0.00049283 | 0.00012351 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6783-2_0_3_load_19 | 28 | 0.001007 | 0.00025238 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6783-2_0_3_load_21 | 29 | 0.00039286 | 9.846e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6783-2_0_3_load_91 | 31 | 0.0025736 | 0.00064501 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6783-2_0_3_load_33 | 32 | 0.00033489 | 8.3931e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6783-2_0_3_load_99 | 33 | 0.0021338 | 0.00053478 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6783-2_0_3_load_85 | 34 | 0.0021203 | 0.00053139 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6783-2_0_3_load_92 | 35 | 0.0037996 | 0.00095226 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6783-2_0_3_load_32 | 36 | 0.00048465 | 0.00012146 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6783-2_0_3_load_24 | 37 | 0.0003792 | 9.5036e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6783-2_0_3_load_26 | 38 | 0.00034559 | 8.6613e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6783-2_0_3_load_27 | 39 | 0.00013717 | 3.4378e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6783-2_0_3_load_29 | 41 | 0.0001776 | 4.4511e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6783-2_0_3_load_30 | 42 | 0.00065131 | 0.00016323 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6783-2_0_3_load_31 | 43 | 0.0019127 | 0.00047938 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6783-2_0_3_load_86 | 44 | 0.0018509 | 0.00046388 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6783-2_0_3_load_84 | 45 | 0.0011362 | 0.00028476 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6783-2_0_3_load_34 | 46 | 0.0027606 | 0.00069186 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6783-2_0_3_load_35 | 47 | 0.0040564 | 0.0010166 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6783-2_0_3_load_37 | 49 | 0.0011315 | 0.00028358 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6783-2_0_3_load_38 | 50 | 0.00073008 | 0.00018297 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6783-2_0_3_load_39 | 51 | 0.0010672 | 0.00026746 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6783-2_0_3_load_40 | 52 | 0.0046442 | 0.0011639 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6783-2_0_3_load_59 | 53 | 0.00089688 | 0.00022478 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6783-2_0_3_load_60 | 56 | 0.0018068 | 0.00045282 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6783-2_0_3_load_42 | 58 | 0.0038054 | 0.00095373 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6783-2_0_3_load_43 | 59 | 0.0039358 | 0.00098642 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6783-2_0_3_load_45 | 60 | 0.001173 | 0.00029399 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6783-2_0_3_load_44 | 61 | 0.0012295 | 0.00030815 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6783-2_0_3_load_46 | 63 | 0.00044869 | 0.00011245 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6783-2_0_3_load_97 | 64 | 0.0011605 | 0.00029085 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6783-2_0_3_load_152 | 65 | 0.00081172 | 0.00020344 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6783-2_0_3_load_148 | 66 | 0.0011255 | 0.00028207 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6783-2_0_3_load_110 | 67 | 0.00055651 | 0.00013947 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6783-2_0_3_load_47 | 68 | 0.0011061 | 0.00027721 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6783-2_0_3_load_48 | 69 | 0.0010082 | 0.00025269 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6783-2_0_3_load_61 | 74 | 0.0011843 | 0.00029681 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6783-2_0_3_load_75 | 75 | 0.000561 | 0.0001406 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6783-2_0_3_load_127 | 76 | 0.0010205 | 0.00025575 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6783-2_0_3_load_62 | 77 | 0.0013516 | 0.00033873 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6783-2_0_3_load_74 | 78 | 0.00040738 | 0.0001021 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6783-2_0_3_load_128 | 79 | 0.00098268 | 0.00024628 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_6783-2_0_3_load_53 | 80 | 0.0016372 | 0.00041032 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_6783-2_0_3_load_54 | 81 | 0.0014206 | 0.00035604 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_6783-2_0_3_load_56 | 83 | 0.0018765 | 0.0004703 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_6783-2_0_3_load_57 | 84 | 0.0030657 | 0.00076835 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_6783-2_0_3_load_58 | 85 | 0.005452 | 0.0013664 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_6783-2_0_3_load_70 | 86 | 0.0017598 | 0.00044104 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_6783-2_0_3_load_72 | 87 | 0.0034299 | 0.00085961 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_6783-2_0_3_load_66 | 88 | 0.0028672 | 0.0007186 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_6783-2_0_3_load_73 | 89 | 0.011883 | 0.0029781 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_6783-2_0_3_load_107 | 90 | 0.0022172 | 0.00055569 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_6783-2_0_3_load_65 | 91 | 0.0019775 | 0.0004956 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_6783-2_0_3_load_63 | 92 | 0.00058928 | 0.00014769 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_6783-2_0_3_load_67 | 93 | 0.001252 | 0.00031379 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_6783-2_0_3_load_68 | 94 | 0.0013933 | 0.00034919 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_6783-2_0_3_load_64 | 95 | 0.0031295 | 0.00078433 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_6783-2_0_3_load_93 | 96 | 0.0014099 | 0.00035335 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_6783-2_0_3_load_69 | 97 | 0.001099 | 0.00027544 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_6783-2_0_3_load_90 | 98 | 0.0011584 | 0.00029031 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_6783-2_0_3_load_129 | 99 | 0.0010397 | 0.00026057 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_6783-2_0_3_load_83 | 100 | 0.0038355 | 0.00096126 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_6783-2_0_3_load_80 | 103 | 0.0017782 | 0.00044566 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_6783-2_0_3_load_79 | 104 | 0.0028266 | 0.00070842 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_6783-2_0_3_load_81 | 105 | 0.00072557 | 0.00018185 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_6783-2_0_3_load_153 | 107 | 0.002328 | 0.00058345 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_6783-2_0_3_load_112 | 109 | 0.0063717 | 0.0015969 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_6783-2_0_3_load_89 | 110 | 0.0021915 | 0.00054923 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_6783-2_0_3_load_98 | 111 | 0.0014181 | 0.0003554 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_6783-2_0_3_load_130 | 112 | 0.00072657 | 0.0001821 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_6783-2_0_3_load_95 | 113 | 0.00024595 | 6.164e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_6783-2_0_3_load_105 | 115 | 0.0002311 | 5.792e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_6783-2_0_3_load_113 | 117 | 6.3029e-05 | 1.5796e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_6783-2_0_3_load_100 | 119 | 0.0001055 | 2.6442e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_6783-2_0_3_load_101 | 120 | 0.00041906 | 0.00010503 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_6783-2_0_3_load_118 | 121 | 0.00022863 | 5.73e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_6783-2_0_3_load_116 | 122 | 8.5596e-05 | 2.1452e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_6783-2_0_3_load_114 | 124 | 0.00015328 | 3.8415e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_6783-2_0_3_load_119 | 125 | 0.00092961 | 0.00023298 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_6783-2_0_3_load_126 | 126 | 0.00044966 | 0.00011269 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_6783-2_0_3_load_120 | 127 | 0.00083391 | 0.000209 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_6783-2_0_3_load_121 | 128 | 0.00032722 | 8.2008e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_6783-2_0_3_load_154 | 129 | 0.0018335 | 0.00045952 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_6783-2_0_3_load_122 | 130 | 0.0020943 | 0.00052489 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_6783-2_0_3_load_124 | 131 | 0.00043311 | 0.00010855 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_6783-2_0_3_load_123 | 132 | 0.00058567 | 0.00014678 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_6783-2_0_3_load_125 | 133 | 0.0014021 | 0.0003514 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_6783-2_0_3_load_132 | 134 | 0.0011953 | 0.00029956 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_6783-2_0_3_load_133 | 136 | 0.00094128 | 0.00023591 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_6783-2_0_3_load_134 | 137 | 0.00090571 | 0.00022699 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_6783-2_0_3_load_135 | 138 | 0.0013465 | 0.00033745 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_6783-2_0_3_load_151 | 139 | 0.0011136 | 0.00027909 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_6783-2_0_3_load_136 | 141 | 0.0021298 | 0.00053378 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_6783-2_0_3_load_137 | 142 | 0.0015754 | 0.00039483 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_6783-2_0_3_load_138 | 143 | 0.001147 | 0.00028747 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_6783-2_0_3_load_139 | 144 | 0.0014155 | 0.00035475 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_6783-2_0_3_load_144 | 146 | 0.0014087 | 0.00035305 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_6783-2_0_3_load_140 | 147 | 0.0021616 | 0.00054175 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_6783-2_0_3_load_141 | 148 | 0.0021108 | 0.00052902 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_6783-2_0_3_load_145 | 149 | 0.0011934 | 0.00029909 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_6783-2_0_3_load_146 | 150 | 0.0020342 | 0.00050982 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_6783-2_0_3_load_147 | 151 | 0.00048742 | 0.00012216 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 95 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6783-2_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.059265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_6783-2_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.12688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_6783-2_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.02104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_6783-2_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.032821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_6783-2_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.050768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_6783-2_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.02648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_6783-2_0_3_line_6 | NAYY 4x150 SE | 5 | 8 | 0.007104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_6783-2_0_3_line_7 | NAYY 4x150 SE | 7 | 8 | 0.03289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_6783-2_0_3_line_8 | NAYY 4x150 SE | 8 | 37 | 0.017044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_6783-2_0_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.0047362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_6783-2_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.092693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_6783-2_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.082349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_6783-2_0_3_line_12 | NAYY 4x150 SE | 12 | 13 | 0.030967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_6783-2_0_3_line_13 | NAYY 4x150 SE | 13 | 120 | 0.00030379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_6783-2_0_3_line_14 | NAYY 4x150 SE | 14 | 15 | 0.054965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_6783-2_0_3_line_15 | NAYY 4x150 SE | 14 | 16 | 0.0078169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_6783-2_0_3_line_16 | NAYY 4x150 SE | 15 | 113 | 0.056156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_6783-2_0_3_line_17 | NAYY 4x150 SE | 16 | 67 | 0.048336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_6783-2_0_3_line_18 | NAYY 4x150 SE | 17 | 18 | 0.17247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_6783-2_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.025888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_6783-2_0_3_line_20 | NAYY 4x150 SE | 19 | 64 | 0.019606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_6783-2_0_3_line_21 | NAYY 4x150 SE | 19 | 86 | 0.012124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_6783-2_0_3_line_22 | NAYY 4x150 SE | 20 | 21 | 0.018885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_6783-2_0_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.00049742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_6783-2_0_3_line_24 | NAYY 4x150 SE | 21 | 23 | 0.024177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_6783-2_0_3_line_25 | NAYY 4x150 SE | 23 | 24 | 0.047327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_6783-2_0_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.016037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_6783-2_0_3_line_27 | NAYY 4x150 SE | 24 | 26 | 0.019786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_6783-2_0_3_line_28 | NAYY 4x150 SE | 25 | 29 | 0.018083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
29 | LV_6783-2_0_3_line_29 | NAYY 4x150 SE | 25 | 28 | 0.023242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_6783-2_0_3_line_30 | NAYY 4x150 SE | 26 | 30 | 0.004387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_6783-2_0_3_line_31 | NAYY 4x150 SE | 26 | 31 | 0.035929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_6783-2_0_3_line_32 | NAYY 4x150 SE | 27 | 28 | 0.029257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_6783-2_0_3_line_33 | NAYY 4x150 SE | 29 | 32 | 0.0091933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_6783-2_0_3_line_34 | NAYY 4x150 SE | 30 | 33 | 0.019667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_6783-2_0_3_line_35 | NAYY 4x150 SE | 30 | 34 | 0.045576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_6783-2_0_3_line_36 | NAYY 4x150 SE | 31 | 35 | 6.1489e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_6783-2_0_3_line_37 | NAYY 4x150 SE | 32 | 36 | 0.020064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_6783-2_0_3_line_38 | NAYY 4x150 SE | 33 | 111 | 0.0072185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_6783-2_0_3_line_39 | NAYY 4x150 SE | 34 | 45 | 0.011047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_6783-2_0_3_line_40 | NAYY 4x150 SE | 35 | 96 | 0.014967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_6783-2_0_3_line_41 | NAYY 4x150 SE | 36 | 40 | 0.014445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_6783-2_0_3_line_42 | NAYY 4x150 SE | 37 | 38 | 0.032136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_6783-2_0_3_line_43 | NAYY 4x150 SE | 38 | 39 | 0.014962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_6783-2_0_3_line_44 | NAYY 4x150 SE | 39 | 40 | 0.022014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_6783-2_0_3_line_45 | NAYY 4x150 SE | 41 | 42 | 0.025295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_6783-2_0_3_line_46 | NAYY 4x150 SE | 42 | 43 | 0.0076837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_6783-2_0_3_line_47 | NAYY 4x150 SE | 43 | 44 | 0.016866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_6783-2_0_3_line_48 | NAYY 4x150 SE | 44 | 45 | 0.0056768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_6783-2_0_3_line_49 | NAYY 4x150 SE | 46 | 47 | 0.024743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_6783-2_0_3_line_50 | NAYY 4x150 SE | 46 | 48 | 0.024471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_6783-2_0_3_line_51 | NAYY 4x150 SE | 47 | 49 | 0.011723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_6783-2_0_3_line_52 | NAYY 4x150 SE | 48 | 50 | 0.030908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_6783-2_0_3_line_53 | NAYY 4x150 SE | 48 | 51 | 0.028121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_6783-2_0_3_line_54 | NAYY 4x150 SE | 49 | 52 | 0.023884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_6783-2_0_3_line_55 | NAYY 4x150 SE | 50 | 53 | 0.034789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_6783-2_0_3_line_56 | NAYY 4x150 SE | 51 | 54 | 0.0073846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_6783-2_0_3_line_57 | NAYY 4x150 SE | 52 | 55 | 0.028106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_6783-2_0_3_line_58 | NAYY 4x150 SE | 53 | 56 | 0.029897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_6783-2_0_3_line_59 | NAYY 4x150 SE | 54 | 57 | 0.016412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_6783-2_0_3_line_60 | NAYY 4x150 SE | 55 | 58 | 0.060295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_6783-2_0_3_line_61 | NAYY 4x150 SE | 57 | 102 | 0.017967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_6783-2_0_3_line_62 | NAYY 4x150 SE | 57 | 78 | 0.0063961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_6783-2_0_3_line_63 | NAYY 4x150 SE | 59 | 60 | 0.0042834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_6783-2_0_3_line_64 | NAYY 4x150 SE | 60 | 63 | 0.026813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_6783-2_0_3_line_65 | NAYY 4x150 SE | 60 | 64 | 0.046078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_6783-2_0_3_line_66 | NAYY 4x150 SE | 61 | 62 | 0.043138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_6783-2_0_3_line_67 | NAYY 4x150 SE | 62 | 65 | 0.024073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_6783-2_0_3_line_68 | NAYY 4x150 SE | 62 | 66 | 0.018965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_6783-2_0_3_line_69 | NAYY 4x150 SE | 63 | 67 | 0.022893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_6783-2_0_3_line_70 | NAYY 4x150 SE | 66 | 151 | 0.021967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_6783-2_0_3_line_71 | NAYY 4x150 SE | 68 | 69 | 0.016745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_6783-2_0_3_line_72 | NAYY 4x150 SE | 68 | 70 | 0.025857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_6783-2_0_3_line_73 | NAYY 4x150 SE | 69 | 71 | 0.015152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_6783-2_0_3_line_74 | NAYY 4x150 SE | 70 | 72 | 0.011849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_6783-2_0_3_line_75 | NAYY 4x150 SE | 70 | 73 | 0.033394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_6783-2_0_3_line_76 | NAYY 4x150 SE | 71 | 74 | 0.0128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_6783-2_0_3_line_77 | NAYY 4x150 SE | 72 | 75 | 0.0095631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_6783-2_0_3_line_78 | NAYY 4x150 SE | 73 | 76 | 0.051977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_6783-2_0_3_line_79 | NAYY 4x150 SE | 74 | 77 | 0.00337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_6783-2_0_3_line_80 | NAYY 4x150 SE | 75 | 78 | 0.020888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_6783-2_0_3_line_81 | NAYY 4x150 SE | 76 | 79 | 0.032457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_6783-2_0_3_line_82 | NAYY 4x150 SE | 77 | 92 | 0.0047848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_6783-2_0_3_line_83 | NAYY 4x150 SE | 80 | 81 | 0.013606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_6783-2_0_3_line_84 | NAYY 4x150 SE | 80 | 82 | 0.033727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_6783-2_0_3_line_85 | NAYY 4x150 SE | 81 | 83 | 0.0096702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_6783-2_0_3_line_86 | NAYY 4x150 SE | 82 | 84 | 0.021604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
87 | LV_6783-2_0_3_line_87 | NAYY 4x150 SE | 82 | 85 | 0.031773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_6783-2_0_3_line_88 | NAYY 4x150 SE | 83 | 86 | 0.035352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_6783-2_0_3_line_89 | NAYY 4x150 SE | 84 | 87 | 0.0027946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
90 | LV_6783-2_0_3_line_90 | NAYY 4x150 SE | 85 | 88 | 0.021657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
91 | LV_6783-2_0_3_line_91 | NAYY 4x150 SE | 87 | 89 | 0.014067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
92 | LV_6783-2_0_3_line_92 | NAYY 4x150 SE | 88 | 90 | 0.017327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
93 | LV_6783-2_0_3_line_93 | NAYY 4x150 SE | 88 | 91 | 0.012988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
94 | LV_6783-2_0_3_line_94 | NAYY 4x150 SE | 89 | 100 | 0.0065943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
95 | LV_6783-2_0_3_line_95 | NAYY 4x150 SE | 90 | 96 | 0.017475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_6783-2_0_3_line_96 | NAYY 4x150 SE | 91 | 95 | 0.029961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_6783-2_0_3_line_97 | NAYY 4x150 SE | 92 | 93 | 0.026569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
98 | LV_6783-2_0_3_line_98 | NAYY 4x150 SE | 93 | 94 | 0.0058302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
99 | LV_6783-2_0_3_line_99 | NAYY 4x150 SE | 94 | 97 | 0.038804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_6783-2_0_3_line_100 | NAYY 4x150 SE | 97 | 98 | 0.028758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_6783-2_0_3_line_101 | NAYY 4x150 SE | 98 | 99 | 0.03558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_6783-2_0_3_line_102 | NAYY 4x150 SE | 99 | 112 | 0.0062787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
103 | LV_6783-2_0_3_line_103 | NAYY 4x150 SE | 100 | 101 | 0.041381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
104 | LV_6783-2_0_3_line_104 | NAYY 4x150 SE | 101 | 110 | 0.014468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
105 | LV_6783-2_0_3_line_105 | NAYY 4x150 SE | 102 | 103 | 0.046361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_6783-2_0_3_line_106 | NAYY 4x150 SE | 103 | 104 | 0.029286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_6783-2_0_3_line_107 | NAYY 4x150 SE | 104 | 105 | 0.024734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_6783-2_0_3_line_108 | NAYY 4x150 SE | 105 | 106 | 0.044311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_6783-2_0_3_line_109 | NAYY 4x150 SE | 106 | 107 | 0.027846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_6783-2_0_3_line_110 | NAYY 4x150 SE | 108 | 109 | 0.019466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
111 | LV_6783-2_0_3_line_111 | NAYY 4x150 SE | 108 | 110 | 0.028566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
112 | LV_6783-2_0_3_line_112 | NAYY 4x150 SE | 109 | 134 | 0.045292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
113 | LV_6783-2_0_3_line_113 | NAYY 4x150 SE | 112 | 135 | 0.012093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
114 | LV_6783-2_0_3_line_114 | NAYY 4x150 SE | 113 | 114 | 0.024127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_6783-2_0_3_line_115 | NAYY 4x150 SE | 114 | 115 | 0.032353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_6783-2_0_3_line_116 | NAYY 4x150 SE | 114 | 116 | 0.030769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_6783-2_0_3_line_117 | NAYY 4x150 SE | 115 | 117 | 0.021354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_6783-2_0_3_line_118 | NAYY 4x150 SE | 116 | 118 | 0.016468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_6783-2_0_3_line_119 | NAYY 4x150 SE | 116 | 119 | 0.016513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_6783-2_0_3_line_120 | NAYY 4x150 SE | 117 | 124 | 0.008842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_6783-2_0_3_line_121 | NAYY 4x150 SE | 118 | 121 | 0.026279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_6783-2_0_3_line_122 | NAYY 4x150 SE | 118 | 122 | 0.03778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_6783-2_0_3_line_123 | NAYY 4x150 SE | 119 | 120 | 0.010085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_6783-2_0_3_line_124 | NAYY 4x150 SE | 122 | 123 | 0.04147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_6783-2_0_3_line_125 | NAYY 4x150 SE | 123 | 125 | 0.017718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_6783-2_0_3_line_126 | NAYY 4x150 SE | 125 | 126 | 0.00783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_6783-2_0_3_line_127 | NAYY 4x150 SE | 126 | 133 | 0.038203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_6783-2_0_3_line_128 | NAYY 4x150 SE | 127 | 128 | 0.0050822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_6783-2_0_3_line_129 | NAYY 4x150 SE | 127 | 129 | 0.054609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_6783-2_0_3_line_130 | NAYY 4x150 SE | 128 | 130 | 0.018309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_6783-2_0_3_line_131 | NAYY 4x150 SE | 130 | 131 | 0.026643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_6783-2_0_3_line_132 | NAYY 4x150 SE | 131 | 132 | 0.0088881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_6783-2_0_3_line_133 | NAYY 4x150 SE | 132 | 133 | 0.014396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_6783-2_0_3_line_134 | NAYY 4x150 SE | 134 | 135 | 0.013471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
135 | LV_6783-2_0_3_line_135 | NAYY 4x150 SE | 135 | 136 | 0.034602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_6783-2_0_3_line_136 | NAYY 4x150 SE | 136 | 137 | 0.016801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_6783-2_0_3_line_137 | NAYY 4x150 SE | 137 | 138 | 0.022393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_6783-2_0_3_line_138 | NAYY 4x150 SE | 138 | 139 | 0.0069305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_6783-2_0_3_line_139 | NAYY 4x150 SE | 139 | 140 | 0.014404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_6783-2_0_3_line_140 | NAYY 4x150 SE | 140 | 151 | 0.018359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_6783-2_0_3_line_141 | NAYY 4x150 SE | 140 | 150 | 0.0030556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_6783-2_0_3_line_142 | NAYY 4x150 SE | 141 | 142 | 0.021746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_6783-2_0_3_line_143 | NAYY 4x150 SE | 141 | 143 | 0.0029759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_6783-2_0_3_line_144 | NAYY 4x150 SE | 142 | 144 | 0.012963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_6783-2_0_3_line_145 | NAYY 4x150 SE | 144 | 145 | 0.025993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_6783-2_0_3_line_146 | NAYY 4x150 SE | 145 | 146 | 0.0016121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_6783-2_0_3_line_147 | NAYY 4x150 SE | 145 | 147 | 0.026525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_6783-2_0_3_line_148 | NAYY 4x150 SE | 146 | 149 | 0.027205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_6783-2_0_3_line_149 | NAYY 4x150 SE | 147 | 148 | 0.0029376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_6783-2_0_3_line_150 | NAYY 4x150 SE | 149 | 150 | 0.021773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6783-2_0_3_trafo_64 | 0.25 MVA 20/0.4 kV | 152 | 95 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2570844.6695 | 1254559.3451 | 2570884.3352 | 1254546.8471 | 2570901.644 | 1254543.2591
1 | 2570844.6695 | 1254559.3451 | 2570724.1118 | 1254598.8898
2 | 2570922.2464 | 1254538.9883 | 2570901.644 | 1254543.2591
3 | 2570922.2464 | 1254538.9883 | 2570921.963 | 1254528.9274 | 2570923.7625 | 1254525.1938 | 2570932.4552 | 1254522.7271 | 2570942.0163 | 1254522.1984
4 | 2570922.2464 | 1254538.9883 | 2570954.5732 | 1254578.1332
5 | 2570968.1685 | 1254523.463 | 2570962.5923 | 1254521.5669 | 2570950.5541 | 1254521.7262 | 2570942.0163 | 1254522.1984
6 | 2570954.5732 | 1254578.1332 | 2570959.3138 | 1254583.4356
7 | 2570959.3138 | 1254583.4356 | 2570952.5608 | 1254584.5807 | 2570945.9256 | 1254586.6815 | 2570931.0775 | 1254598.6644
8 | 2570959.3138 | 1254583.4356 | 2570965.098 | 1254584.6747 | 2570972.8829 | 1254584.7476 | 2570976.1674 | 1254584.1226
9 | 2571045.9077 | 1254049.2924 | 2571047.5893 | 1254049.6665 | 2571050.5134 | 1254050.3949
10 | 2571045.9077 | 1254049.2924 | 2570980.8429 | 1254115.3112
11 | 2571130.9652 | 1254067.9678 | 2571050.5134 | 1254050.3949
12 | 2571161.6234 | 1254072.3209 | 2571153.6031 | 1254071.3065 | 2571130.9652 | 1254067.9678
13 | 2571161.6234 | 1254072.3209 | 2571161.9248 | 1254072.359
14 | 2571157.4392 | 1254237.1766 | 2571172.2359 | 1254184.2411
15 | 2571157.4392 | 1254237.1766 | 2571160.7379 | 1254244.2633
16 | 2571172.2359 | 1254184.2411 | 2571172.2963 | 1254183.9239 | 2571180.2469 | 1254162.2039 | 2571184.2723 | 1254149.2644 | 2571185.7916 | 1254140.6068 | 2571186.7424 | 1254131.396 | 2571186.7515 | 1254130.2934
17 | 2571160.7379 | 1254244.2633 | 2571206.1593 | 1254227.7339
18 | 2571161.6394 | 1254293.4922 | 2570989.6549 | 1254306.4652
19 | 2571177.0625 | 1254307.1498 | 2571172.9642 | 1254306.6917 | 2571163.8827 | 1254303.7897 | 2571159.9345 | 1254300.1065 | 2571161.6394 | 1254293.4922
20 | 2571177.0625 | 1254307.1498 | 2571179.9027 | 1254287.7503
21 | 2571177.0625 | 1254307.1498 | 2571175.3084 | 1254319.1466
22 | 2571039.6944 | 1254485.2415 | 2571038.0589 | 1254491.665 | 2571038.7924 | 1254496.6425 | 2571040.4845 | 1254500.2032 | 2571043.1334 | 1254502.1434
23 | 2571039.9231 | 1254484.7998 | 2571039.6944 | 1254485.2415 | 2571039.6944 | 1254485.2415
24 | 2571043.1334 | 1254502.1434 | 2571047.8884 | 1254505.6261 | 2571061.7446 | 1254513.1521 | 2571063.7298 | 1254514.6952
25 | 2571100.3916 | 1254544.5394 | 2571095.9184 | 1254539.9026 | 2571076.3285 | 1254524.4882 | 2571063.7298 | 1254514.6952
26 | 2571100.3916 | 1254544.5394 | 2571084.3202 | 1254545.1852
27 | 2571119.8182 | 1254540.4971 | 2571110.3157 | 1254542.445 | 2571100.3916 | 1254544.5394
28 | 2571084.3202 | 1254545.1852 | 2571081.0423 | 1254555.119 | 2571077.3566 | 1254561.7912
29 | 2571084.3202 | 1254545.1852 | 2571071.0266 | 1254544.6944 | 2571061.1202 | 1254543.8809
30 | 2571119.8182 | 1254540.4971 | 2571120.8499 | 1254544.7616
31 | 2571119.8182 | 1254540.4971 | 2571117.9498 | 1254533.2792 | 2571116.8844 | 1254526.7356 | 2571116.6516 | 1254520.7883 | 2571117.4864 | 1254511.0444 | 2571118.6227 | 1254505.0395
32 | 2571031.961 | 1254541.4862 | 2571061.1202 | 1254543.8809
33 | 2571077.3566 | 1254561.7912 | 2571076.2571 | 1254563.7816 | 2571070.9326 | 1254568.2006
34 | 2571120.8499 | 1254544.7616 | 2571140.4771 | 1254543.5182
35 | 2571120.8499 | 1254544.7616 | 2571123.5801 | 1254553.9322 | 2571124.7618 | 1254565.7232 | 2571122.9007 | 1254576.9398 | 2571117.8619 | 1254587.7162 | 2571117.4569 | 1254588.5105
36 | 2571118.6341 | 1254504.9791 | 2571118.6227 | 1254505.0395
37 | 2571052.528 | 1254574.8943 | 2571059.8712 | 1254574.1022 | 2571067.4974 | 1254571.0516 | 2571070.9326 | 1254568.2006
38 | 2571147.6812 | 1254543.0618 | 2571140.4771 | 1254543.5182
39 | 2571111.7031 | 1254597.8758 | 2571114.3727 | 1254594.5601 | 2571117.4569 | 1254588.5105
40 | 2571121.7136 | 1254490.3404 | 2571120.6409 | 1254494.3733 | 2571118.6341 | 1254504.9791
41 | 2571038.202 | 1254573.0411 | 2571052.528 | 1254574.8943
42 | 2571007.5793 | 1254590.9055 | 2570976.1674 | 1254584.1226
43 | 2571007.5793 | 1254590.9055 | 2571010.116 | 1254589.3677 | 2571021.7744 | 1254586.5453
44 | 2571038.202 | 1254573.0411 | 2571034.7738 | 1254578.4615 | 2571030.5251 | 1254582.6741 | 2571024.0392 | 1254585.9971 | 2571021.7744 | 1254586.5453
45 | 2571063.8682 | 1254624.7836 | 2571087.1068 | 1254614.7939
46 | 2571087.1068 | 1254614.7939 | 2571094.1659 | 1254611.7594
47 | 2571094.1659 | 1254611.7594 | 2571094.1659 | 1254611.7594 | 2571103.3853 | 1254605.9326 | 2571107.9799 | 1254602.1365
48 | 2571111.7031 | 1254597.8758 | 2571108.8545 | 1254601.4139 | 2571107.9799 | 1254602.1365
49 | 2571226.1757 | 1254696.4623 | 2571222.6322 | 1254701.3029 | 2571210.1565 | 1254715.2919
50 | 2571239.0418 | 1254675.7391 | 2571237.3399 | 1254677.8488 | 2571231.0619 | 1254689.7874 | 2571226.1757 | 1254696.4623
51 | 2571210.1565 | 1254715.2919 | 2571208.8886 | 1254716.7136 | 2571202.219 | 1254723.9182
52 | 2571239.0418 | 1254675.7391 | 2571236.6739 | 1254668.1233 | 2571235.6843 | 1254645.2123
53 | 2571239.0418 | 1254675.7391 | 2571241.5086 | 1254672.6917 | 2571253.1667 | 1254662.6949 | 2571257.8067 | 1254655.1672
54 | 2571202.219 | 1254723.9182 | 2571199.0141 | 1254727.38 | 2571190.588 | 1254739.6071 | 2571188.2393 | 1254743.2299
55 | 2571234.4344 | 1254610.4459 | 2571235.5345 | 1254641.7445 | 2571235.6843 | 1254645.2123
56 | 2571260.1109 | 1254648.1513 | 2571257.8067 | 1254655.1672
57 | 2571176.7666 | 1254768.3717 | 2571178.8794 | 1254757.7431 | 2571183.5881 | 1254750.4041 | 2571188.2393 | 1254743.2299
58 | 2571234.4344 | 1254610.4459 | 2571234.3697 | 1254608.6057 | 2571234.4745 | 1254580.55
59 | 2571273.5073 | 1254640.3809 | 2571267.9139 | 1254641.1197 | 2571262.6411 | 1254644.1808 | 2571260.1109 | 1254648.1513
60 | 2571176.7666 | 1254768.3717 | 2571120.2816 | 1254789.4639
61 | 2571273.5073 | 1254640.3809 | 2571265.6573 | 1254633.1142 | 2571261.4569 | 1254627.1529
62 | 2571273.5073 | 1254640.3809 | 2571278.3023 | 1254644.6139
63 | 2571223.9288 | 1254274.1524 | 2571225.5638 | 1254278.1115
64 | 2571223.9288 | 1254274.1524 | 2571223.0499 | 1254272.0241 | 2571217.4308 | 1254256.7413 | 2571214.4509 | 1254249.0724
65 | 2571179.9027 | 1254287.7503 | 2571223.9288 | 1254274.1524
66 | 2571291.3231 | 1254342.6057 | 2571249.6194 | 1254331.5739
67 | 2571308.3108 | 1254325.5005 | 2571291.3231 | 1254342.6057
68 | 2571291.3231 | 1254342.6057 | 2571310.2033 | 1254344.3988
69 | 2571206.1593 | 1254227.7339 | 2571214.4509 | 1254249.0724
70 | 2571332.0715 | 1254346.4757 | 2571310.2033 | 1254344.3988
71 | 2571302.9001 | 1254638.2118 | 2571302.5647 | 1254637.571 | 2571298.4984 | 1254629.7077 | 2571296.5942 | 1254622.8234 | 2571296.5975 | 1254622.7977
72 | 2571313.5438 | 1254661.6449 | 2571311.8535 | 1254655.3155 | 2571302.9001 | 1254638.2118
73 | 2571300.4381 | 1254608.2394 | 2571297.4227 | 1254616.3706 | 2571296.5975 | 1254622.7977
74 | 2571313.5438 | 1254661.6449 | 2571301.8627 | 1254663.8253
75 | 2571345.883 | 1254654.3162 | 2571336.6926 | 1254658.3747 | 2571323.9049 | 1254661.0274 | 2571313.5438 | 1254661.6449
76 | 2571300.4381 | 1254608.2394 | 2571304.1015 | 1254598.4039 | 2571304.6664 | 1254596.1697
77 | 2571301.8627 | 1254663.8253 | 2571293.9615 | 1254658.4379
78 | 2571345.883 | 1254654.3162 | 2571349.7405 | 1254648.7159 | 2571357.0705 | 1254634.3596 | 2571367.1172 | 1254612.4629 | 2571368.2028 | 1254607.617
79 | 2571304.6664 | 1254596.1697 | 2571305.4925 | 1254592.9025
80 | 2571278.3023 | 1254644.6139 | 2571293.9615 | 1254658.4379 | 2571293.9615 | 1254658.4379
81 | 2571373.9011 | 1254575.6942 | 2571371.6579 | 1254592.1939 | 2571368.2028 | 1254607.617
82 | 2571306.6654 | 1254588.2637 | 2571305.4925 | 1254592.9025
83 | 2571165.4298 | 1254376.8314 | 2571167.4484 | 1254371.2175 | 2571168.6421 | 1254363.6714
84 | 2571152.8058 | 1254408.0693 | 2571158.8898 | 1254395.0197 | 2571165.4298 | 1254376.8314
85 | 2571170.1529 | 1254354.12 | 2571168.6421 | 1254363.6714
86 | 2571152.8058 | 1254408.0693 | 2571161.7249 | 1254411.7281 | 2571173.5609 | 1254413.4684
87 | 2571152.8058 | 1254408.0693 | 2571145.1988 | 1254424.3729 | 2571139.173 | 1254436.7682
88 | 2571170.1529 | 1254354.12 | 2571170.7046 | 1254350.6322 | 2571175.3084 | 1254319.1466
89 | 2571173.5609 | 1254413.4684 | 2571176.3258 | 1254413.875
90 | 2571131.1914 | 1254456.8743 | 2571136.4162 | 1254442.4391 | 2571139.173 | 1254436.7682
91 | 2571176.3258 | 1254413.875 | 2571177.0942 | 1254413.9879 | 2571190.0114 | 1254410.8602
92 | 2571131.1914 | 1254456.8743 | 2571129.0182 | 1254462.8779 | 2571126.2056 | 1254473.4521
93 | 2571131.1914 | 1254456.8743 | 2571118.2503 | 1254457.973
94 | 2571190.0114 | 1254410.8602 | 2571194.9961 | 1254409.6532 | 2571196.44 | 1254409.402
95 | 2571121.7136 | 1254490.3404 | 2571126.2056 | 1254473.4521
96 | 2571094.2525 | 1254474.6769 | 2571096.4148 | 1254471.8657 | 2571105.5746 | 1254463.0927 | 2571117.0159 | 1254458.0778 | 2571118.2503 | 1254457.973
97 | 2571306.6654 | 1254588.2637 | 2571310.3107 | 1254573.8461 | 2571313.1026 | 1254562.4867
98 | 2571313.1026 | 1254562.4867 | 2571314.4941 | 1254556.825
99 | 2571314.4941 | 1254556.825 | 2571315.2518 | 1254553.742 | 2571325.4932 | 1254540.8613 | 2571333.3461 | 1254531.6281 | 2571336.5837 | 1254525.3628
100 | 2571336.5837 | 1254525.3628 | 2571337.3665 | 1254523.8478 | 2571338.973 | 1254511.3761 | 2571339.9993 | 1254496.9342
101 | 2571342.5213 | 1254461.4433 | 2571339.9993 | 1254496.9342
102 | 2571342.5213 | 1254461.4433 | 2571342.9664 | 1254455.1804
103 | 2571237.5875 | 1254408.4002 | 2571231.4641 | 1254407.2404 | 2571203.8068 | 1254408.1203 | 2571196.44 | 1254409.402
104 | 2571237.5875 | 1254408.4002 | 2571246.4398 | 1254413.8608 | 2571249.0417 | 1254416.9864
105 | 2571261.4569 | 1254627.1529 | 2571257.427 | 1254614.3862 | 2571253.686 | 1254598.994 | 2571251.0624 | 1254583.8077 | 2571250.969 | 1254582.0885
106 | 2571251.7634 | 1254552.8712 | 2571251.5498 | 1254555.353 | 2571250.3746 | 1254571.1471 | 2571250.969 | 1254582.0885
107 | 2571254.9197 | 1254528.4017 | 2571253.3203 | 1254534.775 | 2571251.7634 | 1254552.8712
108 | 2571264.9369 | 1254485.2408 | 2571258.2262 | 1254515.2269 | 2571254.9197 | 1254528.4017
109 | 2571264.9369 | 1254485.2408 | 2571279.1621 | 1254492.6876 | 2571282.9656 | 1254503.8877
110 | 2571269.5265 | 1254434.8068 | 2571288.9565 | 1254435.9856
111 | 2571269.5265 | 1254434.8068 | 2571262.589 | 1254433.7399 | 2571254.3767 | 1254423.3952 | 2571249.0417 | 1254416.9864
112 | 2571288.9565 | 1254435.9856 | 2571307.6996 | 1254437.1227 | 2571307.7181 | 1254440.9363 | 2571330.3775 | 1254442.3055
113 | 2571343.8236 | 1254443.1179 | 2571342.9664 | 1254455.1804
114 | 2571186.9511 | 1254106.1669 | 2571186.7515 | 1254130.2934
115 | 2571186.9511 | 1254106.1669 | 2571180.9975 | 1254116.6586 | 2571175.5964 | 1254136.2168
116 | 2571188.34 | 1254075.4507 | 2571188.2083 | 1254090.1946 | 2571186.9511 | 1254106.1669
117 | 2571169.9122 | 1254156.8005 | 2571175.5964 | 1254136.2168
118 | 2571188.34 | 1254075.4507 | 2571189.0452 | 1254063.8395 | 2571189.4592 | 1254059.0232
119 | 2571188.34 | 1254075.4507 | 2571179.502 | 1254074.5822 | 2571171.9297 | 1254073.6244
120 | 2571167.5585 | 1254165.3235 | 2571169.9122 | 1254156.8005
121 | 2571189.4592 | 1254059.0232 | 2571182.3795 | 1254055.1885 | 2571174.2227 | 1254047.0784 | 2571168.4881 | 1254043.5655
122 | 2571189.4592 | 1254059.0232 | 2571190.1759 | 1254051.2923 | 2571192.4492 | 1254044.1097 | 2571197.5192 | 1254033.4111 | 2571204.1474 | 1254025.0843
123 | 2571171.9297 | 1254073.6244 | 2571161.9248 | 1254072.359
124 | 2571240.4577 | 1254006.8618 | 2571233.6591 | 1254008.0957 | 2571226.3517 | 1254010.1772 | 2571217.5004 | 1254014.3342 | 2571210.2453 | 1254019.4175 | 2571204.1474 | 1254025.0843
125 | 2571240.4577 | 1254006.8618 | 2571240.0991 | 1253999.8477 | 2571241.4889 | 1253995.5492 | 2571245.9643 | 1253991.2912 | 2571245.9643 | 1253991.2912
126 | 2571245.9643 | 1253991.2912 | 2571253.1018 | 1253988.0717
127 | 2571253.1018 | 1253988.0717 | 2571253.9132 | 1253987.7057 | 2571277.6841 | 1253976.8605 | 2571287.3116 | 1253971.1665
128 | 2571329.831 | 1253918.5114 | 2571333.038 | 1253914.5689
129 | 2571333.038 | 1253914.5689 | 2571383.8559 | 1253934.561
130 | 2571329.831 | 1253918.5114 | 2571318.2772 | 1253932.7148
131 | 2571318.2772 | 1253932.7148 | 2571315.6649 | 1253935.9262 | 2571303.61 | 1253954.9283
132 | 2571298.2173 | 1253961.9294 | 2571300.849 | 1253959.2805 | 2571303.61 | 1253954.9283
133 | 2571298.2173 | 1253961.9294 | 2571291.5025 | 1253968.6878 | 2571287.3116 | 1253971.1665
134 | 2571343.8236 | 1254443.1179 | 2571330.3775 | 1254442.3055
135 | 2571343.8236 | 1254443.1179 | 2571346.1967 | 1254408.5971
136 | 2571347.3489 | 1254391.836 | 2571346.1967 | 1254408.5971
137 | 2571347.3489 | 1254391.836 | 2571348.8847 | 1254369.4955
138 | 2571348.8847 | 1254369.4955 | 2571349.36 | 1254362.5813
139 | 2571350.3478 | 1254348.2115 | 2571349.36 | 1254362.5813
140 | 2571350.3478 | 1254348.2115 | 2571332.0715 | 1254346.4757
141 | 2571350.3478 | 1254348.2115 | 2571353.3944 | 1254348.4456
142 | 2571396.5107 | 1254412.5803 | 2571399.1348 | 1254390.9935
143 | 2571396.1515 | 1254415.5344 | 2571396.5107 | 1254412.5803
144 | 2571399.1348 | 1254390.9935 | 2571400.6991 | 1254378.1248
145 | 2571403.8357 | 1254352.3216 | 2571400.6991 | 1254378.1248
146 | 2571403.8357 | 1254352.3216 | 2571402.2284 | 1254352.1981
147 | 2571403.8357 | 1254352.3216 | 2571412.7028 | 1254353.0458 | 2571416.6912 | 1254351.0585 | 2571429.801 | 1254352.3364
148 | 2571375.103 | 1254350.1137 | 2571402.2284 | 1254352.1981
149 | 2571432.7248 | 1254352.6214 | 2571429.801 | 1254352.3364
150 | 2571353.3944 | 1254348.4456 | 2571375.103 | 1254350.1137

## bus_geodata
| x | y | coords
0 | 2570844.6695 | 1254559.3451
1 | 2570901.644 | 1254543.2591
2 | 2570724.1118 | 1254598.8898
3 | 2570922.2464 | 1254538.9883
4 | 2570942.0163 | 1254522.1984
5 | 2570954.5732 | 1254578.1332
6 | 2570968.1685 | 1254523.463
7 | 2570931.0775 | 1254598.6644
8 | 2570959.3138 | 1254583.4356
9 | 2571045.9077 | 1254049.2924
10 | 2571050.5134 | 1254050.3949
11 | 2570980.8429 | 1254115.3112
12 | 2571130.9652 | 1254067.9678
13 | 2571161.6234 | 1254072.3209
14 | 2571157.4392 | 1254237.1766
15 | 2571172.2359 | 1254184.2411
16 | 2571160.7379 | 1254244.2633
17 | 2570989.6549 | 1254306.4652
18 | 2571161.6394 | 1254293.4922
19 | 2571177.0625 | 1254307.1498
20 | 2571039.6944 | 1254485.2415
21 | 2571043.1334 | 1254502.1434
22 | 2571039.9231 | 1254484.7998
23 | 2571063.7298 | 1254514.6952
24 | 2571100.3916 | 1254544.5394
25 | 2571084.3202 | 1254545.1852
26 | 2571119.8182 | 1254540.4971
27 | 2571031.961 | 1254541.4862
28 | 2571061.1202 | 1254543.8809
29 | 2571077.3566 | 1254561.7912
30 | 2571120.8499 | 1254544.7616
31 | 2571118.6227 | 1254505.0395
32 | 2571070.9326 | 1254568.2006
33 | 2571140.4771 | 1254543.5182
34 | 2571117.4569 | 1254588.5105
35 | 2571118.6341 | 1254504.9791
36 | 2571052.528 | 1254574.8943
37 | 2570976.1674 | 1254584.1226
38 | 2571007.5793 | 1254590.9055
39 | 2571021.7744 | 1254586.5453
40 | 2571038.202 | 1254573.0411
41 | 2571063.8682 | 1254624.7836
42 | 2571087.1068 | 1254614.7939
43 | 2571094.1659 | 1254611.7594
44 | 2571107.9799 | 1254602.1365
45 | 2571111.7031 | 1254597.8758
46 | 2571226.1757 | 1254696.4623
47 | 2571210.1565 | 1254715.2919
48 | 2571239.0418 | 1254675.7391
49 | 2571202.219 | 1254723.9182
50 | 2571235.6843 | 1254645.2123
51 | 2571257.8067 | 1254655.1672
52 | 2571188.2393 | 1254743.2299
53 | 2571234.4343 | 1254610.4459
54 | 2571260.1109 | 1254648.1513
55 | 2571176.7666 | 1254768.3717
56 | 2571234.4745 | 1254580.55
57 | 2571273.5073 | 1254640.3809
58 | 2571120.2816 | 1254789.4639
59 | 2571225.5638 | 1254278.1115
60 | 2571223.9288 | 1254274.1524
61 | 2571249.6194 | 1254331.5739
62 | 2571291.3231 | 1254342.6057
63 | 2571214.4509 | 1254249.0724
64 | 2571179.9027 | 1254287.7503
65 | 2571308.3108 | 1254325.5005
66 | 2571310.2033 | 1254344.3988
67 | 2571206.1593 | 1254227.7339
68 | 2571302.9001 | 1254638.2118
69 | 2571296.5975 | 1254622.7977
70 | 2571313.5438 | 1254661.6449
71 | 2571300.4381 | 1254608.2394
72 | 2571301.8627 | 1254663.8253
73 | 2571345.883 | 1254654.3162
74 | 2571304.6664 | 1254596.1697
75 | 2571293.9615 | 1254658.4379
76 | 2571368.2028 | 1254607.617
77 | 2571305.4925 | 1254592.9025
78 | 2571278.3023 | 1254644.6139
79 | 2571373.9011 | 1254575.6942
80 | 2571165.4298 | 1254376.8314
81 | 2571168.6421 | 1254363.6714
82 | 2571152.8058 | 1254408.0693
83 | 2571170.1529 | 1254354.12
84 | 2571173.5609 | 1254413.4684
85 | 2571139.173 | 1254436.7682
86 | 2571175.3084 | 1254319.1466
87 | 2571176.3258 | 1254413.875
88 | 2571131.1914 | 1254456.8743
89 | 2571190.0114 | 1254410.8602
90 | 2571126.2056 | 1254473.4521
91 | 2571118.2503 | 1254457.973
92 | 2571306.6654 | 1254588.2637
93 | 2571313.1026 | 1254562.4867
94 | 2571314.4941 | 1254556.825
95 | 2571094.2525 | 1254474.6769
96 | 2571121.7136 | 1254490.3404
97 | 2571336.5837 | 1254525.3628
98 | 2571339.9993 | 1254496.9342
99 | 2571342.5213 | 1254461.4433
100 | 2571196.44 | 1254409.402
101 | 2571237.5875 | 1254408.4002
102 | 2571261.4569 | 1254627.1529
103 | 2571250.969 | 1254582.0885
104 | 2571251.7634 | 1254552.8712
105 | 2571254.9197 | 1254528.4017
106 | 2571264.9369 | 1254485.2408
107 | 2571282.9656 | 1254503.8877
108 | 2571269.5265 | 1254434.8068
109 | 2571288.9565 | 1254435.9856
110 | 2571249.0417 | 1254416.9864
111 | 2571147.6812 | 1254543.0618
112 | 2571342.9664 | 1254455.1804
113 | 2571186.7515 | 1254130.2934
114 | 2571186.9511 | 1254106.167
115 | 2571175.5964 | 1254136.2168
116 | 2571188.34 | 1254075.4507
117 | 2571169.9122 | 1254156.8005
118 | 2571189.4592 | 1254059.0232
119 | 2571171.9297 | 1254073.6244
120 | 2571161.9248 | 1254072.359
121 | 2571168.4881 | 1254043.5655
122 | 2571204.1474 | 1254025.0843
123 | 2571240.4577 | 1254006.8618
124 | 2571167.5585 | 1254165.3235
125 | 2571245.9643 | 1253991.2912
126 | 2571253.1018 | 1253988.0717
127 | 2571333.038 | 1253914.5689
128 | 2571329.831 | 1253918.5114
129 | 2571383.8559 | 1253934.561
130 | 2571318.2772 | 1253932.7148
131 | 2571303.61 | 1253954.9283
132 | 2571298.2173 | 1253961.9294
133 | 2571287.3116 | 1253971.1665
134 | 2571330.3775 | 1254442.3055
135 | 2571343.8236 | 1254443.1179
136 | 2571346.1967 | 1254408.5971
137 | 2571347.3489 | 1254391.836
138 | 2571348.8847 | 1254369.4955
139 | 2571349.36 | 1254362.5813
140 | 2571350.3478 | 1254348.2115
141 | 2571396.5106 | 1254412.5803
142 | 2571399.1348 | 1254390.9935
143 | 2571396.1515 | 1254415.5344
144 | 2571400.6991 | 1254378.1248
145 | 2571403.8357 | 1254352.3216
146 | 2571402.2284 | 1254352.1981
147 | 2571429.801 | 1254352.3364
148 | 2571432.7248 | 1254352.6214
149 | 2571375.103 | 1254350.1137
150 | 2571353.3944 | 1254348.4456
151 | 2571332.0715 | 1254346.4757
152 | 2571074.1675 | 1254488.3635

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1